## Building Description
Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on Friday, August 14, 2015
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm, marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs et al. (2003)
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Retail
| Building Prototype | Standalone Retail
Form
| Total Floor Area (sq feet) | 24695 (178 ft x 139 ft)
Building shape
| Aspect Ratio | 1.28
| Number of Floors | 1
| Window Fraction (Window-to-Wall Ratio) | 7.1% (Window Dimensions: 82.136 ft x 5 ft, 9.843 ft x 8.563 ft and 82.136 ft x 5 on the street facing facade) |  |  | 2003 CBECS Data and PNNL's CBECS Study 2007.
| Window Locations | Windows only on the street facing façade (25.4% WWR)
| Shading Geometry | None
| Azimuth | Non-directional
| Thermal Zoning | Five thermal zones (See ZoneSummary tab)
| Floor to floor height (feet) | N/A
| Floor to ceiling height (feet) | 20
| Glazing sill height (feet) | 5 ft (top of the window is 8.73 ft high with 3.74 ft high glass)
Architecture
Exterior walls
| Construction | Concrete Block Wall: 8 in. CMU+Wall Insulation+0.5 in. gypsum board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Exterior wall layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Mass |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up roof: Roof membrane+roof insulation+metal decking |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Roofs, Insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential; Vertical Glazing |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Same as above requirements |  |  | Ducker Fenestration Market Data provided by the 90.1 envelope subcommittee
| Operable area | 2% |  |  | Ducker Fenestration Market Data provided by the envelope subcommittee
Skylight
| Dimensions | Core Retail, Rectangular skylight 4 ft x 4 ft = 16 ft² per skylight Number of skylights and total skylight area vary according to requirements in codes or standards |  |  | Applicable codes or standards
| Glass-Type and frame | Hypothetical glass and frame meeting requirements in codes or standards below
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential; Skylight with Curb, Glass |  |  | Applicable codes or standards
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 6" concrete slab poured directly on to the earth with carpet
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Slab-on-Grade Floors, unheated |  |  | Applicable codes or standards
| Thermal properties for basement walls | NA
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 0.5 in gypsum board + 0.5 in gypsum board
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Additional infiltration through building entrance |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. PNNL-20026. Energy Saving Impact of ASHRAE 90.1 Vestibule Requirements: Modeling of Air Infiltration through Door Openings. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | Gas furnace inside the packaged air conditioning unit for back_space, core_retail, point_of_sale, and front_retail. Standalone gas furnace for front_entry. |  |  | 2003 CBECS Data, PNNL's CBECS Study 2006, and 90.1 Mechanical Subcommittee input.
| Cooling type | Packaged air conditioning unit for back_space, core_retail, point_of_sale, and front_retail; No cooling for front_entry.
| Distribution and terminal units | Constant air volume air distribution 4 single-zone roof top units serving four thermal zones ( back_space, core_retail, point_of_sale, and front_retail)
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Various by climate location and design cooling capacity Requirements in codes or standards Minimum equipment efficiency for Air Conditioners and Condensing Units |  |  | Applicable codes or standards
| Heating | Various by climate location and design heating capacity Requirements in codes or standards Minimum equipment efficiency for Warm Air Furnaces |  |  | Applicable codes or standards
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating
| Thermostat Setback | 85°F Cooling/60°F Heating
| Supply air temperature | Maximum 104°F, Minimum 55°F
| Chilled water supply temperatures | NA
| Hot water supply temperatures | NA
| Economizers | Requirements in codes or standards |  |  | Applicable codes or standards
| Ventilation | ASHRAE Standard 62.1 or International Mechanical Code See under Outdoor Air. |  |  | Applicable codes or standards
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Mechanical Efficiency (%) | Depending on the fan motor size and requirements in codes or standards |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Depending on the fan supply air cfm
Pump
| Pump Type | N/A
| Rated Pump Heat | N/A
| Pump Power | N/A
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Efficiency | NA
Service Water Heating
| SWH type | Storage Tank
| Fuel type | Natural Gas |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 40
| Water temperature setpoint | 140 F
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary |  |  | User's Manual for ASHRAE Standard 90.1-2004 (Appendix G)
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | ASHRAE Standard 62.1
| Schedule | See under Schedules
Misc.
Elevator
| Peak Power | NA
| Schedule | NA
Exterior Lighting
| Peak Power | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting [W/ft²] | People [ft²/person] | Number of People | Plug and Process [W/ft²]
BACK_SPACE | 4089.1018 | Yes | 81835.7442 | 1 | 4479.6164 | 0 | 0.839 | 66.6286 | 61.3716 | 0.74973
CORE_RETAIL | 17227.4227 | Yes | 344775.3575 | 1 | 3841.2089 | 0 | 1.7 | 66.6286 | 258.559 | 0.30008
POINT_OF_SALE | 1623.3053 | Yes | 32487.3775 | 1 | 2042.9901 | 409.5668 | 1.7 | 66.6286 | 24.3635 | 1.9993
FRONT_RETAIL | 1623.3053 | Yes | 32487.3775 | 1 | 2042.9901 | 409.5668 | 1.7 | 66.6286 | 24.3635 | 0.30008
FRONT_ENTRY | 129.1669 | Yes | 2585.0338 | 1 | 262.4241 | 84.2814 | 1.3 | 66.6286 | 1.9386 | 0
TOTAL1 | 24692.3019 |  | 494170.8906 |  | 12669.3373 |  |  |  | 370.5961
AREA WEIGHTED AVERAGE | [6 empty] | 179.4548 | 66.6286 |  | 0.48468
1. Only volume, and gross wall area include unconditioned space.
2. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone | Area (ft2) | Multipliers | Assumed Space Type | 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
BACK_SPACE | 4089.5158 | 1 | Storage rooms | 61.3427 | 613.4274 | 490.7419 | 490.7419 | 0.15 | 0.12 | 0.12
CORE_RETAIL | 17229 | 1 | Sales (except as below) | 258.435 | 5168.7 | 4005.7425 | 4005.7425 | 0.3 | 0.2325 | 0.2325
POINT_OF_SALE | 1623.4697 | 1 | Sales (except as below) | 24.352 | 487.0409 | 377.4567 | 377.4567 | 0.3 | 0.2325 | 0.2325
FRONT_RETAIL | 1623.4697 | 1 | Sales (except as below) | 24.352 | 487.0409 | 377.4567 | 377.4567 | 0.3 | 0.2325 | 0.2325
FRONT_ENTRY2. | 129.18 | 1 | Sales (except as below) | 1.9377 | 38.754 | 30.0343 | 30.0343 | 0.3 | 0.2325 | 0.2325
TOTAL | 24694.6351 |  |  | 370.4195 | 6794.9632 | 5281.4321 | 5281.4321 | 0.27516 | 0.21387 | 0.21387
1. The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1 or International Mechanical Code

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat. | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat. | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
Exterior Loads Schedules
BLDG_EXTERIOR_LIGHT | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
(AstronomicalClock control) |  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
(FAN_SCH) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
| (°C) |  | SummerDesign | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  |  | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
|  |  | Sun, Hol, Other | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  |  | WinterDesign | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
HTGSETP_SCH | Temperature | Through 12/31 | WD | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 64.04 | 68 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 60.008 | 60.008 | 60.008
| (°F) |  | SummerDesign | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008
|  |  | Sat | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 64.04 | 68 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 60.008 | 60.008
|  |  | Sun, Hol, Other | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 64.04 | 68 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008
|  |  | WinterDesign | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 64.994 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 60.008 | 60.008 | 60.008
CLGSETP_SCH | Temperature | Through 12/31 | WD | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
| (°C) |  | WinterDesign | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
|  |  | Sat | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
|  |  | Sun, Hol, Other | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
|  |  | SummerDesign | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
CLGSETP_SCH | Temperature | Through 12/31 | WD | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 82.04 | 78.08 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 84.992 | 84.992 | 84.992
| (°F) |  | WinterDesign | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992
|  |  | Sat | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 82.04 | 78.08 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 84.992 | 84.992 | 84.992
|  |  | Sun, Hol, Other | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 82.04 | 78.08 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 84.992 | 84.992 | 84.992
|  |  | SummerDesign | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 80.006 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 84.992 | 84.992 | 84.992
OA_DAMPER_SCH | on/off | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
MinOA_Sched | fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
Notes: | 1. For climate zones other than 1B, 2B, and 3B occupied cooling thermostat setpoints are maintained continuously (no setback). 2. These schedules reflect optimum start controls. For systems less than 10,000 cfm there is no optimal start and full occupied temperature setpoints begin two hours prior to occupancy instead of being ramped up incrementally beginning two hours prior to occupancy. 3. The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.

## SchedulePlots
RetailStandalone: Weekday Schedules