## Building Description
Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on Friday, August 14, 2015
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm, marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs' paper. See Reference.
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Food service
| Building Prototype | Fast Food
Form
| Total Floor Area (sq feet) | 2500 (50 ft x 50 ft)
Building shape
| Aspect Ratio | 1
| Number of Floors | 1
| Window Fraction (Window-to-Wall Ratio) | South: 28% East: 14% North: 0% West: 14% Total: 14%
| Window Locations | East (23.3 ft x 3 ft), south (46.7 ft x 3 ft), and west (23.3 ft x 3 ft) sides of dining zone façade
| Shading Geometry | none
| Azimuth | non-directional
| Thermal Zoning | Kitchen, Dining, and Unconditioned Attic (See ZoneSummary tab)
| Floor to floor height (feet) | NA
| Floor to ceiling height (feet) | 10
| Glazing sill height (feet) | 3.5 (top of the window is 6.5 ft high with 3 ft high glass)
Architecture
Exterior walls
| Construction | Wood-framed wall: 1 in. stucco + 0.625 in. gypsum board + wall insulation + 0.625 in. gypsum board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Exterior wall layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Wood-framed |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Unconditioned attic roof modeled with asphalt shingles and 0.625 in. gypsum board (no insulation). Ceiling between attic and conditioned zones modeled with wood-joist attic roof consisting of the following layers: insulation and 0.625 in. gypsum board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Attic Roof (all zones): 0.071 - No Insulation Ceiling: Requirements in codes or standards Nonresidential; roofs, attic and other |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Insulated Ceiling - horizontal Attic Roof East & West - 45 deg. North & South - 18.44 deg.
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential; Vertical Glazing |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Applicable codes or standards |  |  | Ducker Fenestration Market Data provided by the 90.1 envelope subcommittee
| Operable area | 2% of total WWR |  |  | Ducker Fenestration Market Data provided by the envelope subcommittee
Skylight
| Dimensions | Not Modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 6" concrete slab poured directly on to the earth
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; slab-on-grade floors, unheated |  |  | Applicable codes or standards
| Thermal properties for basement walls | NA
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 0.5 in gypsum board + 0.5 in gypsum board
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Additional infiltration through building entrance |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. PNNL-20026. Energy Saving Impact of ASHRAE 90.1 Vestibule Requirements: Modeling of Air Infiltration through Door Openings. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | Gas furnace inside the packaged air conditioning unit |  |  | 2003 CBECS Data, PNNL's CBECS Study 2006, and 90.1 Mechanical Subcommittee input.
| Cooling type | Packaged air conditioning unit
| Distribution and terminal units | Single zone, constant air volume air distribution
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Various by climate location and design cooling capacity Requirements in codes or standards Minimum equipment efficiency for Air Conditioners and Condensing Units |  |  | Applicable codes or standards
| Heating | Various by climate location and design heating capacity Requirements in codes or standards Minimum equipment efficiency for Warm Air Furnaces |  |  | Applicable codes or standards
HVAC Control
| Thermostat Setpoint | Dining - 75°F Cooling/70°F Heating Kitchen - 79°F Cooling/66°F Heating
| Thermostat Setback | Dining - 86°F Cooling/60°F Heating Kitchen - 86°F Cooling/60°F Heating
| Supply air temperature | Maximum 104°F, Minimum 55°F
| Chilled water supply temperatures | NA
| Hot water supply temperatures | NA
| Economizers | Various by climate location and cooling capacity Requirements in codes or standards Control type: differential dry bulb |  |  | Applicable codes or standards
| Ventilation | ASHRAE Ventilation Standard 62.1 and additional OSA to replace the kitchen exhaust flow See under Outdoor Air. |  |  | Applicable codes or standards
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Depending on the fan motor size and requirements in codes or standards |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Pump
| Pump Type | N/A
| Rated Pump Head | No
| Pump Power | N/A
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Power | NA
Service Water Heating
| SWH type | Storage tank
| Fuel type | Natural gas
| Thermal efficiency (%) | Requirements in codes or standards |  |  | ASHRAE 90.1
| Tank Volume (gal) | 100 |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F
| Water consumption | BLDG_SWH_SCH See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | ASHRAE Standard 62.1
| Schedule | See under Schedules
Misc.
Elevator
| Peak Power | NA
| Schedule | NA
Exterior Lighting
| Peak Power | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf
Kitchen
Dining

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting [W/ft²] | People [ft²/person] | Number of People | Plug and Process, Electricity [W/ft²] | Plug and Process, Gas [W/ft²]
DINING | 1250.4434 | Yes | 12507.7498 | 1 | 1000.3978 | 280.0769 | 2.1 | 14.316 | 87.3459 | 10.85 | 0
KITCHEN | 1250.4434 | Yes | 12507.7498 | 1 | 1000.3978 | 0 | 1.2 | 199.3476 | 6.2727 | 25.31 | 73.52
ATTIC | 2500.8868 | No | 9264.4505 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL1 | 2500.8868 |  | 34280.3033 |  | 2000.9032 | 280.0769 |  |  | 93.6185
AREA WEIGHTED AVERAGE | [6 empty] | 1.65 | 106.8318 |  | 18.08 | 36.76
1. Only volume, and gross wall area include unconditioned space.
2. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Occupant Density (Sqft/Person) (Note 1) |  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) (Note 2 3) |  |  | Total OSA Ventilation (cfm/ft2) (Note 2 3)
Zone | Area (sqft) | Multiplier | Assumed Space Type | 90.1-1989 | 62-1999 | 62.1-2004 | 62.1-2007 | 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
DINING | 1250.4434 | 1 | Restaurant dining rooms | 100 | 14.2857 | 14.2857 | 14.2857 | 87.531 | 1750.6208 | 881.5626 | 881.5626 | 1.4 | 0.705 | 0.705
KITCHEN | 1250.4434 | 1 | Kitchen | 100 | 50 | NA | NA | 6 | 90 | 875.3104 | 875.3104 | 0.071974 | 0.7 | 0.7
TOTAL2 | 2500.8868 | [6 empty] | 93.531 | 1840.6208 | 1756.873 | 1756.873 | 0.73599 | 0.7025 | 0.7025
1. Kitchen occupancy not included in ASHRAE 62.1-2004, therefore the value is from the DOE's benchmark model V1.0_3.0
2. In order to provide sufficient OSA to replace exhaust flow through kitchen hoods (3,300 cfm), modeled OSA to kitchen is different from OSA determined based on ASHRAE 62.1. It takes into account the available OSA in dining as transfer air.
3. The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1 or International Mechanical Code

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  |  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  |  | Sun, Hol, Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | Sun, Hol, Other | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | SummerDesign | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FF_GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | Sun, Hol, Other | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | SummerDesign | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exterior Loads Schedules
BLDG_EXTERIOR_LIGHT | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
(AstronomicalClock control) |  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sat, WinterDesign | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sun, Hol, Other | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
(FAN_SCH) |  |  | Sat, WinterDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
HTGSETP_SCH | Temperature | Through 12/31 | WD | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 13 | 13
| (°C) |  | SummerDesign | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  |  | Sat | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  | Sun, Hol, Other | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
CLGSETP_SCH | Temperature | Through 12/31 | WD | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33
| (°C) |  | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  |  | Sat | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 33
|  |  | WinterDesign | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
|  |  | Sun, Hol, Other | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| (°C) | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
HTGSETP_DINING_SCH | Temperature | Through 12/31 | WD, Winter Design | 60 | 60 | 60 | 60 | 60 | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| (°F) |  | SummerDesign | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Sat, Sun, Hol, Other | 60 | 60 | 60 | 60 | 60 | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, Winter Design | 60 | 60 | 60 | 60 | 60 | 63 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
| (°F) |  | SummerDesign | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Sat, Sun, Hol, Other | 60 | 60 | 60 | 60 | 60 | 63 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
CLGSETP_DINING_SCH | Temperature | Through 12/31 | WD, SummerDesign | 86 | 86 | 86 | 86 | 86 | 80 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| (°F) |  | WinterDesign | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
|  |  | Sat, Sun, Hol, Other | 86 | 86 | 86 | 86 | 86 | 80 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, SummerDesign | 86 | 86 | 86 | 86 | 86 | 83 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| (°F) |  | WinterDesign | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
|  |  | Sat, Sun, Hol, Other | 86 | 86 | 86 | 86 | 86 | 83 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
HTGSETP_DINING_SCH | Temperature | Through 12/31 | WD, Winter Design | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 18.3333 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
| (°C) |  | SummerDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  |  | Sat, Sun, Hol, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 18.3333 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, Winter Design | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 17.2222 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889
| (°C) |  | SummerDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  |  | Sat, Sun, Hol, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 17.2222 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889
CLGSETP_DINING_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 26.6667 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889
| (°C) |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Sat, Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 26.6667 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 28.3333 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111
| (°C) |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Sat, Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 28.3333 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111
MinOA_FFKitch_Sched (for kichen) | fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
MinOA_Sched (for dining) | fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
Notes: | The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.

## SchedulePlots
Restaurant FastFood: Weekday Schedules