## Building Description
Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on Friday, August 14, 2015
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing All 17 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm, marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs et al. (2003)
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Office
| Building Prototype | Large Office
Form
| Total Floor Area (sq feet) | 498,600 (240 ft x 160 ft) |  |  | Time Saver Standards; Large Office studies (ConEd, EPRI, MEOS, NEU1(1-4), NEU2, PNL) cited in Huang et al. 1991
Building shape
| Aspect Ratio | 1.5
| Number of Floors | 12 (plus basement)
| Window Fraction (Window-to-Wall Ratio) | 40% of above-grade gross walls 37.5% of gross walls (including the below-grade walls) |  |  | When applicable, certain codes or standards may restrict the window area to lower fractions
| Window Locations | Even distribution among all four sides |  |  | PNNL's CBECS Study
| Shading Geometry | None
| Azimuth | Nnon-directional
| Thermal Zoning |  |  |  | Time Saver Standards; Large Office studies (ConEd, EPRI, MEOS, NEU1(1-4), NEU2, PNL) cited in Huang et al. 1992
Perimeter zone depth: 15 ft. Each floor has four perimeter zones, one core zone and one IT closet zone. Percentages of floor area: Perimeter 29%, Core 70%, IT Closet 1% The basement has a datacenter zone occupying 28% of the basement floor area.
| Floor to floor height (feet) | 13
| Floor to ceiling height (feet) | 9
| Glazing sill height (feet) | 3 ft
Architecture
Exterior walls
| Construction | Mass (pre-cast concrete panel): 8 in. heavy-weight concrete + wall insulation + 0.5 in. gypsum board |  |  | Construction type: PNNL's CBECS Study
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Steel-Framed |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up roof: Roof membrane+roof insulation+metal decking |  |  | Construction type: PNNL's CBECS Study Base assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with a weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 0% |  |  | Ducker Fenestration Market Data provided by the 90.1 Envelope Subcommittee
Skylight
| Dimensions | Not modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Basement (conditioned)
| Construction | 8" concrete wall; 6" concrete slab, 140 lbs heavy-weight aggregate
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Floors, Mass |  |  | Applicable codes or standards
| Thermal properties for basement walls | No insulation
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | One gas-fired boiler |  |  | PNNL's CBECS Study
| Cooling type | Water-source DX cooling coil with fluid cooler for datacenter in the basement and IT closets in other floors Two water-cooled centrifugal chillers for the rest of the building |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Distribution and terminal units | VAV terminal box with damper and hot-water reheating coil except non-datacenter portion of the basement and IT closets that are served by CAV units.
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Requirements in codes or standards |  |  | Applicable codes or standards
Heating
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating |  |  | 90.1 Simulation Working Group
| Thermostat Setback | 85°F Cooling/60°F Heating
| Supply air temperature | Maximum 110F, Minimum 52F |  |  | Temperature setpoint reset may be required by codes and standards.
| Chilled water supply temperatures | 44 F
| Hot water supply temperatures | 180 F
| Economizers | Requirements in codes or standards |  |  | Applicable codes or standards
| Ventilation | ASHRAE Standard 62.1 or International Mechanical Code See under Outdoor Air |  |  | Applicable codes or standards
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Depending on the fan motor size and requirements in codes or standards |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Depending on the fan supply air cfm
Pump
| Pump Type | Primary chilled water (CHW) pumps: constant speed; secondary CHW pump: variable speed; IT closet (water loop heat pump) pump: constant speed; cooling tower pump: variable speed; service hot water (SWH): constant speed; hot water (HW) pump: variable speed
| Rated Pump Head | Use the pump power assumptions as specified in 90.1 Appendix G, i.e., 22 W/gpm for chilled water pump, 19 W/gpm for hot water and condensing water pumps. For SWH pump, first estimated based on circulation flow and then adjusted based on modeled design flow. |  |  | If applicable, model inputs for other codes or standards may be different. PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | Open cooling tower with two-speed fans; two-speed fluid-cooler for data center and IT closets
| Cooling Tower Power | Autosized
Service Water Heating
| SWH type | One main water heater with storage tank
| Fuel type | Natural gas
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 300 |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary |  |  | For data center and IT closet, see PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | ASHRAE Standard 62.1
| Schedule | See under Schedules
Misc.
Elevator
| Quantity |  | 12 |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0).
| Motor type |  | Traction
| Peak Motor Power Watts per elevator |  | 20370
| Heat Gain to Building |  | Exterior
| Peak Fan/lights Power Watts per elevator |  | 161.9 |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Motor and fan/lights Schedules |  | See under Schedules |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0) and Appendix DF 2007
Exterior Lighting
| Peak Power | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
McGraw-Hill Companies, Inc. (2001). Time-Saver Standards for Building Types. New York, NY.
LBNL (1991). Huang, Joe, Akbari, H., Rainer, L. and Ritschard, R. 481 Prototypical Commercial Buildings for 20 Urban Market Areas, prepared for the Gas Research Institute, Chicago IL, also LBL-29798, Berkeley CA.
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf

## Zone Summary
Zone Summary
Zone | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting2 [W/ft²] | People [ft²/person] | Number of People | Plug and Process [W/ft²]
BASEMENT | 29920.42 | Y | 239433.94 | 1 | 0 | 0 | 1.0004 | 199.9208 | 149.6614 | 0.45
CORE_BOTTOM | 26870.64 | Y | 241918.09 | 1 | 0 | 0 | 1.0004 | 199.9208 | 134.4064 | 0.75
CORE_MID | 26870.64 | Y | 241918.09 | 10 | 0 | 0 | 1.0004 | 199.9208 | 134.4064 | 0.75
CORE_TOP | 26870.64 | Y | 241918.09 | 1 | 0 | 0 | 1.0004 | 199.9208 | 134.4064 | 0.75
PERIMETER_BOT_ZN_3 | 3373.88 | Y | 30375.23 | 1 | 2159.52 | 2159.52 | 1.0004 | 199.9208 | 16.8761 | 0.75
PERIMETER_BOT_ZN_2 | 2174.25 | Y | 19574.95 | 1 | 1439.68 | 1439.68 | 1.0004 | 199.9208 | 10.8756 | 0.75
PERIMETER_BOT_ZN_1 | 3373.95 | Y | 30375.89 | 1 | 2159.52 | 2159.52 | 1.0004 | 199.9208 | 16.8764 | 0.74999
PERIMETER_BOT_ZN_4 | 2174.25 | Y | 19574.95 | 1 | 1439.68 | 1439.68 | 1.0004 | 199.9208 | 10.8756 | 0.74999
PERIMETER_MID_ZN_3 | 3373.88 | Y | 30375.23 | 10 | 2159.52 | 2159.52 | 1.0004 | 199.9208 | 16.8761 | 0.75
PERIMETER_MID_ZN_2 | 2174.25 | Y | 19574.95 | 10 | 1439.68 | 1439.68 | 1.0004 | 199.9208 | 10.8756 | 0.75
PERIMETER_MID_ZN_1 | 3373.95 | Y | 30375.89 | 10 | 2159.52 | 2159.52 | 1.0004 | 199.9208 | 16.8764 | 0.74999
PERIMETER_MID_ZN_4 | 2174.25 | Y | 19574.95 | 10 | 1439.68 | 1439.68 | 1.0004 | 199.9208 | 10.8756 | 0.74999
PERIMETER_TOP_ZN_3 | 3373.88 | Y | 30375.23 | 1 | 2159.52 | 2159.52 | 1.0004 | 199.9208 | 16.8761 | 0.75
PERIMETER_TOP_ZN_2 | 2174.25 | Y | 19574.95 | 1 | 1439.68 | 1439.68 | 1.0004 | 199.9208 | 10.8756 | 0.75
PERIMETER_TOP_ZN_1 | 3373.95 | Y | 30375.89 | 1 | 2159.52 | 2159.52 | 1.0004 | 199.9208 | 16.8764 | 0.74999
PERIMETER_TOP_ZN_4 | 2174.25 | Y | 19574.95 | 1 | 1439.68 | 1439.68 | 1.0004 | 199.9208 | 10.8756 | 0.74999
DATACENTER_BOT_ZN_6 | 389.72 | Y | 3508.68 | 1 | 0 | 0 | 1 | 0 | 0 | 20
DATACENTER_MID_ZN_6 | 389.72 | Y | 3508.68 | 10 | 0 | 0 | 1 | 0 | 0 | 20
DATACENTER_TOP_ZN_6 | 389.72 | Y | 3508.68 | 1 | 0 | 0 | 1 | 0 | 0 | 20
DATACENTER_BASEMENT_ZN_6 | 8436.28 | Y | 67509.29 | 1 | 0 | 0 | 1 | 0 | 0 | 45
GROUNDFLOOR_PLENUM | 38356.7 | N | 153434.28 | 1 | 3198.35 | 0 | 0 | 0 | 0 | 0
MIDFLOOR_PLENUM | 38356.7 | N | 153434.28 | 10 | 3198.35 | 0 | 0 | 0 | 0 | 0
TOPFLOOR_PLENUM | 38356.7 | N | 153434.28 | 1 | 3198.35 | 0 | 0 | 0 | 0 | 0
TOTAL1 | 498636.98 |  | 4450876.71 |  | 124761 | 86380.8 |  |  | 2428.582
AREA WEIGHTED AVERAGE | [6 empty] | 1.0004 | 194.6634 |  | 1.6612
1. Only volume, and gross wall area include unconditioned space. Total area and volume include multiplier of zone area and zone volume from Multipliers column
2. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone | Area (ft2) | Multipliers | Assumed Space Type | 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
BASEMENT | 29920.42 | 1 | Office space | 149.6614 | 2992.042 | 2543.2357 | 2543.2357 | 0.1 | 0.085 | 0.085
CORE_BOTTOM | 26870.64 | 1 | Office space | 134.4064 | 2687.064 | 2284.0044 | 2284.0044 | 0.1 | 0.085 | 0.085
CORE_MID | 26870.64 | 10 | Office space | 134.4064 | 2687.064 | 2284.0044 | 2284.0044 | 0.1 | 0.085 | 0.085
CORE_TOP | 26870.64 | 1 | Office space | 134.4064 | 2687.064 | 2284.0044 | 2284.0044 | 0.1 | 0.085 | 0.085
PERIMETER_BOT_ZN_3 | 3373.88 | 1 | Office space | 16.8761 | 337.388 | 286.7798 | 286.7798 | 0.1 | 0.085 | 0.085
PERIMETER_BOT_ZN_2 | 2174.25 | 1 | Office space | 10.8756 | 217.425 | 184.8113 | 184.8113 | 0.1 | 0.085 | 0.085
PERIMETER_BOT_ZN_1 | 3373.95 | 1 | Office space | 16.8764 | 337.395 | 286.7858 | 286.7858 | 0.1 | 0.085 | 0.085
PERIMETER_BOT_ZN_4 | 2174.25 | 1 | Office space | 10.8756 | 217.425 | 184.8113 | 184.8113 | 0.1 | 0.085 | 0.085
PERIMETER_MID_ZN_3 | 3373.88 | 10 | Office space | 16.8761 | 337.388 | 286.7798 | 286.7798 | 0.1 | 0.085 | 0.085
PERIMETER_MID_ZN_2 | 2174.25 | 10 | Office space | 10.8756 | 217.425 | 184.8113 | 184.8113 | 0.1 | 0.085 | 0.085
PERIMETER_MID_ZN_1 | 3373.95 | 10 | Office space | 16.8764 | 337.395 | 286.7858 | 286.7858 | 0.1 | 0.085 | 0.085
PERIMETER_MID_ZN_4 | 2174.25 | 10 | Office space | 10.8756 | 217.425 | 184.8113 | 184.8113 | 0.1 | 0.085 | 0.085
PERIMETER_TOP_ZN_3 | 3373.88 | 1 | Office space | 16.8761 | 337.388 | 286.7798 | 286.7798 | 0.1 | 0.085 | 0.085
PERIMETER_TOP_ZN_2 | 2174.25 | 1 | Office space | 10.8756 | 217.425 | 184.8113 | 184.8113 | 0.1 | 0.085 | 0.085
PERIMETER_TOP_ZN_1 | 3373.95 | 1 | Office space | 16.8764 | 337.395 | 286.7858 | 286.7858 | 0.1 | 0.085 | 0.085
PERIMETER_TOP_ZN_4 | 2174.25 | 1 | Office space | 10.8756 | 217.425 | 184.8113 | 184.8113 | 0.1 | 0.085 | 0.085
DATACENTER_BOT_ZN_6 | 389.72 | 1 | IT Closet | 0 | 0 | 23.3832 | 23.3832 | 0 | 0.06 | 0.06
DATACENTER_MID_ZN_6 | 389.72 | 10 | IT Closet | 0 | 0 | 23.3832 | 23.3832 | 0 | 0.06 | 0.06
DATACENTER_TOP_ZN_6 | 389.72 | 1 | IT Closet | 0 | 0 | 23.3832 | 23.3832 | 0 | 0.06 | 0.06
DATACENTER_BASEMENT_ZN_6 | 8436.28 | 1 | Datacenter | 0 | 0 | 506.1768 | 506.1768 | 0 | 0.06 | 0.06
TOTAL | 498636.98 |  |  | 2428.582 | 48552.406 | 42056.3203 | 42056.3203 | 0.09737 | 0.084343 | 0.084343
1. The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1 or International Mechanical Code

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
(Fan Schedule) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | WD | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
| (°F) |  | SummerDesign | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | Sat | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
|  |  | WinterDesign | 60.08 | 60.08 | 60.08 | 60.08 | 63.68 | 67.28 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
|  |  | Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
CLGSETP_SCH | Temperature | Through 12/31 | WD | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
| (°F) |  | SummerDesign | 80.06 | 80.06 | 80.06 | 80.06 | 78.26 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
|  |  | Sat | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
|  |  | WinterDesign | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
|  |  | Sun, Hol, Other | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
HTGSETP_DC_SCH | Temperature | Through 12/31 | WD | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
| (°F) |  | SummerDesign | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
|  |  | Sat | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
|  |  | WinterDesign | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
|  |  | Sun, Hol, Other | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
CLGSETP_DC_SCH | Temperature | Through 12/31 | WD | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
| (°F) |  | SummerDesign | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
|  |  | Sat | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
|  |  | WinterDesign | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
|  |  | Sun, Hol, Other | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
Cool-Supply-Air-Temp-Sch | Temperature (°F) | Through 12/31 | All | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04
Heat-Supply-Air-Temp-Sch | Temperature (°F) | Through 12/31 | All | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04
CW-Loop-Temp-Schedule | Temperature (°F) | Through 12/31 | All | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06
HW-Loop-Temp-Schedule | Temperature (°F) | Through 12/31 | All | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
MinOA_Sched | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
(Climate Zone 1-3) |  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
MinOA_MotorizedDamper_Sched | fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
(Climate Zone 4-8) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes: | The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.