## Building Description
Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on Friday, August 14, 2015
| Item | Input (Based on AEDG for Highway Lodging Buildings Prototype) |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm, marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs et al. (2003)
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Lodging
| Building Prototype | Small Hotel
Form
| Total Floor Area (sq feet) | 43200 (180 ft x 60 ft) |  |  | Hampton Inn Prototype from Hilton Hotels Corporation, Version 5.1, September 2004 (URL: http://www.hamptonfranchise.com ), referred as Hilton prototype; F.W.Dodge Database
| Building shape |  |  |  | Hilton prototype and CBECS 2003
| Aspect Ratio | 3 |  |  | Hilton prototype
| Number of Floors | 4
| Window Fraction (Window-to-Wall Ratio) | South: 3.1%, East: 11.4%, North: 4.0%, West: 15.2% Average Total: 10.9% |  |  | Hilton prototype
| Window Locations | One per guest room (4' x 5') |  |  | Hilton prototype
| Shading Geometry | None
| Azimuth | Non-directional
Thermal Zoning
Ground Floor: 19 zones including guest rooms, lobby, office space, meeting room, laundry room, employee lounge, restrooms, exercise room, mechanical room, corridor, stairs, storage; 2nd-4th Floor: 16 zones per floor, including guest rooms, corridor, stairs and storage; Guest rooms accounts for 63% of total floor area.
| Floor to floor height (feet) | Ground floor: 11 ft Upper floors: 9 ft
| Floor to ceiling height (feet) | Same as above
| Glazing sill height (feet) | 3 ft in ground floor, 2 ft. in upper floors
Architecture
Exterior walls
| Construction | Steel-Frame Walls (2x4 16 in. OC) 1 in. Stucco + 5/8 in. gypsum board + wall Insulation + 5/8 in. gypsum board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Base Assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Steel-Framed |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up roof: Roof membrane + roof insulation + metal decking |  |  | AEDG Highway Lodging Committee Recommendation
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Roofs, Insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential for ground floor and residential for upper floors; vertical glazing |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 0%
Skylight
| Dimensions | Not modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 6" concrete slab poured directly on to the earth
| Thermal properties for slab-on-grade floor F-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards |  |  | Applicable codes or standards
| Thermal properties for basement walls | NA
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Additional infiltration through building entrance |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. PNNL-20026. Energy Saving Impact of ASHRAE 90.1 Vestibule Requirements: Modeling of Air Infiltration through Door Openings. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | Guest rooms: PTAC with electric resistance heating Public spaces (office, laundry, lobby, and meeting room): gas furnace inside the packaged air conditioning units Storage and stairs: electric cabinet heaters |  |  | 2003 CBECS, NC3, Ducker report
| Cooling type | Guest rooms and corridors: PTAC Public space: Split system with DX cooling Storage and stairs: No cooling
| Distribution and terminal units | Constant air volume systems
HVAC Sizing
| Air Conditioning | PTAC: 9,000 Btu/hr Split system: autosized to design day |  |  | PTAC: Ducker report
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | PTAC: requirements in codes or standards Split system: varies by climate locations based on cooling capacity |  |  | Applicable codes or standards
| Heating | PTAC and electric cabinet heater: Et = 100% Gas furnace: varies by climate locations based on heating capacity |  |  | Applicable codes or standards
HVAC Control
| Thermostat Setpoint | 70°F Cooling/Heating for rented guest rooms 74°F Cooling/66°F Heating for vacant guest rooms 75°F Cooling/70°F Heating for air conditioned public spaces (lobby, meeting room etc.) 45°F heating for stairs and storage rooms |  |  | AEDG Highway Lodging Committee Recommendation
| Thermostat Setback | 74°F Cooling/66°F Heating for rented guest rooms
| Supply air temperature | No seasonal supply air temperature reset.
| Chilled water supply temperatures | NA
| Hot water supply temperatures | NA
| Economizers | Requirements in codes or standards |  |  | Applicable codes or standards
| Ventilation | See under Outdoor Air. |  |  | Applicable codes or standards
| Demand Control Ventilation | No |  |  | Applicable codes or standards
| Energy Recovery Ventilation | No |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Mechanical Efficiency (%) | Varies by fan motor size |  |  | AEDG-SR Technical Support Document (Liu 2006)
| Supply Fan Pressure Drop | PTAC: 1.33 in. w.c. Cabinet heater: 0.2 in w.c. Split DX units: fan power limitation (depends on design flow rate) |  |  | PTAC Manufacture's Catalogs Split System: Wassmer and Brandemuehl, 2006.
Pump
| Pump Type | Constant speed (recirculating pump for main water heater) |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Rated Pump Head | 10 ft
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Power | NA
Service Water Heating
| SWH type | Main water heater and laundry water heater, both with storage tank
| Fuel type | Natural gas
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 300 (main); 200 (laundry) |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F for guest rooms and 180 F for laundry
| Water consumption | See under Schedules |  |  | Guest room: ASHRAE Handbook of Applications 2007, Chapter 49, Table 7 Laundry: AEDG Highway Lodging Committee Recommendation
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary |  |  | AEDG Highway Lodging Committee Recommendation
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | Guest Room: AEDG Highway Lodging Committee Recommendation All other spaces: ASHRAE 62.1-1999
| Schedule | See under Schedules
Misc.
Elevator
| Motor type |  | 2 |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0).
| Peak Motor Power Watts per elevator |  | hydraulic
| Heat Gain to Building |  | 16055
| Peak Fan/lights Power Watts per elevator |  | Interior
| Motor and fan/lights Schedules |  | 161.9 |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Exterior Lighting |  | See under Schedules |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0) and Appendix DF 2007
| Peak Power, kW | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Derived based on ASHRAE 90.1-2004 and inputs from 90.1 Lighting Subcommittee. Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
McGraw-Hill Companies, Inc. (2001). Time-Saver Standards for Building Types. New York, NY.
LBNL (1991). Huang, Joe, Akbari, H., Rainer, L. and Ritschard, R. 481 Prototypical Commercial Buildings for 20 Urban Market Areas, prepared for the Gas Research Institute, Chicago IL, also LBL-29798, Berkeley CA.
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Ducker International Standard. 2001. 2000 U.S. Market For Residential and Specialty Air Conditioning: PTAC.
Sachs, H., 2005. Opportunities for Elevator Energy Efficiency Improvements, ACEEE.
Wassmer and Brandemuehl, 2006, Effect of Data Availability on Modeling of Residential Air Conditioners and Heat Pumps for Energy Calculations
Jiang W, RE Jarnagin, K Gowri, M McBride, and B Liu. 2008. Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings . PNNL-17875, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/publications/abstracts.asp?report=246912
Liu B, RE Jarnagin, DW Winiarski, W Jiang, MF McBride, and C Crall. 2006. Technical Support Document: The Development of the Advanced Energy Design Guide for Small Retail Buildings . PNNL-16031, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/publications/abstracts.asp?report=221540
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf

## Zone Summary
Zone Summary
Zone | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting2 [W/ft²] | People [ft²/person] | Number of People | Plug and Process [W/ft²]
REARSTAIRSFLR1 | 216.0536 | Y | 2375.2054 | 1 | 384.8852 | 0 | 0.59993 |  |  | 0
CORRIDORFLR1 | 1620.2402 | Y | 17809.4527 | 1 | 351.852 | 105.6632 | 0.49995 |  |  | 0
REARSTORAGEFLR1 | 216.0536 | N | 2375.2054 | 1 | 384.8852 | 0 | 0.79992 |  |  | 0
FRONTLOUNGEFLR1 | 1755.3409 | Y | 19294.5738 | 1 | 1011.6552 | 159.5708 | 1.0999 | 33.1408 | 52.9662 | 2.4219
RESTROOMFLR1 | 351.0466 | Y | 3858.9148 | 1 | 143.0004 | 0 | 0.89991 | 350.8836 | 1.0005 | 0
MEETINGROOMFLR1 | 864.1065 | Y | 9498.7042 | 1 | 351.852 | 53.1544 | 1.2999 | 20.1212 | 42.9451 | 0.57435
MECHANICALROOMFLR1 | 351.0466 | Y | 3858.9148 | 1 | 143.0004 | 0 | 1.4999 |  |  | 0
GUESTROOM101 | 351.0466 | Y | 3858.9148 | 1 | 143.0004 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM102 | 351.0466 | Y | 3858.9148 | 1 | 143.0004 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM103 | 351.0466 | Y | 3858.9148 | 1 | 143.0004 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM104 | 351.0466 | Y | 3858.5618 | 1 | 143.0004 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM105 | 351.0466 | Y | 3858.5618 | 1 | 143.0004 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
EMPLOYEELOUNGEFLR1 | 351.0466 | Y | 3858.5618 | 1 | 143.0004 | 17.754 | 1.1999 | 19.4756 | 18.0249 | 1.9991
LAUNDRYROOMFLR1 | 1053.1399 | N | 11575.6855 | 1 | 428.8936 | 53.1544 | 0.59993 | 95.6564 | 11.0096 | 40.6654
ELEVATORCOREFLR1 | 162.0132 | N | 1780.8747 | 1 | 65.9588 | 0 | 0 |  |  | 200.2807
EXERCISECENTERFLR1 | 351.0466 | Y | 3858.5618 | 1 | 143.0004 | 17.754 | 0.89991 | 50.1416 | 7.0011 | 1.7277
FRONTOFFICEFLR1 | 1404.1866 | Y | 15434.6002 | 1 | 571.7864 | 70.8008 | 1.0999 | 140.3104 | 10.0077 | 1.2807
FRONTSTAIRSFLR1 | 216.0536 | Y | 2374.4996 | 1 | 384.8852 | 0 | 0.59993 |  |  | 0
FRONTSTORAGEFLR1 | 134.9931 | N | 1484.0622 | 1 | 54.9836 | 0 | 0.79992 |  |  | 0
REARSTAIRSFLR2 | 216.0536 | Y | 1943.2216 | 1 | 314.9452 | 0 | 0.59993 |  |  | 0
CORRIDORFLR2 | 1350.1463 | Y | 12142.4878 | 1 | 197.8764 | 28.1912 | 0.49995 |  |  | 0
REARSTORAGEFLR2 | 216.0536 | N | 1943.5745 | 1 | 314.9452 | 0 | 0.79992 |  |  | 0
GUESTROOM201 | 351.0466 | Y | 3157.2939 | 1 | 359.922 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM202_205 | 1404.2942 | Y | 12629.1756 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0032 | 1.1053
GUESTROOM206_208 | 1134.2004 | Y | 10200.3251 | 1 | 377.8912 | 72.092 | 1.0999 | 251.8916 | 4.5027 | 1.1053
GUESTROOM209_212 | 1404.2942 | Y | 12629.1756 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0032 | 1.1053
GUESTROOM213 | 351.0466 | Y | 3157.2939 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM214 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM215_218 | 1404.1866 | Y | 12628.1168 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0028 | 1.1053
ELEVATORCOREFLR2 | 162.0132 | N | 1457.2397 | 1 | 54.0152 | 0 | 0 |  |  | 0
GUESTROOM219 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM220_223 | 1404.1866 | Y | 12628.1168 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0028 | 1.1053
GUESTROOM224 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
FRONTSTORAGEFLR2 | 134.9931 | N | 1214.0723 | 1 | 44.9768 | 0 | 0.79992 |  |  | 0
FRONTSTAIRSFLR2 | 216.0536 | Y | 1942.8686 | 1 | 314.8376 | 0 | 0.59993 |  |  | 0
REARSTAIRSFLR3 | 216.0536 | Y | 1943.2216 | 1 | 314.9452 | 0 | 0.59993 |  |  | 0
CORRIDORFLR3 | 1350.1463 | Y | 12142.4878 | 1 | 197.8764 | 28.1912 | 0.49995 |  |  | 0
REARSTORAGEFLR3 | 216.0536 | N | 1943.5745 | 1 | 314.9452 | 0 | 0.79992 |  |  | 0
GUESTROOM301 | 351.0466 | Y | 3157.2939 | 1 | 359.922 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM302_305 | 1404.2942 | Y | 12629.1756 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0032 | 1.1053
GUESTROOM306_308 | 1134.2004 | Y | 10200.3251 | 1 | 377.8912 | 72.092 | 1.0999 | 251.8916 | 4.5027 | 1.1053
GUESTROOM309_312 | 1404.2942 | Y | 12629.1756 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0032 | 1.1053
GUESTROOM313 | 351.0466 | Y | 3157.2939 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM314 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM315_318 | 1404.1866 | Y | 12628.1168 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0028 | 1.1053
ELEVATORCOREFLR3 | 162.0132 | N | 1457.2397 | 1 | 54.0152 | 0 | 0 |  |  | 0
GUESTROOM319 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM320_323 | 1404.1866 | Y | 12628.1168 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0028 | 1.1053
GUESTROOM324 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
FRONTSTORAGEFLR3 | 134.9931 | N | 1214.0723 | 1 | 44.9768 | 0 | 0.79992 |  |  | 0
FRONTSTAIRSFLR3 | 216.0536 | Y | 1942.8686 | 1 | 314.8376 | 0 | 0.59993 |  |  | 0
REARSTAIRSFLR4 | 216.0536 | Y | 1943.2216 | 1 | 314.9452 | 0 | 0.59993 |  |  | 0
CORRIDORFLR4 | 1350.1463 | Y | 12142.4878 | 1 | 197.8764 | 28.1912 | 0.49995 |  |  | 0
REARSTORAGEFLR4 | 216.0536 | N | 1943.5745 | 1 | 314.9452 | 0 | 0.79992 |  |  | 0
GUESTROOM401 | 351.0466 | Y | 3157.2939 | 1 | 359.922 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM402_405 | 1404.2942 | Y | 12629.1756 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0032 | 1.1053
GUESTROOM406_408 | 1134.2004 | Y | 10200.3251 | 1 | 377.8912 | 72.092 | 1.0999 | 251.8916 | 4.5027 | 1.1053
GUESTROOM409_412 | 1404.2942 | Y | 12629.1756 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0032 | 1.1053
GUESTROOM413 | 351.0466 | Y | 3157.2939 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM414 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM415_418 | 1404.1866 | Y | 12628.1168 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0028 | 1.1053
ELEVATORCOREFLR4 | 162.0132 | N | 1457.2397 | 1 | 54.0152 | 0 | 0 |  |  | 0
GUESTROOM419 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
GUESTROOM420_423 | 1404.1866 | Y | 12628.1168 | 1 | 467.8448 | 70.8008 | 1.0999 | 233.9224 | 6.0028 | 1.1053
GUESTROOM424 | 351.0466 | Y | 3156.941 | 1 | 116.9612 | 17.754 | 1.0999 | 233.9224 | 1.5007 | 1.1053
FRONTSTORAGEFLR4 | 134.9931 | N | 1214.0723 | 1 | 44.9768 | 0 | 0.79992 |  |  | 0
FRONTSTAIRSFLR4 | 216.0536 | Y | 1942.8686 | 1 | 314.8376 | 0 | 0.59993 |  |  | 0
TOTAL1 | 40101.3474 |  | 410163.0396 |  | 18234.5416 | 1983.3908 |  |  | 258.5134
AREA WEIGHTED AVERAGE | [6 empty] | 1.0425 | 173.6145 |  | 2.8247
1. Only volume, and gross wall area include unconditioned space.
2. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone | Area (ft2) | Multiplier | Assumed Space Type | 62.1-2004 1,2,3 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
REARSTAIRSFLR1 | 216.0536 | 1 | Corridors (public spaces) | 0 | 10.8027 | 12.9632 | 12.9632 | 0.05 | 0.06 | 0.06
CORRIDORFLR1 | 1620.2402 | 1 | Corridors (public spaces) | 0 | 81.012 | 97.2144 | 97.2144 | 0.05 | 0.06 | 0.06
REARSTORAGEFLR1 | 216.0536 | 1 | Storage rooms | 0 | 32.408 | 25.9264 | 25.9264 | 0.15 | 0.12 | 0.12
FRONTLOUNGEFLR1 | 1755.3409 | 1 | Lobbies/prefunction (hotel, motel, resort, dorm) | 52.6602 | 789.9034 | 500.2722 | 500.2722 | 0.45 | 0.285 | 0.285
RESTROOMFLR1 | 351.0466 | 1 | Restroom | 0 | 0 | 0 | 0 | 0 | 0 | 0
MEETINGROOMFLR1 | 864.1065 | 1 | Conference / meeting | 43.2053 | 864.1065 | 267.873 | 267.873 | 1 | 0.31 | 0.31
MECHANICALROOMFLR1 | 351.0466 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
GUESTROOM101 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM102 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM103 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM104 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM105 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
EMPLOYEELOUNGEFLR1 | 351.0466 | 1 | Conference / meeting | 17.5523 | 351.0466 | 108.8245 | 108.8245 | 1 | 0.31 | 0.31
LAUNDRYROOMFLR1 | 1053.1399 | 1 | Commercial laundry | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELEVATORCOREFLR1 | 162.0132 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
EXERCISECENTERFLR1 | 351.0466 | 1 | Health club/weight rooms | 3.5105 | 52.657 | 91.2721 | 91.2721 | 0.15 | 0.26 | 0.26
FRONTOFFICEFLR1 | 1404.1866 | 1 | Office space | 7.0209 | 140.4187 | 119.3559 | 119.3559 | 0.1 | 0.085 | 0.085
FRONTSTAIRSFLR1 | 216.0536 | 1 | Corridors (public spaces) | 0 | 10.8027 | 12.9632 | 12.9632 | 0.05 | 0.06 | 0.06
FRONTSTORAGEFLR1 | 134.9931 | 1 | Storage rooms | 0 | 20.249 | 16.1992 | 16.1992 | 0.15 | 0.12 | 0.12
REARSTAIRSFLR2 | 216.0536 | 1 | Corridors (public spaces) | 0 | 10.8027 | 12.9632 | 12.9632 | 0.05 | 0.06 | 0.06
CORRIDORFLR2 | 1350.1463 | 1 | Corridors (public spaces) | 0 | 67.5073 | 81.0088 | 81.0088 | 0.05 | 0.06 | 0.06
REARSTORAGEFLR2 | 216.0536 | 1 | Storage rooms | 0 | 32.408 | 25.9264 | 25.9264 | 0.15 | 0.12 | 0.12
GUESTROOM201 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM202_205 | 1404.2942 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2577 | 114.2577 | 0.099694 | 0.081363 | 0.081363
GUESTROOM206_208 | 1134.2004 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 4.5 | 180 | 90.552 | 90.552 | 0.1587 | 0.079838 | 0.079838
GUESTROOM209_212 | 1404.2942 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2577 | 114.2577 | 0.099694 | 0.081363 | 0.081363
GUESTROOM213 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM214 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM215_218 | 1404.1866 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2512 | 114.2512 | 0.099702 | 0.081365 | 0.081365
ELEVATORCOREFLR2 | 162.0132 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
GUESTROOM219 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM220_223 | 1404.1866 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2512 | 114.2512 | 0.099702 | 0.081365 | 0.081365
GUESTROOM224 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
FRONTSTORAGEFLR2 | 134.9931 | 1 | Storage rooms | 0 | 20.249 | 16.1992 | 16.1992 | 0.15 | 0.12 | 0.12
FRONTSTAIRSFLR2 | 216.0536 | 1 | Corridors (public spaces) | 0 | 10.8027 | 12.9632 | 12.9632 | 0.05 | 0.06 | 0.06
REARSTAIRSFLR3 | 216.0536 | 1 | Corridors (public spaces) | 0 | 10.8027 | 12.9632 | 12.9632 | 0.05 | 0.06 | 0.06
CORRIDORFLR3 | 1350.1463 | 1 | Corridors (public spaces) | 0 | 67.5073 | 81.0088 | 81.0088 | 0.05 | 0.06 | 0.06
REARSTORAGEFLR3 | 216.0536 | 1 | Storage rooms | 0 | 32.408 | 25.9264 | 25.9264 | 0.15 | 0.12 | 0.12
GUESTROOM301 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM302_305 | 1404.2942 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2577 | 114.2577 | 0.099694 | 0.081363 | 0.081363
GUESTROOM306_308 | 1134.2004 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 4.5 | 180 | 90.552 | 90.552 | 0.1587 | 0.079838 | 0.079838
GUESTROOM309_312 | 1404.2942 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2577 | 114.2577 | 0.099694 | 0.081363 | 0.081363
GUESTROOM313 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM314 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM315_318 | 1404.1866 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2512 | 114.2512 | 0.099702 | 0.081365 | 0.081365
ELEVATORCOREFLR3 | 162.0132 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
GUESTROOM319 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM320_323 | 1404.1866 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2512 | 114.2512 | 0.099702 | 0.081365 | 0.081365
GUESTROOM324 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
FRONTSTORAGEFLR3 | 134.9931 | 1 | Storage rooms | 0 | 20.249 | 16.1992 | 16.1992 | 0.15 | 0.12 | 0.12
FRONTSTAIRSFLR3 | 216.0536 | 1 | Corridors (public spaces) | 0 | 10.8027 | 12.9632 | 12.9632 | 0.05 | 0.06 | 0.06
REARSTAIRSFLR4 | 216.0536 | 1 | Corridors (public spaces) | 0 | 10.8027 | 12.9632 | 12.9632 | 0.05 | 0.06 | 0.06
CORRIDORFLR4 | 1350.1463 | 1 | Corridors (public spaces) | 0 | 67.5073 | 81.0088 | 81.0088 | 0.05 | 0.06 | 0.06
REARSTORAGEFLR4 | 216.0536 | 1 | Storage rooms | 0 | 32.408 | 25.9264 | 25.9264 | 0.15 | 0.12 | 0.12
GUESTROOM401 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM402_405 | 1404.2942 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2577 | 114.2577 | 0.099694 | 0.081363 | 0.081363
GUESTROOM406_408 | 1134.2004 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 4.5 | 180 | 90.552 | 90.552 | 0.1587 | 0.079838 | 0.079838
GUESTROOM409_412 | 1404.2942 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2577 | 114.2577 | 0.099694 | 0.081363 | 0.081363
GUESTROOM413 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM414 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM415_418 | 1404.1866 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2512 | 114.2512 | 0.099702 | 0.081365 | 0.081365
ELEVATORCOREFLR4 | 162.0132 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
GUESTROOM419 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
GUESTROOM420_423 | 1404.1866 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 6 | 140 | 114.2512 | 114.2512 | 0.099702 | 0.081365 | 0.081365
GUESTROOM424 | 351.0466 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 28.5628 | 28.5628 | 0.099702 | 0.081365 | 0.081365
FRONTSTORAGEFLR4 | 134.9931 | 1 | Storage rooms | 0 | 20.249 | 16.1992 | 16.1992 | 0.15 | 0.12 | 0.12
FRONTSTAIRSFLR4 | 216.0536 | 1 | Corridors (public spaces) | 0 | 10.8027 | 12.9632 | 12.9632 | 0.05 | 0.06 | 0.06
TOTAL | 43206.7269 |  |  | 239.4493 | 5698.7156 | 3914.0116 | 3914.0116 | 0.13189 | 0.090588 | 0.090588
1. Assume each guestroom and suite contains 1.5 persons (per AEDG)
2. Laundry occupancy not included in ASHRAE 62.1, 2004, therefore occupancy based on ASHRAE 62-1999.
3. Kitchen occupancy not included in ASHRAE 62.1, 2004, therefore occupancy based on ASHRAE 62-1999.
4. Each single room zone (351 sf) contains one guestroom with one bedroom and one bath. Multiple guestroom zones are indicated by zone name. ASHRAE 62-1999 requires 30 cfm per each living room and each bedroom and 35 cfm per bath, regardless of area. For bathroom, the 35 cfm OA requirement is the installed capacity for intermittent use. Based on the interpretation from ASHRAE (http://www.ashrae.org/technology/page/913), the 35 cfm of outdoor air can be supplied to the hotel/motel bedroom then exhausted through the bathroom at the same rate, this would meet the standard for both the bedroom and the bathroom. So, we should use a ventilation rate of 35 cfm for guestroom, not 65 cfm. This is consistent with inputs from AEDG Highway Lodging project committee. Thus, the OA rate equals to 35 cfm for standard guest room and 60 cfm for suite.
5. 62-1999 specifies 50 cfm/wc or cfm/urinal of OA ventilation air for public restrooms. But there OA ventilation air can by supplied by transfer air. Reviewing the the Hamption Inn protocol blueprints and Staybridge protocol blueprints shows that no OA air is supplied to restrooms. Instead, exhaust air of 50 cfm/wc or 50 cfm/urinal is applied in practice. Thus, no OA is applied to public restrooms.
6. The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1 or International Mechanical Code

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
GUESTROOM_ EQUIP_SCH | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
LOBBY_ LIGHT_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5
LOBBY_ EQUIP_SCH | Fraction | Through 12/31 | WD | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
|  |  | Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OFFICE_ EQUIP_SCH | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
MEETINGROOM_ EQUIP_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LAUNDRY_ ELE_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LAUNDRY_ GAS_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ExerciseCenter_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
ExerciseCenter_Eqp_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
ExerciseCenter_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
EMPLOYEELOUNGE_ LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Service Water Heater Load Schedule
GuestRoom_SHW_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
|  |  | Sat, Sun, Hol | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
LaundryRoom_SHW_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration Schedule
GUESTROOM_INFIL_SCH | fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sat, Sun, Hol | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
COMMONAREA_INFIL_SCH | fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sat, Sun, Hol | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HVAC Schedules
GUESTROOM_FAN_SCH | on/off | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(HVAC Operation) |  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
COMMONAREA_FAN_SCH | on/off | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(HVAC Operation) |  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | WD | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
(Vacant) | (°F) |  | Sat, Sun, Hol | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | WD | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
(Vacant) | (°F) |  | Sat, Sun, Hol | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | WD | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
(Rented) | (°F) |  | Sat, Sun, Hol | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | WD | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
(Rented) | (°F) |  | Sat, Sun, Hol | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | WD | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| (°F) |  | Sat, Sun, Hol | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | WD | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| (°F) |  | Sat, Sun, Hol | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | WD | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
(for storage rooms and stairs) | (°F) |  | Sat, Sun, Hol | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
GUESTROOM_OA_SCH | on/off | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
COMMONAREA_OA_SCH | on/off | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Elevator Schedules
HTGSETP_SCH | Temperature | Through 12/31 | WD
| (°C) |  | SummerDesign
Sat
WinterDesign
Sun, Hol, Other
CLGSETP_SCH | Temperature | Through 12/31 | WD
| (°C) |  | SummerDesign
Sat
WinterDesign
Sun, Hol, Other
Dual Zone Control Type Sched | Control Type | Through 12/31 | All
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All
| (°C) | Through 9/30 | All
|  | Through 12/31 | All
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | WD | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889
(Vacant) | (°F) |  | Sat, Sun, Hol | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | WD | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333
(Vacant) | (°F) |  | Sat, Sun, Hol | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333 | 23.3333
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | WD | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
(Rented) | (°F) |  | Sat, Sun, Hol | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | WD | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
(Rented) | (°F) |  | Sat, Sun, Hol | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | WD | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
| (°F) |  | Sat, Sun, Hol | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | WD | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889
| (°F) |  | Sat, Sun, Hol | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | WD | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222
(for storage rooms and stairs) | (°F) |  | Sat, Sun, Hol | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222 | 7.2222
Notes: | The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.