## Baseline Description
Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on Friday, August 14, 2015
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm, marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs et al. (2003)
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Health Care
| Building Prototype | Outpatient Healthcare
Form
| Total Floor Area (sq feet) | 40950
Building shape
| Aspect Ratio | NA
| Number of Floors | 3
| Window Fraction (Window-to-Wall Ratio) | North: 20.5%, East:19.1%, South: 24.1%, West: 12.9% Average Total: 20%
| Window Locations | See pictures
| Shading Geometry | Nne
| Azimuth | Non-directional
| Thermal Zoning | See Zone Summary and HVAC Zoning
| Floor to floor height (feet) | 10 ft
| Floor to ceiling height (feet) | 10 ft
| Glazing sill height (feet) | 3 ft (4 ft high windows)
Architecture
Exterior walls
| Construction | Steel-Frame Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in. |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Exterior wall layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; walls, above-grade, steel-framed |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up roof: Roof membrane+roof insulation+metal decking |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Non-residential; roofs, insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with a weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Non-residential; vertical glazing |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 12% |  |  | Ducker Fenestration Market Data provided by the 90.1 envelope subcommittee
Skylight
| Dimensions | Not modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 6" concrete slab poured directly on to the earth
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; slab-on-grade floors, unheated |  |  | Applicable codes or standards
| Thermal properties for basement walls | NA
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions | Bsed on floor plan and floor-to-floor height
| Internal Mass | Interior furnishings: 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Additional infiltration through building entrance |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. PNNL-20026. Energy Saving Impact of ASHRAE 90.1 Vestibule Requirements: Modeling of Air Infiltration through Door Openings. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | Gas boiler
| Cooling type | DX cooling coil
| Distribution and terminal units | VAV terminal box with damper and hot water reheating coil Electric resistance reheat in AHU-2 See Outdoor&Supply Air for minimum total supply air requirements.
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Various by climate location and design cooling capacity Requirements in codes or standards for DX cooling coil |  |  | Applicable codes or standards
| Heating | Various by climate location and design heating capacity Requirements in codes or standards for boiler |  |  | Applicable codes or standards
HVAC Control
| Thermostat Setpoint | Administration zones: 72°F Cooling/70°F Heating Critical zones: 72°F Cooling/70°F Heating Operating rooms: 65°F Cooling/65°F Heating
| Thermostat Setback | Administration zones: 77°F Cooling/65°F Heating Critical zones: no setback Operating rooms: 72°F Cooling/65°F Heating
| Supply air temperature | Cooling temps: design = 49 deg F, operation = 52 deg F for critical spaces (first floor) Cooling temps: design = 52 deg F, operation = 55 deg F for admin spaces (second and third floor)
| Chilled water supply temperatures | NA
| Hot water supply temperatures | 180 F
| Economizers | Various by climate location and cooling capacity per requirements in codes or standards Control type: differential dry bulb |  |  | Applicable codes or standards
| OA Ventilation | ASHRAE Standard 62.1 or International Mechanical Code See under Outdoor Air |  |  | Applicable codes or standards
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | 60% to 62% depending on the fan motor size |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Pump
| Pump Type | Pump serving the hot water system, constant speed
| Rated Pump Head | Requirements in codes or standards |  |  | Applicable codes or standards
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Power | NA
Service Water Heating
| SWH type | Storage Tank
| Fuel type | Natural Gas
| SWH Design Capacity (kBtu/h) | 200 |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 200 |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary
| Schedule | See under Schedules
Misc.
Elevator
| Quantity | 3 |  |  | Reference: DOE Commercial Reference Building Models of the National Building Stock
| Motor type | hydraulic
| Peak Motor Power (W/elevator) | 16055
| Heat Gain to Building | Interior
| Peak Fan/lights Power (W/elevator) | 161.9 |  |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Motor and fan/lights Schedules | See under Schedules |  |  | DOE Commercial Reference Building TSD and models (V1.3_5.0) and Addendum DF to 90.1-2007
Exterior Lighting
| Peak Power | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf

## Zone Summary
Zone Summary
Zone | Area (ft²) | Conditioned (Y/N) | Volume (ft³) | Multipliers | Gross Wall Area (ft²) | Window Glass Area (ft²) | Lighting (W/ft²) | People (ft²/person) | Number of People | Plug and Process (W/ft²)
Floor 1 Anesthesia | 108 | Yes | 1080 | 1 | 89.9863 | 24.0035 | 1.5 | 49.9445 | 2.1624 | 2.0002
Floor 1 Bio Haz | 56 | Yes | 560 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 1 Café | 420 | Yes | 4200 | 1 | 199.9934 | 96.0141 | 0.9 | 10.0104 | 41.9562 | 0.99964
Floor 1 Clean | 126 | Yes | 1260 | 1 | 0 | 0 | 1.5 | 49.9445 | 2.5228 | 2.0002
Floor 1 Clean Work | 165 | Yes | 1650 | 1 | 0 | 0 | 1.5 | 49.9445 | 3.3037 | 2.0002
Floor 1 Dictation | 126 | Yes | 1260 | 1 | 0 | 0 | 1.1 | 199.9934 | 0.63002 | 1.1
Floor 1 Dressing Room | 45 | Yes | 450 | 1 | 89.9863 | 24.9723 | 1.1 | 199.9934 | 0.22501 | 1.1
Floor 1 Electrical Room | 98 | Yes | 980 | 1 | 69.9654 | 0 | 1.5 | 0 | 0 | 5
Floor 1 Elevator Pump Room | 91 | Yes | 910 | 1 | 199.9934 | 0 | 1.5 | 0 | 0 | 534.6213
Floor 1 Humid | 54 | Yes | 540 | 1 | 0 | 0 | 1.1 | 199.9934 | 0.27001 | 1.1
Floor 1 IT Hall | 140 | Yes | 1400 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 IT Room | 112 | Yes | 1120 | 1 | 0 | 0 | 1.1 | 199.9934 | 0.56002 | 1.1
Floor 1 Lobby | 622 | Yes | 6220 | 1 | 220.0143 | 96.0141 | 1.3 | 99.9967 | 6.2202 | 1.1
Floor 1 Lobby Hall | 240 | Yes | 2400 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 Lobby Toilet | 54 | Yes | 540 | 1 | 59.955 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 1 Locker Room | 660 | Yes | 6600 | 1 | 220.0143 | 59.955 | 0.8 | 66.6286 | 9.9057 | 2.9998
Floor 1 Locker Room Hall | 496 | Yes | 4960 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 Lounge | 360 | Yes | 3600 | 1 | 0 | 0 | 0.8 | 66.6286 | 5.4031 | 2.9998
Floor 1 Med Gas | 56 | Yes | 560 | 1 | 150.0489 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 1 MRI Control Room | 168 | Yes | 1680 | 1 | 50.0522 | 0 | 0.4 | 49.9445 | 3.3637 | 10.0001
Floor 1 MRI Hall | 147 | Yes | 1470 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 MRI Room | 440 | Yes | 4400 | 1 | 0 | 0 | 0.4 | 49.9445 | 8.8098 | 10.0001
Floor 1 MRI Toilet | 54 | Yes | 540 | 1 | 59.955 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 1 Nourishment | 182 | Yes | 1820 | 1 | 0 | 0 | 1 | 49.9445 | 3.644 | 2.0002
Floor 1 Nurse Hall | 496 | Yes | 4960 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 Nurse Janitor | 54 | Yes | 540 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 1 Nurse Station | 261 | Yes | 2610 | 1 | 0 | 0 | 1 | 49.9445 | 5.2258 | 2.0002
Floor 1 Nurse Toilet | 54 | Yes | 540 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 1 Office | 483 | Yes | 4830 | 1 | 0 | 0 | 1.1 | 199.9934 | 2.4151 | 1.1
Floor 1 Operating Room 1 | 460 | Yes | 4600 | 1 | 430.0182 | 96.0141 | 2.2 | 49.9445 | 9.2102 | 10.996
Floor 1 Operating Room 2 | 480 | Yes | 4800 | 1 | 240.0352 | 72.0106 | 2.2 | 49.9445 | 9.6107 | 10.996
Floor 1 Operating Room 3 | 476 | Yes | 4760 | 1 | 0 | 0 | 2.2 | 49.9445 | 9.5306 | 10.996
Floor 1 PACU | 108 | Yes | 1080 | 1 | 0 | 0 | 0.8 | 49.9445 | 2.1624 | 2.9998
Floor 1 Pre-Op Hall | 528 | Yes | 5280 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 Pre-Op Room 1 | 189 | Yes | 1890 | 1 | 40.0417 | 0 | 0.7 | 99.9967 | 1.8901 | 2.0002
Floor 1 Pre-Op Room 2 | 338 | Yes | 3380 | 1 | 0 | 0 | 0.7 | 99.9967 | 3.3801 | 2.0002
Floor 1 Pre-Op Toilet | 54 | Yes | 540 | 1 | 59.955 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 1 Procedure Room | 285 | Yes | 2850 | 1 | 189.983 | 59.955 | 2.7 | 49.9445 | 5.7063 | 2.9998
Floor 1 Reception | 509 | Yes | 5090 | 1 | 130.028 | 35.9515 | 1.3 | 33.3681 | 15.2541 | 1.1
Floor 1 Reception Hall | 128 | Yes | 1280 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 Recovery Room | 540 | Yes | 5400 | 1 | 450.0391 | 96.0141 | 0.8 | 49.9445 | 10.812 | 2.9998
Floor 1 Scheduling | 119 | Yes | 1190 | 1 | 69.9654 | 7.9653 | 1.1 | 199.9934 | 0.59502 | 1.1
Floor 1 Scrub | 84 | Yes | 840 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 Soil | 126 | Yes | 1260 | 1 | 0 | 0 | 1.5 | 49.9445 | 2.5228 | 2.0002
Floor 1 Soil Hold | 56 | Yes | 560 | 1 | 0 | 0 | 1.5 | 49.9445 | 1.1212 | 2.0002
Floor 1 Soil Work | 180 | Yes | 1800 | 1 | 0 | 0 | 1.5 | 49.9445 | 3.604 | 2.0002
Floor 1 Step Down | 300 | Yes | 3000 | 1 | 369.9556 | 72.0106 | 0.8 | 49.9445 | 6.0067 | 2.9998
Floor 1 Sterile Hall | 616 | Yes | 6160 | 1 | 79.9759 | 24.0035 | 1 | 0 | 0 | 0.40041
Floor 1 Sterile Storage | 396 | Yes | 3960 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 1 Storage | 920 | Yes | 9200 | 1 | 630.0117 | 89.9863 | 0.9 | 0 | 0 | 0.10034
Floor 1 Sub-Sterile | 196 | Yes | 1960 | 1 | 140.0385 | 31.9688 | 1 | 0 | 0 | 0.40041
Floor 1 Utility Hall | 256 | Yes | 2560 | 1 | 159.9517 | 0 | 1 | 0 | 0 | 0.40041
Floor 1 Utility Janitor | 42 | Yes | 420 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 1 Utility Room | 360 | Yes | 3600 | 1 | 179.9726 | 24.0035 | 0.9 | 0 | 0 | 0.10034
Floor 1 Vestibule | 72 | Yes | 720 | 1 | 79.9759 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Conference | 336 | Yes | 3360 | 1 | 399.9869 | 96.0141 | 1.3 | 20.0209 | 16.7825 | 0.99964
Floor 2 Conference Toilet | 64 | Yes | 640 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 2 Dictation | 70 | Yes | 700 | 1 | 0 | 0 | 1.1 | 199.9934 | 0.35001 | 1.1
Floor 2 Exam 1 | 360 | Yes | 3600 | 1 | 420.0078 | 96.0141 | 1.5 | 49.9445 | 7.208 | 1.1
Floor 2 Exam 2 | 540 | Yes | 5400 | 1 | 179.9726 | 40.0417 | 1.5 | 49.9445 | 10.812 | 1.1
Floor 2 Exam 3 | 720 | Yes | 7200 | 1 | 240.0352 | 64.0453 | 1.5 | 49.9445 | 14.416 | 1.1
Floor 2 Exam 4 | 84 | Yes | 840 | 1 | 69.9654 | 24.0035 | 1.5 | 49.9445 | 1.6819 | 1.1
Floor 2 Exam 5 | 350 | Yes | 3500 | 1 | 250.0456 | 64.0453 | 1.5 | 49.9445 | 7.0078 | 1.1
Floor 2 Exam 6 | 225 | Yes | 2250 | 1 | 150.0489 | 44.9931 | 1.5 | 49.9445 | 4.505 | 1.1
Floor 2 Exam 7 | 792 | Yes | 7920 | 1 | 240.0352 | 59.955 | 1.5 | 49.9445 | 15.8576 | 1.1
Floor 2 Exam 8 | 270 | Yes | 2700 | 1 | 179.9726 | 59.955 | 1.5 | 49.9445 | 5.406 | 1.1
Floor 2 Exam 9 | 396 | Yes | 3960 | 1 | 120.0176 | 30.0313 | 1.5 | 49.9445 | 7.9288 | 1.1
Floor 2 Exam Hall 1 | 180 | Yes | 1800 | 1 | 59.955 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Exam Hall 2 | 180 | Yes | 1800 | 1 | 59.955 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Exam Hall 3 | 180 | Yes | 1800 | 1 | 59.955 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Exam Hall 4 | 198 | Yes | 1980 | 1 | 59.955 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Exam Hall 5 | 198 | Yes | 1980 | 1 | 59.955 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Exam Hall 6 | 198 | Yes | 1980 | 1 | 59.955 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Janitor | 63 | Yes | 630 | 1 | 159.9517 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 2 Lounge | 80 | Yes | 800 | 1 | 0 | 0 | 0.8 | 66.6286 | 1.2007 | 2.9998
Floor 2 Nurse Station 1 | 150 | Yes | 1500 | 1 | 0 | 0 | 1 | 49.9445 | 3.0033 | 2.0002
Floor 2 Nurse Station 2 | 180 | Yes | 1800 | 1 | 0 | 0 | 1 | 49.9445 | 3.604 | 2.0002
Floor 2 Office | 560 | Yes | 5600 | 1 | 399.9869 | 96.0141 | 1.1 | 199.9934 | 2.8001 | 1.1
Floor 2 Office Hall | 444 | Yes | 4440 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Reception | 984 | Yes | 9840 | 1 | 489.9732 | 179.9726 | 1.3 | 33.3681 | 29.4892 | 1.1
Floor 2 Reception Hall | 564 | Yes | 5640 | 1 | 69.9654 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Reception Toilet | 126 | Yes | 1260 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 2 Scheduling 1 | 324 | Yes | 3240 | 1 | 0 | 0 | 1.1 | 199.9934 | 1.6201 | 1.1
Floor 2 Scheduling 2 | 342 | Yes | 3420 | 1 | 0 | 0 | 1.1 | 199.9934 | 1.7101 | 1.1
Floor 2 Storage 1 | 56 | Yes | 560 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 2 Storage 2 | 120 | Yes | 1200 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 2 Storage 3 | 144 | Yes | 1440 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 2 Utility | 126 | Yes | 1260 | 1 | 89.9863 | 24.0035 | 0.9 | 0 | 0 | 0.10034
Floor 2 Work | 1690 | Yes | 16900 | 1 | 259.9484 | 59.955 | 1.1 | 199.9934 | 8.4503 | 0.90862
Floor 2 Work Hall | 834 | Yes | 8340 | 1 | 59.955 | 0 | 1 | 0 | 0 | 0.40041
Floor 2 Work Toilet | 54 | Yes | 540 | 1 | 59.955 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 2 X-Ray | 900 | Yes | 9000 | 1 | 0 | 0 | 0.4 | 49.9445 | 18.02 | 10.0001
Floor 3 Dressing Room | 42 | Yes | 420 | 1 | 0 | 0 | 1.1 | 199.9934 | 0.21001 | 1.1
Floor 3 Elevator Hall | 370 | Yes | 3700 | 1 | 40.0417 | 0 | 1 | 0 | 0 | 0.40041
Floor 3 Humid | 108 | Yes | 1080 | 1 | 0 | 0 | 1.1 | 199.9934 | 0.54002 | 1.1
Floor 3 Janitor | 63 | Yes | 630 | 1 | 159.9517 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 3 Locker | 120 | Yes | 1200 | 1 | 0 | 0 | 0.8 | 66.6286 | 1.801 | 2.9998
Floor 3 Lounge | 759 | Yes | 7590 | 1 | 230.0248 | 59.955 | 0.8 | 66.6286 | 11.3915 | 2.9998
Floor 3 Lounge Toilet | 192 | Yes | 1920 | 1 | 120.0176 | 44.9931 | 0.9 | 0 | 0 | 0.40041
Floor 3 Mechanical | 350 | Yes | 3500 | 1 | 250.0456 | 64.0453 | 1.5 | 0 | 0 | 5
Floor 3 Mechanical Hall | 300 | Yes | 3000 | 1 | 0 | 0 | 1 | 0 | 0 | 0.40041
Floor 3 Office | 3036 | Yes | 30360 | 1 | 740.0188 | 210.0039 | 1.1 | 199.9934 | 15.1805 | 1.1
Floor 3 Office Hall | 834 | Yes | 8340 | 1 | 59.955 | 0 | 1 | 0 | 0 | 0.40041
Floor 3 Office Toilet | 54 | Yes | 540 | 1 | 59.955 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 3 Physical Therapy 1 | 1300 | Yes | 13000 | 1 | 850.026 | 312.0458 | 0.9 | 49.9445 | 26.0289 | 1.5004
Floor 3 Physical Therapy 2 | 592 | Yes | 5920 | 1 | 0 | 0 | 0.9 | 49.9445 | 11.8531 | 1.5004
Floor 3 Physical Therapy Toilet | 84 | Yes | 840 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.40041
Floor 3 Storage 1 | 108 | Yes | 1080 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 3 Storage 2 | 84 | Yes | 840 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 3 Treatment | 476 | Yes | 4760 | 1 | 0 | 0 | 1.5 | 49.9445 | 9.5306 | 1.1
Floor 3 Undeveloped 1 | 2268 | Yes | 22680 | 1 | 719.9979 | 275.9867 | 0.9 | 0 | 0 | 1.1
Floor 3 Undeveloped 2 | 1152 | Yes | 11520 | 1 | 560.0462 | 144.0211 | 0.9 | 0 | 0 | 1.1
Floor 3 Utility | 216 | Yes | 2160 | 1 | 0 | 0 | 0.9 | 0 | 0 | 0.10034
Floor 3 Work | 574 | Yes | 5740 | 1 | 409.9973 | 96.0141 | 1.1 | 199.9934 | 2.8701 | 1.1
NE Stair | 168 | Yes | 5040 | 1 | 1050.0194 | 129.3822 | 1 | 0 | 0 | 0.40041
NW Elevator | 140 | Yes | 4200 | 1 | 809.9842 | 0 | 1 | 0 | 0 | 0.40041
NW Stair | 192 | Yes | 5760 | 1 | 1199.9607 | 120.0176 | 1 | 0 | 0 | 0.40041
SW Stair | 96 | Yes | 2880 | 1 | 599.9803 | 11.9479 | 1 | 0 | 0 | 0.40041
TOTAL1 | 40946 |  | 421380 |  | 16719.4738 | 3318.2982 |  |  | 419.2826
AREA WEIGHTED AVERAGE | [6 empty] | 1.0942 | 59.4344 |  | 2.9733
1. Only volume, and gross wall area include unconditioned space.
2. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards

## Outdoor&Supply Air
Minimum Outdoor Ventilation Air Requirements
(Note that a lookup table under OA&SA Lookup is used to determined the outdoor and supply air rates.)
[5 empty] | Inputs for 90.1-2004 | [8 empty] | Inputs for 90.1-2007 and 90.1-2010
Zone | Zone Category | Area | Volume | Occupants | Total OSA Ventilation |  |  | Minimum Total Supply Air Rate | Minimum Total Exhaust Air Rate | Total OSA Ventilation | Minimum Total Supply Air Rate | Minimum Total Exhaust Air Rate | Number of Occupants | Total OSA Ventilation |  |  | Minimum Total Supply Air Rate | Minimum Total Exhaust Air Rate | Total OSA Ventilation | Minimum Total Supply Air Rate | Minimum Total Exhaust Air Rate | Number of Occupants
|  | [ft2] | [ft3] | [#/1000ft2] | [cfm/#] | [cfm/ft2] | [ach] | [ach] | [ach] | [cfm] | [cfm] | [cfm] |  | [cfm/#] | [cfm/ft2] | [ach] | [ach] | [ach] | [cfm] | [cfm] | [cfm] | Number of
Floor 1 Anesthesia | Anesthesia | 108 | 1080 | 20 | 15 | 0 | - | 8 | 8 | 32.4 | 144 | 144 | 2.16 | 15 | 0 | - | 8 | 8 | 32.4 | 144 | 144 | 2.16
Floor 1 Bio Haz | Storage | 56 | 560 | - | - | 0.15 | - | - | - | 8.4 | - | - | 0 | - | 0.12 | - | - | - | 6.72 | - | - | 0
Floor 1 Café | Dining | 420 | 4200 | 100 | 20 | 0 | - | - | - | 840 | - | - | 42 | 7.5 | 0.18 | - | - | - | 390.6 | - | - | 42
Floor 1 Clean | Clean | 126 | 1260 | 20 | 15 | 0 | - | 4 | - | 37.8 | 84 | - | 2.52 | 15 | 0 | - | 4 | - | 37.8 | 84 | - | 2.52
Floor 1 Clean Work | Clean | 165 | 1650 | 20 | 15 | 0 | - | 4 | - | 49.5 | 110 | - | 3.3 | 15 | 0 | - | 4 | - | 49.5 | 110 | - | 3.3
Floor 1 Dictation | Office | 126 | 1260 | 5 | 20 | 0 | - | - | - | 12.6 | - | - | 0.63 | 5 | 0.06 | - | - | - | 10.71 | - | - | 0.63
Floor 1 Dressing Room | Office | 45 | 450 | 5 | 20 | 0 | - | - | - | 4.5 | - | - | 0.225 | 5 | 0.06 | - | - | - | 3.825 | - | - | 0.225
Floor 1 Electrical Room | Utility | 98 | 980 | - | - | - | - | - | - | 0 | - | - | 0 | - | - | - | - | - | 0 | - | - | 0
Floor 1 Elevator Pump Room | Utility | 91 | 910 | - | - | - | - | - | - | 0 | - | - | 0 | - | - | - | - | - | 0 | - | - | 0
Floor 1 Humid | Office | 54 | 540 | 5 | 20 | 0 | - | - | - | 5.4 | - | - | 0.27 | 5 | 0.06 | - | - | - | 4.59 | - | - | 0.27
Floor 1 IT Hall | Corridor | 140 | 1400 | - | - | 0.05 | - | - | - | 7 | - | - | 0 | - | 0.06 | - | - | - | 8.4 | - | - | 0
Floor 1 IT Room | Office | 112 | 1120 | 5 | 20 | 0 | - | - | - | 11.2 | - | - | 0.56 | 5 | 0.06 | - | - | - | 9.52 | - | - | 0.56
Floor 1 Lobby | Lobby | 622 | 6220 | 10 | 15 | 0 | - | - | - | 93.3 | - | - | 6.22 | 5 | 0.06 | - | - | - | 68.42 | - | - | 6.22
Floor 1 Lobby Hall | Corridor | 240 | 2400 | - | - | 0.05 | - | - | - | 12 | - | - | 0 | - | 0.06 | - | - | - | 14.4 | - | - | 0
Floor 1 Lobby Toilet | Toilet room | 54 | 540 | - | - | - | - | 10 | 10 | 0 | 90 | 90 | 0 | - | - | - | 10 | 10 | 0 | 90 | 90 | 0
Floor 1 Locker Room | Lounge | 660 | 6600 | 15 | 15 | 0 | - | - | - | 148.5 | - | - | 9.9 | 5 | 0.06 | - | - | - | 89.1 | - | - | 9.9
Floor 1 Locker Room Hall | Corridor | 496 | 4960 | - | - | 0.05 | - | - | - | 24.8 | - | - | 0 | - | 0.06 | - | - | - | 29.76 | - | - | 0
Floor 1 Lounge | Lounge | 360 | 3600 | 15 | 15 | 0 | - | - | - | 81 | - | - | 5.4 | 5 | 0.06 | - | - | - | 48.6 | - | - | 5.4
Floor 1 Med Gas | Storage | 56 | 560 | - | - | 0.15 | - | - | - | 8.4 | - | - | 0 | - | 0.12 | - | - | - | 6.72 | - | - | 0
Floor 1 MRI Control Room | Radiology | 168 | 1680 | 20 | 15 | 0 | - | - | 12 | 50.4 | - | 336 | 3.36 | 15 | 0 | - | - | 12 | 50.4 | - | 336 | 3.36
Floor 1 MRI Hall | Corridor | 147 | 1470 | - | - | 0.05 | - | - | - | 7.35 | - | - | 0 | - | 0.06 | - | - | - | 8.82 | - | - | 0
Floor 1 MRI Room | Radiology | 440 | 4400 | 20 | 15 | 0 | - | - | 12 | 132 | - | 880 | 8.8 | 15 | 0 | - | - | 12 | 132 | - | 880 | 8.8
Floor 1 MRI Toilet | Toilet room | 54 | 540 | - | - | - | - | 10 | 10 | 0 | 90 | 90 | 0 | - | - | - | 10 | 10 | 0 | 90 | 90 | 0
Floor 1 Nourishment | Nurse Station | 182 | 1820 | 20 | 15 | 0 | - | - | - | 54.6 | - | - | 3.64 | 5 | 0.06 | - | - | - | 29.12 | - | - | 3.64
Floor 1 Nurse Hall | Corridor | 496 | 4960 | - | - | 0.05 | - | - | - | 24.8 | - | - | 0 | - | 0.06 | - | - | - | 29.76 | - | - | 0
Floor 1 Nurse Janitor | Storage | 54 | 540 | - | - | 0.15 | - | - | - | 8.1 | - | - | 0 | - | 0.12 | - | - | - | 6.48 | - | - | 0
Floor 1 Nurse Station | Nurse Station | 261 | 2610 | 20 | 15 | 0 | - | - | - | 78.3 | - | - | 5.22 | 5 | 0.06 | - | - | - | 41.76 | - | - | 5.22
Floor 1 Nurse Toilet | Toilet room | 54 | 540 | - | - | - | - | 10 | 10 | 0 | 90 | 90 | 0 | - | - | - | 10 | 10 | 0 | 90 | 90 | 0
Floor 1 Office | Office | 483 | 4830 | 5 | 20 | 0 | - | - | - | 48.3 | - | - | 2.415 | 5 | 0.06 | - | - | - | 41.055 | - | - | 2.415
Floor 1 Operating Room 1 | Operating room | 460 | 4600 | 20 | 30 | 0 | 3 | 20 | - | 506 | 1533.3333 | - | 9.2 | 30 | 0 | 3 | 20 | - | 506 | 1533.3333 | - | 9.2
Floor 1 Operating Room 2 | Operating room | 480 | 4800 | 20 | 30 | 0 | 3 | 20 | - | 528 | 1600 | - | 9.6 | 30 | 0 | 3 | 20 | - | 528 | 1600 | - | 9.6
Floor 1 Operating Room 3 | Operating room | 476 | 4760 | 20 | 30 | 0 | 3 | 20 | - | 523.6 | 1586.6667 | - | 9.52 | 30 | 0 | 3 | 20 | - | 523.6 | 1586.6667 | - | 9.52
Floor 1 PACU | Recovery room | 108 | 1080 | 20 | 15 | 0 | 2 | 6 | - | 68.4 | 108 | - | 2.16 | 15 | 0 | 2 | 6 | - | 68.4 | 108 | - | 2.16
Floor 1 Pre-Op Hall | Corridor | 528 | 5280 | - | - | 0.05 | - | - | - | 26.4 | - | - | 0 | - | 0.06 | - | - | - | 31.68 | - | - | 0
Floor 1 Pre-Op Room 1 | Patient room | 189 | 1890 | 10 | 25 | 0 | 2 | 6 | - | 110.25 | 189 | - | 1.89 | 25 | 0 | 2 | 6 | - | 110.25 | 189 | - | 1.89
Floor 1 Pre-Op Room 2 | Patient room | 338 | 3380 | 10 | 25 | 0 | 2 | 6 | - | 197.1667 | 338 | - | 3.38 | 25 | 0 | 2 | 6 | - | 197.1667 | 338 | - | 3.38
Floor 1 Pre-Op Toilet | Toilet room | 54 | 540 | - | - | - | - | 10 | 10 | 0 | 90 | 90 | 0 | - | - | - | 10 | 10 | 0 | 90 | 90 | 0
Floor 1 Procedure Room | Procedure room | 285 | 2850 | 20 | 15 | 0 | 3 | 15 | - | 228 | 712.5 | - | 5.7 | 15 | 0 | 3 | 15 | - | 228 | 712.5 | - | 5.7
Floor 1 Reception | Reception Area | 509 | 5090 | 30 | 15 | 0 | - | - | - | 229.05 | - | - | 15.27 | 5 | 0.06 | - | - | - | 106.89 | - | - | 15.27
Floor 1 Reception Hall | Corridor | 128 | 1280 | - | - | 0.05 | - | - | - | 6.4 | - | - | 0 | - | 0.06 | - | - | - | 7.68 | - | - | 0
Floor 1 Recovery Room | Recovery room | 540 | 5400 | 20 | 15 | 0 | 2 | 6 | - | 342 | 540 | - | 10.8 | 15 | 0 | 2 | 6 | - | 342 | 540 | - | 10.8
Floor 1 Scheduling | Office | 119 | 1190 | 5 | 20 | 0 | - | - | - | 11.9 | - | - | 0.595 | 5 | 0.06 | - | - | - | 10.115 | - | - | 0.595
Floor 1 Scrub | Corridor | 84 | 840 | - | - | 0.05 | - | - | - | 4.2 | - | - | 0 | - | 0.06 | - | - | - | 5.04 | - | - | 0
Floor 1 Soil | Soiled | 126 | 1260 | 20 | 15 | 0 | - | 10 | 10 | 37.8 | 210 | 210 | 2.52 | 15 | 0 | - | 10 | 10 | 37.8 | 210 | 210 | 2.52
Floor 1 Soil Hold | Soiled | 56 | 560 | 20 | 15 | 0 | - | 10 | 10 | 16.8 | 93.3333 | 93.3333 | 1.12 | 15 | 0 | - | 10 | 10 | 16.8 | 93.3333 | 93.3333 | 1.12
Floor 1 Soil Work | Soiled | 180 | 1800 | 20 | 15 | 0 | - | 10 | 10 | 54 | 300 | 300 | 3.6 | 15 | 0 | - | 10 | 10 | 54 | 300 | 300 | 3.6
Floor 1 Step Down | Recovery room | 300 | 3000 | 20 | 15 | 0 | 2 | 6 | - | 190 | 300 | - | 6 | 15 | 0 | 2 | 6 | - | 190 | 300 | - | 6
Floor 1 Sterile Hall | Corridor | 616 | 6160 | - | - | 0.05 | - | - | - | 30.8 | - | - | 0 | - | 0.06 | - | - | - | 36.96 | - | - | 0
Floor 1 Sterile Storage | Storage | 396 | 3960 | - | - | 0.15 | - | - | - | 59.4 | - | - | 0 | - | 0.12 | - | - | - | 47.52 | - | - | 0
Floor 1 Storage | Storage | 920 | 9200 | - | - | 0.15 | - | - | - | 138 | - | - | 0 | - | 0.12 | - | - | - | 110.4 | - | - | 0
Floor 1 Sub-Sterile | Corridor | 196 | 1960 | - | - | 0.05 | - | - | - | 9.8 | - | - | 0 | - | 0.06 | - | - | - | 11.76 | - | - | 0
Floor 1 Utility Hall | Corridor | 256 | 2560 | - | - | 0.05 | - | - | - | 12.8 | - | - | 0 | - | 0.06 | - | - | - | 15.36 | - | - | 0
Floor 1 Utility Janitor | Storage | 42 | 420 | - | - | 0.15 | - | - | - | 6.3 | - | - | 0 | - | 0.12 | - | - | - | 5.04 | - | - | 0
Floor 1 Utility Room | Storage | 360 | 3600 | - | - | 0.15 | - | - | - | 54 | - | - | 0 | - | 0.12 | - | - | - | 43.2 | - | - | 0
Floor 1 Vestibule | Corridor | 72 | 720 | - | - | 0.05 | - | - | - | 3.6 | - | - | 0 | - | 0.06 | - | - | - | 4.32 | - | - | 0
Floor 2 Conference | Conference | 336 | 3360 | 50 | 20 | 0 | - | - | - | 336 | - | - | 16.8 | 5 | 0.06 | - | - | - | 104.16 | - | - | 16.8
Floor 2 Conference Toilet | Toilet room | 64 | 640 | - | - | - | - | 10 | 10 | 0 | 106.6667 | 106.6667 | 0 | - | - | - | 10 | 10 | 0 | 106.6667 | 106.6667 | 0
Floor 2 Dictation | Office | 70 | 700 | 5 | 20 | 0 | - | - | - | 7 | - | - | 0.35 | 5 | 0.06 | - | - | - | 5.95 | - | - | 0.35
Floor 2 Exam 1 | Examination room | 360 | 3600 | 20 | 15 | 0 | - | 6 | - | 108 | 360 | - | 7.2 | 15 | 0 | - | 6 | - | 108 | 360 | - | 7.2
Floor 2 Exam 2 | Examination room | 540 | 5400 | 20 | 15 | 0 | - | 6 | - | 162 | 540 | - | 10.8 | 15 | 0 | - | 6 | - | 162 | 540 | - | 10.8
Floor 2 Exam 3 | Examination room | 720 | 7200 | 20 | 15 | 0 | - | 6 | - | 216 | 720 | - | 14.4 | 15 | 0 | - | 6 | - | 216 | 720 | - | 14.4
Floor 2 Exam 4 | Examination room | 84 | 840 | 20 | 15 | 0 | - | 6 | - | 25.2 | 84 | - | 1.68 | 15 | 0 | - | 6 | - | 25.2 | 84 | - | 1.68
Floor 2 Exam 5 | Examination room | 350 | 3500 | 20 | 15 | 0 | - | 6 | - | 105 | 350 | - | 7 | 15 | 0 | - | 6 | - | 105 | 350 | - | 7
Floor 2 Exam 6 | Examination room | 225 | 2250 | 20 | 15 | 0 | - | 6 | - | 67.5 | 225 | - | 4.5 | 15 | 0 | - | 6 | - | 67.5 | 225 | - | 4.5
Floor 2 Exam 7 | Examination room | 792 | 7920 | 20 | 15 | 0 | - | 6 | - | 237.6 | 792 | - | 15.84 | 15 | 0 | - | 6 | - | 237.6 | 792 | - | 15.84
Floor 2 Exam 8 | Examination room | 270 | 2700 | 20 | 15 | 0 | - | 6 | - | 81 | 270 | - | 5.4 | 15 | 0 | - | 6 | - | 81 | 270 | - | 5.4
Floor 2 Exam 9 | Examination room | 396 | 3960 | 20 | 15 | 0 | - | 6 | - | 118.8 | 396 | - | 7.92 | 15 | 0 | - | 6 | - | 118.8 | 396 | - | 7.92
Floor 2 Exam Hall 1 | Corridor | 180 | 1800 | - | - | 0.05 | - | - | - | 9 | - | - | 0 | - | 0.06 | - | - | - | 10.8 | - | - | 0
Floor 2 Exam Hall 2 | Corridor | 180 | 1800 | - | - | 0.05 | - | - | - | 9 | - | - | 0 | - | 0.06 | - | - | - | 10.8 | - | - | 0
Floor 2 Exam Hall 3 | Corridor | 180 | 1800 | - | - | 0.05 | - | - | - | 9 | - | - | 0 | - | 0.06 | - | - | - | 10.8 | - | - | 0
Floor 2 Exam Hall 4 | Corridor | 198 | 1980 | - | - | 0.05 | - | - | - | 9.9 | - | - | 0 | - | 0.06 | - | - | - | 11.88 | - | - | 0
Floor 2 Exam Hall 5 | Corridor | 198 | 1980 | - | - | 0.05 | - | - | - | 9.9 | - | - | 0 | - | 0.06 | - | - | - | 11.88 | - | - | 0
Floor 2 Exam Hall 6 | Corridor | 198 | 1980 | - | - | 0.05 | - | - | - | 9.9 | - | - | 0 | - | 0.06 | - | - | - | 11.88 | - | - | 0
Floor 2 Janitor | Storage | 63 | 630 | - | - | 0.15 | - | - | - | 9.45 | - | - | 0 | - | 0.12 | - | - | - | 7.56 | - | - | 0
Floor 2 Lounge | Lounge | 80 | 800 | 15 | 15 | 0 | - | - | - | 18 | - | - | 1.2 | 5 | 0.06 | - | - | - | 10.8 | - | - | 1.2
Floor 2 Nurse Station 1 | Nurse station | 150 | 1500 | 20 | 15 | 0 | - | - | - | 45 | - | - | 3 | 5 | 0.06 | - | - | - | 24 | - | - | 3
Floor 2 Nurse Station 2 | Nurse station | 180 | 1800 | 20 | 15 | 0 | - | - | - | 54 | - | - | 3.6 | 5 | 0.06 | - | - | - | 28.8 | - | - | 3.6
Floor 2 Office | Office | 560 | 5600 | 5 | 20 | 0 | - | - | - | 56 | - | - | 2.8 | 5 | 0.06 | - | - | - | 47.6 | - | - | 2.8
Floor 2 Office Hall | Corridor | 444 | 4440 | - | - | 0.05 | - | - | - | 22.2 | - | - | 0 | - | 0.06 | - | - | - | 26.64 | - | - | 0
Floor 2 Reception | Reception area | 984 | 9840 | 30 | 15 | 0 | - | - | - | 442.8 | - | - | 29.52 | 5 | 0.06 | - | - | - | 206.64 | - | - | 29.52
Floor 2 Reception Hall | Corridor | 564 | 5640 | - | - | 0.05 | - | - | - | 28.2 | - | - | 0 | - | 0.06 | - | - | - | 33.84 | - | - | 0
Floor 2 Reception Toilet | Toilet room | 126 | 1260 | - | - | - | - | 10 | 10 | 0 | 210 | 210 | 0 | - | - | - | 10 | 10 | 0 | 210 | 210 | 0
Floor 2 Scheduling 1 | Office | 324 | 3240 | 5 | 20 | 0 | - | - | - | 32.4 | - | - | 1.62 | 5 | 0.06 | - | - | - | 27.54 | - | - | 1.62
Floor 2 Scheduling 2 | Office | 342 | 3420 | 5 | 20 | 0 | - | - | - | 34.2 | - | - | 1.71 | 5 | 0.06 | - | - | - | 29.07 | - | - | 1.71
Floor 2 Storage 1 | Storage | 56 | 560 | - | - | 0.15 | - | - | - | 8.4 | - | - | 0 | - | 0.12 | - | - | - | 6.72 | - | - | 0
Floor 2 Storage 2 | Storage | 120 | 1200 | - | - | 0.15 | - | - | - | 18 | - | - | 0 | - | 0.12 | - | - | - | 14.4 | - | - | 0
Floor 2 Storage 3 | Storage | 144 | 1440 | - | - | 0.15 | - | - | - | 21.6 | - | - | 0 | - | 0.12 | - | - | - | 17.28 | - | - | 0
Floor 2 Utility | Storage | 126 | 1260 | - | - | 0.15 | - | - | - | 18.9 | - | - | 0 | - | 0.12 | - | - | - | 15.12 | - | - | 0
Floor 2 Work | Office | 1690 | 16900 | 5 | 20 | 0 | - | - | - | 169 | - | - | 8.45 | 5 | 0.06 | - | - | - | 143.65 | - | - | 8.45
Floor 2 Work Hall | Corridor | 834 | 8340 | - | - | 0.05 | - | - | - | 41.7 | - | - | 0 | - | 0.06 | - | - | - | 50.04 | - | - | 0
Floor 2 Work Toilet | Toilet room | 54 | 540 | - | - | - | - | 10 | 10 | 0 | 90 | 90 | 0 | - | - | - | 10 | 10 | 0 | 90 | 90 | 0
Floor 2 X-Ray | Radiology | 900 | 9000 | 20 | 15 | 0 | - | - | 12 | 270 | - | 1800 | 18 | 15 | 0 | - | - | 12 | 270 | - | 1800 | 18
Floor 3 Dressing Room | Office | 42 | 420 | 5 | 20 | 0 | - | - | - | 4.2 | - | - | 0.21 | 5 | 0.06 | - | - | - | 3.57 | - | - | 0.21
Floor 3 Elevator Hall | Corridor | 370 | 3700 | - | - | 0.05 | - | - | - | 18.5 | - | - | 0 | - | 0.06 | - | - | - | 22.2 | - | - | 0
Floor 3 Humid | Office | 108 | 1080 | 5 | 20 | 0 | - | - | - | 10.8 | - | - | 0.54 | 5 | 0.06 | - | - | - | 9.18 | - | - | 0.54
Floor 3 Janitor | Storage | 63 | 630 | - | - | 0.15 | - | - | - | 9.45 | - | - | 0 | - | 0.12 | - | - | - | 7.56 | - | - | 0
Floor 3 Locker | Lounge | 120 | 1200 | 15 | 15 | 0 | - | - | - | 27 | - | - | 1.8 | 5 | 0.06 | - | - | - | 16.2 | - | - | 1.8
Floor 3 Lounge | Lounge | 759 | 7590 | 15 | 15 | 0 | - | - | - | 170.775 | - | - | 11.385 | 5 | 0.06 | - | - | - | 102.465 | - | - | 11.385
Floor 3 Lounge Toilet | Toilet room | 192 | 1920 | - | - | - | - | 10 | 10 | 0 | 320 | 320 | 0 | - | - | - | 10 | 10 | 0 | 320 | 320 | 0
Floor 3 Mechanical | Utility | 350 | 3500 | - | - | - | - | - | - | 0 | - | - | 0 | - | - | - | - | - | 0 | - | - | 0
Floor 3 Mechanical Hall | Corridor | 300 | 3000 | - | - | 0.05 | - | - | - | 15 | - | - | 0 | - | 0.06 | - | - | - | 18 | - | - | 0
Floor 3 Office | Office | 3036 | 30360 | 5 | 20 | 0 | - | - | - | 303.6 | - | - | 15.18 | 5 | 0.06 | - | - | - | 258.06 | - | - | 15.18
Floor 3 Office Hall | Corridor | 834 | 8340 | - | - | 0.05 | - | - | - | 41.7 | - | - | 0 | - | 0.06 | - | - | - | 50.04 | - | - | 0
Floor 3 Office Toilet | Toilet room | 54 | 540 | - | - | - | - | 10 | 10 | 0 | 90 | 90 | 0 | - | - | - | 10 | 10 | 0 | 90 | 90 | 0
Floor 3 Physical Therapy 1 | Physical therapy | 1300 | 13000 | 20 | 15 | 0 | - | 6 | - | 390 | 1300 | - | 26 | 15 | 0 | - | 6 | - | 390 | 1300 | - | 26
Floor 3 Physical Therapy 2 | Physical therapy | 592 | 5920 | 20 | 15 | 0 | - | 6 | - | 177.6 | 592 | - | 11.84 | 15 | 0 | - | 6 | - | 177.6 | 592 | - | 11.84
Floor 3 Physical Therapy Toilet | Toilet room | 84 | 840 | - | - | - | - | 10 | 10 | 0 | 140 | 140 | 0 | - | - | - | 10 | 10 | 0 | 140 | 140 | 0
Floor 3 Storage 1 | Storage | 108 | 1080 | - | - | 0.15 | - | - | - | 16.2 | - | - | 0 | - | 0.12 | - | - | - | 12.96 | - | - | 0
Floor 3 Storage 2 | Storage | 84 | 840 | - | - | 0.15 | - | - | - | 12.6 | - | - | 0 | - | 0.12 | - | - | - | 10.08 | - | - | 0
Floor 3 Treatment | Examination room | 476 | 4760 | 20 | 15 | 0 | - | 6 | - | 142.8 | 476 | - | 9.52 | 15 | 0 | - | 6 | - | 142.8 | 476 | - | 9.52
Floor 3 Undeveloped 1 | Storage | 2268 | 22680 | - | - | 0.15 | - | - | - | 340.2 | - | - | 0 | - | 0.12 | - | - | - | 272.16 | - | - | 0
Floor 3 Undeveloped 2 | Storage | 1152 | 11520 | - | - | 0.15 | - | - | - | 172.8 | - | - | 0 | - | 0.12 | - | - | - | 138.24 | - | - | 0
Floor 3 Utility | Storage | 216 | 2160 | - | - | 0.15 | - | - | - | 32.4 | - | - | 0 | - | 0.12 | - | - | - | 25.92 | - | - | 0
Floor 3 Work | Office | 574 | 5740 | 5 | 20 | 0 | - | - | - | 57.4 | - | - | 2.87 | 5 | 0.06 | - | - | - | 48.79 | - | - | 2.87
NE Stair | Corridor | 168 | 5040 | - | - | 0.05 | - | - | - | 8.4 | - | - | 0 | - | 0.06 | - | - | - | 10.08 | - | - | 0
NW Elevator | Corridor | 140 | 4200 | - | - | 0.05 | - | - | - | 7 | - | - | 0 | - | 0.06 | - | - | - | 8.4 | - | - | 0
NW Stair | Corridor | 192 | 5760 | - | - | 0.05 | - | - | - | 9.6 | - | - | 0 | - | 0.06 | - | - | - | 11.52 | - | - | 0
SW Stair | Corridor | 96 | 2880 | - | - | 0.05 | - | - | - | 4.8 | - | - | 0 | - | 0.06 | - | - | - | 5.76 | - | - | 0
Total | [9 empty] | 9958.7917 |  |  | 419.11 | [5 empty] | 8388.9767 | 15270.5 |  | 419.11
Changed based on input from NREL
Input from NREL
1. The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1 or International Mechanical Code

## OA&SA Lookup
Zone Model Inputs (Use for 90.1-2004 Standard) | [8 empty] | Use for 90.1-2007 and 90.1-2010 Standard
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
ZONE CATEGORY | AIA | Occupants | ASHRAE 62-1999 OA |  | AIA OA C | AIA TOTAL AIR C | AIA EXH C | 90.1 Space Category | ASHRAE 62.1-2004 OA
| [y/n] | [#/1000ft2] | [cfm/#] | [cfm/ft2] | [ach] | [ach] | [ach] |  | [cfm/#] | [cfm/ft2]
Anesthesia | y | 20 | 15 | 0 | - | 8 | 8 | Exam/treatment | 15 | 0
Clean | y | 20 | 15 | 0 | - | 4 | - | Exam/treatment | 15 | 0
Conference | n | 50 | 20 | 0 | - | - | - | Conference/Meeting/Mutlipurpose | 5 | 0.06
Corridor | y | - | - | 0.05 | - | - | - | Corridor for Hospital | - | 0.06
Dining | n | 100 | 20 | 0 | - | - | - | Dining Area | 7.5 | 0.18
Emergency room | y | 20 | 15 | 0 | - | 6 | - | Emergency | 15 | 0
Examination room | y | 20 | 15 | 0 | - | 6 | - | Exam/treatment | 15 | 0
Food preparation center | y | 15 | 15 | 0 | - | 10 | - | Food Preparation | - | 0.7
Laboratory | y | 25 | 20 | 0 | - | 6 | - | Laboratory | 10 | 0.18
Lobby | n | 10 | 15 | 0 | - | - | - | Lobby | 5 | 0.06
Lounge | n | 15 | 15 | 0 | - | - | - | Lounge for Hospital | 5 | 0.06
Nurse station | n | 20 | 15 | 0 | - | - | - | Nurse Station | 5 | 0.06
Nursery | y | 20 | - | - | 2 | 6 | - | Nursey | - | -
Office | n | 5 | 20 | 0 | - | - | - | Office | 5 | 0.06
Operating room | y | 20 | 30 | 0 | 3 | 20 | - | Operating Room | 30 | 0
Patient corridor | y | - | - | 0.05 | - | 2 | - | Corridor for Hospital | - | 0.06
Patient room | y | 10 | 25 | 0 | 2 | 6 | - | Patient Room | 25 | 0
Pharmacy | y | 10 | 15 | 0 | - | 4 | - | Pharmacy | 5 | 0.18
Physical therapy | y | 20 | 15 | 0 | - | 6 | - | Physical Therapy | 15 | 0
Procedure room | y | 20 | 15 | 0 | 3 | 15 | - | Emergency | 15 | 0
Radiology | y | 20 | 15 | 0 | - | - | 12 | Radiology | 15 | 0
Reception area | n | 30 | 15 | 0 | - | - | - | Lobby | 5 | 0.06
Recovery room | y | 20 | 15 | 0 | 2 | 6 | - | Recovery | 15 | 0
Soiled | y | 20 | 15 | 0 | - | 10 | 10 | Exam/treatment | 15 | 0
Storage | n | - | - | 0.15 | - | - | - | Active Storage for Hospital | - | 0.12
Toilet room | y | - | - | - | - | 10 | 10 | Restrooms | - | -
Trauma room | y | 20 | 15 | 0 | 3 | 15 | - | Exam/treatment | 15 | 0
Triage | y | 20 | 15 | 0 | 2 | 12 | 12 | Emergency | 15 | 0
Utility | n | - | - | - | - | - | - | Electrical/Mechanical | - | -
[A] ASHRAE Small Health Care AEDG
[B] Ian (2007 Green Guide for Health Care Table OCC-1 & Table P-1)
[C] AIA 2006 Guidelines for Design and Construction of Health Care Facilities Table 2.1-2

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
Critical Light Schedule | Fraction | Through 12/31 | All Days | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | Critical Light Schedule All Days
|  |  | Winter Design Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Critical Light Schedule Winter Design Day
|  |  | Summer Design Day | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | Critical Light Schedule Summer Design Day
Admin Light Schedule | Fraction | Through 12/31 | Weekdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | Admin Light Schedule Weekdays
|  |  | Saturdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | Admin Light Schedule Saturdays
|  |  | Summer Design Day | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | Admin Light Schedule Summer Design Day
|  |  | Winter Design Day | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | Admin Light Schedule Winter Design Day
|  |  | Sundays, Holidays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | Admin Light Schedule Sundays, Holidays
Critical Equip Schedule | Fraction | Through 12/31 | All Days | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | Critical Equip Schedule All Days
|  |  | Winter Design Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Critical Equip Schedule Winter Design Day
|  |  | Summer Design Day | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | Critical Equip Schedule Summer Design Day
Admin Equip Schedule | Fraction | Through 12/31 | Weekdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Admin Equip Schedule Weekdays
|  |  | Saturdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Admin Equip Schedule Saturdays
|  |  | Summer Design Day | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Admin Equip Schedule Summer Design Day
|  |  | Winter Design Day | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | Admin Equip Schedule Winter Design Day
|  |  | Sundays, Holidays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Admin Equip Schedule Sundays, Holidays
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | 0
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [12 empty] | 0 | bar: 1 pm to 12 pm
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
Critical Occ Schedule | Fraction | Through 12/31 | All Days | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | Critical Occ Schedule All Days
|  |  | Winter Design Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Critical Occ Schedule Winter Design Day
|  |  | Summer Design Day | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | Critical Occ Schedule Summer Design Day
Admin Occ Schedule | Fraction | Through 12/31 | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | Admin Occ Schedule Weekdays
|  |  | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | Admin Occ Schedule Saturdays
|  |  | Summer Design Day | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | Admin Occ Schedule Summer Design Day
|  |  | Winter Design Day | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | Admin Occ Schedule Winter Design Day
|  |  | Sundays, Holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Admin Occ Schedule Sundays, Holidays
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | Weekdays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
|  |  | Saturdays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
|  |  | Summer Design Day | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
|  |  | Winter Design Day | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
|  |  | Sundays, Holidays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Infiltration Schedule
INFIL_SCH | fraction | Through 12/31 | WD, Saturdays | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Summer Design Day | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Summer Design Day | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Winter Design Day | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HVAC Schedules
Critical Heating Schedule | Temperature | Through 12/31 | All Days | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Critical Heating Schedule All Days
|  |  | Winter Design Day | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Critical Heating Schedule Winter Design Day
|  |  | Summer Design Day | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Critical Heating Schedule Summer Design Day
Critical Cooling Schedule | Temperature | Through 12/31 | All Days | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | Critical Cooling Schedule All Days
|  |  | Winter Design Day | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | Critical Cooling Schedule Winter Design Day
|  |  | Summer Design Day | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | Critical Cooling Schedule Summer Design Day
OR Heating Schedule | Temperature | Through 12/31 | All Days | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | OR Heating Schedule All Days
|  |  | Winter Design Day | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | OR Heating Schedule Winter Design Day
|  |  | Summer Design Day | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | OR Heating Schedule Summer Design Day
OR Cooling Schedule | Temperature | Through 12/31 | All Days | 72 | 72 | 72 | 72 | 72 | 72 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | OR Cooling Schedule All Days
|  |  | Winter Design Day | 72 | 72 | 72 | 72 | 72 | 72 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | OR Cooling Schedule Winter Design Day
|  |  | Summer Design Day | 72 | 72 | 72 | 72 | 72 | 72 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | OR Cooling Schedule Summer Design Day
Admin Heating Schedule* | Temperature | Through 12/31 | Weekdays | 64.94 | 66.92 | 68 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | Admin Heating Schedule* Weekdays
|  |  | Saturdays | 64.94 | 66.92 | 68 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | Admin Heating Schedule* Saturdays
|  |  | Summer Design Day | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | Admin Heating Schedule* Summer Design Day
|  |  | Winter Design Day | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | Admin Heating Schedule* Winter Design Day
|  |  | Sundays, Holidays | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | 64.94 | Admin Heating Schedule* Sundays, Holidays
Admin Cooling Schedule* | Temperature | Through 12/31 | Weekdays | 77 | 77 | 77 | 77 | 77 | 77 | 75.02 | 73.94 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 77 | 77 | 77 | 77 | 77 | 77 | Admin Cooling Schedule* Weekdays
|  |  | Saturdays | 77 | 77 | 77 | 77 | 77 | 77 | 75.02 | 73.94 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 77 | 77 | 77 | 77 | 77 | 77 | Admin Cooling Schedule* Saturdays
|  |  | Summer Design Day | 77 | 77 | 77 | 77 | 77 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 77 | 77 | 77 | 77 | 77 | 77 | Admin Cooling Schedule* Summer Design Day
|  |  | Winter Design Day | 77 | 77 | 77 | 77 | 77 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 71.96 | 77 | 77 | 77 | 77 | 77 | 77 | Admin Cooling Schedule* Winter Design Day
|  |  | Sundays, Holidays | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | Admin Cooling Schedule* Sundays, Holidays
HVACOperationSchd | Fraction | Through 12/31 | Weekdays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
(AHU-1 Fan; AHU-2 Fan) |  |  | Saturdays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Summer Design Day | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Winter Design Day | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sundays, Holidays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
Hours_of_operation | Fraction | Through 12/31 | Weekdays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
(Exhaust Fans) |  |  | Saturdays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Summer Design Day | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Winter Design Day | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Sundays, Holidays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
BLDG_OA_SCH | Fraction | Through 12/31 | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Summer Design Day | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Winter Design Day | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sundays, Holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OR_MinSA_Sched | Fraction | Through 12/31 | Weekdays | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Saturdays | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Summer Design Day | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: 1 pm to 12 pm
|  |  | Winter Design Day | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sundays, Holidays | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
*Notes: | 1. For climate zones other than 1B, 2B, and 3B occupied cooling thermostat setpoints are maintained continuously (no setback). 2. These schedules reflect optimum start controls. For systems less than 10,000 cfm there is no optimal start and full occupied temperature setpoints begin two hours prior to occupancy instead of being ramped up incrementally beginning two hours prior to occupancy. 3. The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.

## BremenInfo (hidden)
[6 empty] | AIA 7.2 | AIA 7.2 | IMC 403.3 | IMC 403.3 | HAP Calc | IMC Calc | MIN | HAP Calc
|  |  | [ft2] | [ft] | [ft3] | [ach] | [ach] | [occ/1000ft2] | [cfm/occ] | [occ] | [occ] | [occ] | [btuh]
| ROOM NAME | ZONE CATEGORY | AREA | CEILING | VOLUME | TOTAL AIR | OA AIR | OCCUPANTS | OA PER OCC | OCCUPANTS | OCCUPANTS | OCCUPANTS | SEN CLG LOAD | Room # | AHU #
1 | 001 Vestibule |  | 193 | 9 | 1737 |  |  |  |  | 0 | 0 | 0 | 11800 | 001 | 1
2 | 002 Corridor |  | 1015 | 9 | 9135 | 2 |  |  | 0.05 | 0 | 0 | 0 | 10200 | 002 | 1
3 | 005 Waiting |  | 695 | 9 | 6255 |  |  | 60 | 20 | 20 | 41.7 | 20 | 21600 | 005 | 1
4 | 006 Corridor |  | 780 | 9 | 7020 | 2 |  |  | 0.05 | 0 | 0 | 0 | 7800 | 006 | 2
5 | 008 Corridor |  | 544 | 9 | 4896 | 2 |  |  | 0.05 | 0 | 0 | 0 | 5400 | 008 | 3
6 | 009 Vestibule |  | 72 | 9 | 648 |  |  |  | 0.05 | 0 | 0 | 0 | 7800 | 009 | 3
7 | 010 Corridor |  | 736 | 9 | 6624 | 2 |  |  | 0.05 | 0 | 0 | 0 | 7400 | 010 | 3
8 | 011 Vestibule |  | 72 | 9 | 648 |  |  |  | 0.05 | 0 | 0 | 0 | 7300 | 011 | 3
9 | 012 Corridor |  | 396 | 9 | 3564 | 2 |  |  | 0.05 | 0 | 0 | 0 | 4000 | 012 | 3
10 | 013 Corridor |  | 235 | 9 | 2115 | 2 |  |  | 0.05 | 0 | 0 | 0 | 2400 | 013 | 3
11 | 014 Corridor |  | 172 | 9 | 1548 | 2 |  |  | 0.05 | 0 | 0 | 0 | 1300 | 014 | 3
12 | 015 Corridor |  | 770 | 9 | 6930 | 2 |  |  | 0.05 | 0 | 0 | 0 | 10800 | 015 | 2
13 | 016 Vestibule |  | 85 | 9 | 765 |  |  |  | 0.05 | 0 | 0 | 0 | 5400 | 016 | 4
14 | 017 Corridor |  | 1210 | 9 | 10890 | 2 |  |  | 0.05 | 0 | 0 | 0 | 12100 | 017 | 2
15 | 018 Corridor |  | 635 | 9 | 5715 | 2 |  |  | 0.05 | 0 | 0 | 0 | 9900 | 018 | 2
16 | 019 Vestiblue |  | 200 | 9 | 1800 |  |  |  | 0.05 | 0 | 0 | 0 | 3100 | 019 | 1
17 | 020 Corridor (east) |  | 670 | 9 | 6030 | 2 |  |  | 0.05 | 0 | 0 | 0 | 6700 | 020 | 1
18 | 020 Corridor (west) |  | 865 | 9 | 7785 | 2 |  |  | 0.05 | 0 | 0 | 0 | 8700 | 020 | 2
19 | 021 Vestibule |  | 125 | 9 | 1125 |  |  |  | 0.05 | 0 | 0 | 0 | 5300 | 021 | 1
20 | 100 Control |  | 66 | 9 | 594 |  |  | 20 | 15 | 1 | 1.32 | 1 | 1100 | 100 | 3
21 | 101 Sleep Lab |  | 132 | 9 | 1188 | 10 | 2 | 20 | 15 | 1 | 2.64 | 1 | 3800 | 101 | 3
22 | 102 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 102 | 3
23 | 103 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 4300 | 103 | 3
24 | 104 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 104 | 3
25 | 105 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 4300 | 105 | 3
26 | 106 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 106 | 3
27 | 107 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 4300 | 107 | 3
28 | 108 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 108 | 3
29 | 109 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 4300 | 109 | 3
30 | 110 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 110 | 3
31 | 111 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 4300 | 111 | 3
32 | 112 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 112 | 3
33 | 113 Clean Supply |  | 108 | 9 | 972 | 4 |  |  | 0.15 | 0 | 0 | 0 | 1100 | 113 | 3
34 | 114 Report |  | 118 | 9 | 1062 |  |  | 7 | 20 | 1 | 0.826 | 0.826 | 4000 | 114 | 3
35 | 115 Nurse Sta./Corr. |  | 1226 | 9 | 11034 | 2 |  | 7 | 20 | 9 | 8.582 | 8.582 | 17100 | 115 | 3
36 | 116 Meds |  | 123 | 9 | 1107 | 4 |  |  | 20 | 1 | 0 | 0 | 1200 | 116 | 3
37 | 117 Equip. |  | 80 | 9 | 720 |  |  |  | 0.15 | 0 | 0 | 0 | 800 | 117 | 3
38 | 118 Med/Surg/OB Dir. |  | 91 | 9 | 819 |  |  | 7 | 20 | 3 | 0.637 | 0.637 | 2300 | 118 | 3
39 | 119 Waiting Med/Surg. |  | 322 | 9 | 2898 | 12 | 2 | 60 | 15 | 12 | 19.32 | 12 | 8300 | 119 | 3
40 | 120 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 5400 | 120 | 3
41 | 121 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 121 | 3
42 | 122 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 6900 | 122 | 3
43 | 123 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 123 | 3
44 | 124 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 6900 | 124 | 3
45 | 125 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 125 | 3
46 | 126 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 6900 | 126 | 3
47 | 127 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 127 | 3
48 | 128 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7800 | 128 | 3
49 | 129 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 129 | 3
50 | 130 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7700 | 130 | 3
51 | 131 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 131 | 3
52 | 132 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7700 | 132 | 3
53 | 133 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 133 | 3
54 | 134 Equip Alcove |  | 40 | 9 | 360 | 10 |  |  | 25 | 0 | 0 | 0 | 400 | 134 | 3
55 | 135 Soiled Utility |  | 90 | 9 | 810 | 10 |  |  | 0.15 | 0 | 0 | 0 | 900 | 135 | 3
56 | 136 Adl Kitchen |  | 129 | 9 | 1161 | 10 |  | 20 | 15 | 3 | 2.58 | 2.58 | 5200 | 136 | 3
57 | 137 toilet Adl |  | 91 | 9 | 819 | 10 |  |  | 75 | 0 | 0 | 0 | 900 | 137 | 3
58 | 138 Patient Room |  | 256 | 9 | 2304 | 6 | 2 | 10 | 25 | 1 | 2.56 | 1 | 8300 | 138 | 3
59 | 139 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 139 | 3
60 | 140 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7900 | 140 | 3
61 | 141 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 141 | 3
62 | 142 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7900 | 142 | 3
63 | 143 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 143 | 3
64 | 144 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7900 | 144 | 3
65 | 145 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 145 | 3
66 | 146 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7900 | 146 | 3
67 | 147 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 147 | 3
68 | 148 Patient Room |  | 210 | 9 | 1890 | 6 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7900 | 148 | 3
69 | 149 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 149 | 3
70 | 150 Ante |  | 66 | 9 | 594 | 10 |  | 7 | 20 | 1 | 0.462 | 0.462 | 900 | 150 | 3
71 | 151 Patient Iso. Room |  | 210 | 9 | 1890 | 12 | 2 | 10 | 25 | 1 | 2.1 | 1 | 7900 | 151 | 3
72 | 152 Toilet |  | 48 | 9 | 432 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 152 | 3
73 | 200 Hall |  | 515 | 9 | 4635 | 2 |  |  | 0.05 | 0 | 0 | 0 | 5200 | 200 | 3
74 | 201 Nurse Sta. |  | 140 | 9 | 1260 |  |  | 7 | 20 | 4 | 0.98 | 0.98 | 4200 | 201 | 3
75 | 202 Baby Holding |  | 160 | 9 | 1440 | 6 | 2 | 7 | 20 | 1 | 1.12 | 1 | 3300 | 202 | 3
76 | 203 Neonate Exam |  | 84 | 9 | 756 | 6 | 2 | 7 | 20 | 1 | 0.588 | 0.588 | 1800 | 203 | 3
77 | 204 Janitor Closet |  | 22 | 9 | 198 | 10 |  |  | 0.15 | 0 | 0 | 0 | 200 | 204 | 3
78 | 205 LDRP Iso. |  | 310 | 9 | 2790 | 12 | 2 | 10 | 25 | 1 | 3.1 | 1 | 8900 | 205 | 3
79 | 206 Toilet |  | 70 | 9 | 630 | 10 |  |  | 75 | 0 | 0 | 0 | 700 | 206 | 3
80 | 207 LDRP |  | 310 | 9 | 2790 | 15 | 2 | 10 | 25 | 1 | 3.1 | 1 | 8800 | 207 | 3
81 | 208 Toilet |  | 70 | 9 | 630 | 10 |  |  | 75 | 0 | 0 | 0 | 700 | 208 | 3
82 | 209 LDRP |  | 310 | 9 | 2790 | 15 | 2 | 10 | 25 | 1 | 3.1 | 1 | 8800 | 209 | 3
83 | 210 Toilet |  | 70 | 9 | 630 | 10 |  |  | 75 | 0 | 0 | 0 | 700 | 210 | 3
84 | 211 Test/Eval. |  | 118 | 9 | 1062 | 6 |  | 20 | 25 | 1 | 2.36 | 1 | 2400 | 211 | 3
85 | 212 Toilet |  | 54 | 9 | 486 | 10 |  |  | 75 | 0 | 0 | 0 | 600 | 212 | 3
86 | 213 Equip. Stor. |  | 74 | 9 | 666 |  |  |  | 0.15 | 0 | 0 | 0 | 700 | 213 | 3
87 | 214 Clean Supply |  | 74 | 9 | 666 | 4 |  |  | 0.15 | 0 | 0 | 0 | 700 | 214 | 3
88 | 215 Soiled Utility |  | 56 | 9 | 504 | 10 |  |  | 0.15 | 0 | 0 | 0 | 600 | 215 | 3
89 | 300 Hall |  | 70 | 9 | 630 | 2 |  |  | 0.05 | 0 | 0 | 0 | 700 | 300 | 3
90 | 301 Directors Office |  | 105 | 9 | 945 |  |  | 7 | 20 | 3 | 0.735 | 0.735 | 3100 | 301 | 3
91 | 302 Work Room |  | 502 | 9 | 4518 |  |  | 7 | 20 | 4 | 3.514 | 3.514 | 8900 | 302 | 3
92 | 304 Phys. Dict. |  | 34 | 9 | 306 |  |  | 7 | 20 | 3 | 0.238 | 0.238 | 2900 | 304 | 3
93 | 305 Phys. Lounge |  | 127 | 9 | 1143 |  |  | 70 | 20 | 9 | 8.89 | 8.89 | 5600 | 305 | 3
94 | 306 Toilet |  | 46 | 9 | 414 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 306 | 3
95 | 307 Staff Lounge |  | 155 | 9 | 1395 |  |  | 70 | 20 | 11 | 10.85 | 10.85 | 5900 | 307 | 3
96 | 308 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 308 | 3
97 | 310 Pharmacy |  | 384 | 9 | 3456 | 4 |  | 20 | 15 | 7 | 7.68 | 7 | 7100 | 310 | 3
98 | 311 Ante |  | 76 | 9 | 684 |  |  | 7 | 20 | 1 | 0.532 | 0.532 | 2200 | 311 | 3
99 | 312 IV Mix |  | 67 | 9 | 603 | 4 |  | 20 | 20 | 1 | 1.34 | 1 | 700 | 312 | 3
100 | 313 IV Bulk |  | 65 | 9 | 585 | 4 |  | 20 | 20 | 1 | 1.3 | 1 | 700 | 313 | 3
101 | 314 Office |  | 85 | 9 | 765 |  |  | 7 | 20 | 3 | 0.595 | 0.595 | 3700 | 314 | 3
102 | 315 Comm. Closet |  | 70 | 9 | 630 |  |  | 60 | 20 | 4 | 4.2 | 4 | 700 | 315 | 3
103 | 316 OB Waiting |  | 179 | 9 | 1611 |  |  | 60 | 15 | 11 | 10.74 | 10.74 | 4300 | 316 | 3
104 | 317 Mens Room |  | 150 | 9 | 1350 | 10 |  |  | 75 | 0 | 0 | 0 | 3400 | 317 | 3
105 | 318 Womens Room |  | 150 | 9 | 1350 | 10 |  |  | 75 | 0 | 0 | 0 | 3400 | 318 | 3
106 | 400 Hall |  | 220 | 9 | 1980 | 2 |  |  | 0.05 | 0 | 0 | 0 | 4300 | 400 | 4
107 | 401 Office |  | 100 | 9 | 900 |  |  | 7 | 20 | 1 | 0.7 | 0.7 | 2400 | 401 | 4
108 | 402 Office |  | 95 | 9 | 855 |  |  | 7 | 20 | 1 | 0.665 | 0.665 | 3900 | 402 | 4
109 | 403 Record Rm./Copier |  | 80 | 9 | 720 |  |  | 7 | 20 | 1 | 0.56 | 0.56 | 2700 | 403 | 4
110 | 404 Recv'r Office |  | 80 | 9 | 720 |  |  | 7 | 20 | 1 | 0.56 | 0.56 | 3500 | 404 | 4
111 | 405 Loading dock |  | 268 | 9 | 2412 |  |  |  | 0.15 | 0 | 0 | 0 | 3400 | 405 | 4
112 | 406 Cart Wash |  | 50 | 9 | 450 |  |  |  | 0.15 | 0 | 0 | 0 | 500 | 406 | 4
113 | 407 Bio Haz. |  | 65 | 9 | 585 | 10 |  | 20 | 0.5 | 1 | 1.3 | 1 | 800 | 407 | 4
114 | 408 Med Gas Stor. |  | 53 | 9 | 477 | 8 |  |  | 0.5 | 0 | 0 | 0 | 600 | 408 | 4
115 | 409 Bulk Stor. |  | 760 | 9 | 6840 |  |  |  | 0.15 | 0 | 0 | 0 | 7600 | 409 | 4
116 | 410 Hall |  | 235 | 9 | 2115 | 2 |  |  | 0.05 | 0 | 0 | 0 | 4300 | 410 | 4
117 | 411 Office IT Dir. |  | 110 | 9 | 990 |  |  | 7 | 20 | 1 | 0.77 | 0.77 | 2000 | 411 | 4
118 | 412 Storage |  | 70 | 9 | 630 |  |  |  | 0.15 | 0 | 0 | 0 | 700 | 412 | 4
119 | 413 Computer Room (Liebert) |  | 160 | 9 | 1440 |  |  | 7 | 20 | 1 | 1.12 | 1 | 4000 | 413 | 4
120 | 414 Locker / Lounge |  | 150 | 9 | 1350 |  |  |  | 0.5 | 0 | 0 | 0 | 6000 | 414 | 4
121 | 415 toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 415 | 4
122 | 416 Shower (staff) |  | 70 | 9 | 630 |  |  |  |  | 0 | 0 | 0 | 700 | 416 | 4
123 | 417 Storage |  | 490 | 9 | 4410 |  |  |  | 0.15 | 0 | 0 | 0 | 5000 | 417 | 4
124 | 418 Phone / Data |  | 187 | 9 | 1683 |  |  |  |  | 0 | 0 | 0 | 1900 | 418 | 4
125 | 419 Plant Manager |  | 90 | 9 | 810 |  |  | 7 | 20 | 1 | 0.63 | 0.63 | 2300 | 419 | 4
126 | 420 M.I.S. (Liebert) |  | 100 | 9 | 900 |  |  | 7 | 20 | 1 | 0.7 | 0.7 | 2400 | 420 | 4
127 | 421 Soiled Cart |  | 75 | 9 | 675 | 10 |  |  | 0.15 | 0 | 0 | 0 | 800 | 421 | 4
128 | 422 Hall |  | 85 | 9 | 765 | 2 |  |  | 0.05 | 0 | 0 | 0 | 900 | 422 | 4
129 | 423 Linen Storage |  | 210 | 9 | 1890 | 10 |  |  | 0.15 | 0 | 0 | 0 | 2100 | 423 | 4
130 | 424 Storage |  | 135 | 9 | 1215 |  |  |  | 0.15 | 0 | 0 | 0 | 1400 | 424 | 4
131 | 425 Office |  | 60 | 9 | 540 |  |  | 7 | 20 | 0 | 0.42 | 0 | 2000 | 425 | 2
132 | 500 Body Storage |  | 100 | 9 | 900 | 10 |  |  | 0.5 | 0 | 0 | 0 | 1000 | 500 | 2
133 | 501 X-Ray |  | 60 | 9 | 540 | 15 | 3 | 20 | 15 | 1 | 1.2 | 1 | 4500 | 501 | 2
134 | 502 Janitor |  | 50 | 9 | 450 | 10 |  |  | 0.15 | 0 | 0 | 0 | 500 | 502 | 2
135 | 503 Hall |  | 155 | 9 | 1395 | 2 |  |  | 0.05 | 0 | 0 | 0 | 1600 | 503 | 2
136 | 505 Women Toilet/Locker |  | 230 | 9 | 2070 | 10 |  |  | 0.5 | 0 | 0 | 0 | 2300 | 505 | 2
137 | 506 Womens Shower |  | 40 | 9 | 360 |  |  |  |  | 0 | 0 | 0 | 400 | 506 | 2
138 | 507 Mens Sleep Rm |  | 180 | 9 | 1620 | 6 |  | 20 | 15 | 4 | 3.6 | 3.6 | 2400 | 507 | 2
139 | 509 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 509 | 2
140 | 510 Mens Shower |  | 50 | 9 | 450 |  |  |  |  | 0 | 0 | 0 | 500 | 510 | 2
141 | 511 Lounge |  | 190 | 9 | 1710 |  |  | 70 | 20 | 13 | 13.3 | 13 | 5300 | 511 | 2
142 | 512 Sterile Hall |  | 750 | 9 | 6750 | 4 |  |  | 0.05 | 0 | 0 | 0 | 7500 | 512 | 2
143 | 513 Janitors Closet |  | 35 | 9 | 315 | 10 |  |  | 0.15 | 0 | 0 | 0 | 400 | 513 | 2
144 | 514 Endoscopy |  | 490 | 9 | 4410 | 15 | 2 | 20 | 15 | 10 | 9.8 | 9.8 | 8400 | 514 | 2
145 | 515 Scope |  | 115 | 9 | 1035 | 6 | 2 | 20 | 15 | 2 | 2.3 | 2 | 2100 | 515 | 2
146 | 516 Sterile Core |  | 480 | 9 | 4320 | 4 |  | 20 | 15 | 10 | 9.6 | 9.6 | 6300 | 516 | 2
147 | 517 O.R. #1 |  | 530 | 9 | 4770 | 20 | 3 | 20 | 30 | 11 | 10.6 | 10.6 | 8800 | 517 | 2
148 | 518 O.R. #2 |  | 490 | 9 | 4410 | 20 | 3 | 20 | 30 | 10 | 9.8 | 9.8 | 8400 | 518 | 2
149 | 519 Sterilizing |  | 135 | 9 | 1215 | 10 |  | 20 | 15 | 3 | 2.7 | 2.7 | 2300 | 519 | 2
150 | 520 Clean |  | 550 | 9 | 4950 | 4 |  |  | 0.15 | 0 | 0 | 0 | 9000 | 520 | 2
151 | 521 Decontamination |  | 345 | 9 | 3105 | 6 |  | 20 | 15 | 7 | 6.9 | 6.9 | 5100 | 521 | 2
152 | 523 Soiled Hold |  | 100 | 9 | 900 | 10 |  |  | 0.15 | 0 | 0 | 0 | 1000 | 523 | 2
153 | 524 Hall |  | 810 | 9 | 7290 | 2 |  |  | 0.05 | 0 | 0 | 0 | 8600 | 524 | 2
154 | 525 Hall |  | 155 | 9 | 1395 | 2 |  |  | 0.05 | 0 | 0 | 0 | 2000 | 525 | 2
155 | 526 PACU |  | 200 | 9 | 1800 | 15 | 3 | 7 | 20 | 1 | 1.4 | 1 | 3900 | 526 | 2
156 | 529 Nurse Station |  | 340 | 9 | 3060 |  |  | 7 | 20 | 2 | 2.38 | 2 | 6400 | 529 | 2
157 | 531 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 531 | 2
158 | 532 Equipment Storage |  | 125 | 9 | 1125 |  |  |  | 0.15 | 0 | 0 | 0 | 1300 | 532 | 2
159 | 533 Anesth. Work Rm. |  | 115 | 9 | 1035 |  |  | 7 | 20 | 1 | 0.805 | 0.805 | 2300 | 533 | 2
160 | 534 Hall |  | 105 | 9 | 945 | 2 |  |  | 0.05 | 0 | 0 | 0 | 2000 | 534 | 2
161 | 535 directors Office |  | 90 | 9 | 810 |  |  | 7 | 20 | 1 | 0.63 | 0.63 | 2100 | 535 | 2
162 | 536 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 536 | 2
163 | 537 Holding #7 |  | 110 | 9 | 990 | 10 |  | 10 | 20 | 1 | 1.1 | 1 | 1700 | 537 | 2
164 | 538 Locker |  | 50 | 9 | 450 |  |  |  | 0.5 | 0 | 0 | 0 | 500 | 538 | 2
165 | 539 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 539 | 2
166 | 540 Infect. Control |  | 80 | 9 | 720 | 10 |  | 10 | 20 | 1 | 0.8 | 0.8 | 2200 | 540 | 2
167 | 541 Clean Supply |  | 85 | 9 | 765 | 4 |  |  | 0.15 | 0 | 0 | 0 | 900 | 541 | 2
168 | 542 Pat. Bed #6 Iso |  | 110 | 9 | 990 | 12 | 2 | 10 | 25 | 1 | 1.1 | 1 | 1900 | 542 | 2
169 | 543 Pat Bed #5 |  | 110 | 9 | 990 | 6 | 2 | 10 | 25 | 1 | 1.1 | 1 | 1900 | 543 | 2
170 | 544 Pat Bed #4 |  | 110 | 9 | 990 | 6 | 2 | 10 | 25 | 1 | 1.1 | 1 | 1900 | 544 | 2
171 | 545 Pat Bed #3 |  | 110 | 9 | 990 | 6 | 2 | 10 | 25 | 1 | 1.1 | 1 | 1900 | 545 | 2
172 | 546 Pat Bed #2 |  | 110 | 9 | 990 | 6 | 2 | 10 | 25 | 1 | 1.1 | 1 | 1900 | 546 | 2
173 | 547 Pat Bed #1 |  | 110 | 9 | 990 | 6 | 2 | 10 | 25 | 1 | 1.1 | 1 | 1900 | 547 | 2
174 | 548 Consulting |  | 75 | 9 | 675 |  |  | 7 | 20 | 1 | 0.525 | 0.525 | 2000 | 548 | 2
175 | 549 Gift Shop |  | 365 | 9 | 3285 |  |  | 30 | 20 | 11 | 10.95 | 10.95 | 6400 | 549 | 2
176 | 550 Vol. Office |  | 80 | 9 | 720 |  |  | 7 | 220 | 1 | 0.56 | 0.56 | 1700 | 550 | 2
177 | 600 Waiting |  | 154 | 9 | 1386 | 12 | 2 | 60 | 15 | 9 | 9.24 | 9 | 2200 | 600 | 2
178 | 601 Hall |  | 80 | 9 | 720 | 2 |  |  | 0.05 | 0 | 0 | 0 | 800 | 601 | 2
179 | 602 lab |  | 1000 | 9 | 9000 | 6 |  | 7 | 20 | 7 | 7 | 7 | 19800 | 602 | 2
180 | 603 Storage |  | 70 | 9 | 630 |  |  |  | 0.15 | 0 | 0 | 0 | 700 | 603 | 2
181 | 605 Lab Director |  | 105 | 9 | 945 |  |  | 7 | 20 | 1 | 0.735 | 0.735 | 2500 | 605 | 2
182 | 606 Path. Director |  | 105 | 9 | 945 |  |  | 7 | 20 | 1 | 0.735 | 0.735 | 2500 | 606 | 2
183 | 607 Histology |  | 105 | 9 | 945 | 6 |  | 7 | 20 | 1 | 0.735 | 0.735 | 2500 | 607 | 2
184 | 608 Blood Bank |  | 75 | 9 | 675 | 6 |  | 7 | 15 | 1 | 0.525 | 0.525 | 1700 | 608 | 2
185 | 609 micro. |  | 130 | 9 | 1170 | 6 |  | 7 | 15 | 1 | 0.91 | 0.91 | 2200 | 609 | 2
186 | 610 Phleb. #1 |  | 105 | 9 | 945 |  |  | 7 | 15 | 1 | 0.735 | 0.735 | 5000 | 610 | 2
187 | 611 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 611 | 2
188 | 612 Phleb. #2 |  | 70 | 9 | 630 |  |  | 7 | 15 | 0 | 0.49 | 0 | 4600 | 612 | 2
189 | 613 Hall |  | 350 | 9 | 3150 | 2 |  |  | 0.05 | 0 | 0 | 0 | 3500 | 613 | 2
190 | 614 Hall |  | 120 | 9 | 1080 | 2 |  |  | 0.05 | 0 | 0 | 0 | 1200 | 614 | 2
191 | 615 Ultra. |  | 212 | 9 | 1908 | 6 |  | 20 | 20 | 4 | 4.24 | 4 | 6000 | 615 | 2
192 | 616 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 616 | 2
193 | 617 Waiting |  | 40 | 9 | 360 | 12 | 2 |  | 15 | 0 | 0 | 0 | 2000 | 617 | 2
194 | 618 Mamo. |  | 132 | 9 | 1188 | 6 |  | 20 | 15 | 3 | 2.64 | 2.64 | 5200 | 618 | 2
195 | 619 Locker |  | 65 | 9 | 585 |  |  |  | 0.5 | 0 | 0 | 0 | 900 | 619 | 2
196 | 620 Lounge |  | 95 | 9 | 855 |  |  | 70 | 20 | 7 | 6.65 | 6.65 | 4400 | 620 | 2
197 | 621 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 621 | 2
198 | 622 Transc. |  | 50 | 9 | 450 |  |  | 7 | 20 | 0 | 0.35 | 0 | 1400 | 622 | 2
199 | 623 Hall |  | 345 | 9 | 3105 | 2 |  |  | 0.05 | 0 | 0 | 0 | 3500 | 623 | 2
200 | 624 Soiled Holding |  | 55 | 9 | 495 | 10 |  |  | 0.15 | 0 | 0 | 0 | 2000 | 624 | 2
201 | 625 Sally Port |  | 225 | 9 | 2025 |  |  | 7 | 20 | 2 | 1.575 | 1.575 | 3100 | 625 | 2
202 | 626 Radiology Office |  | 140 | 9 | 1260 |  |  | 7 | 20 | 1 | 0.98 | 0.98 | 2600 | 626 | 2
203 | 627 Film Record Storage |  | 180 | 9 | 1620 |  |  | 7 | 20 | 1 | 1.26 | 1 | 1800 | 627 | 2
204 | 628 CT |  | 290 | 9 | 2610 | 6 |  | 20 | 15 | 6 | 5.8 | 5.8 | 6800 | 628 | 2
205 | 629 Control |  | 85 | 9 | 765 |  |  | 7 | 20 | 1 | 0.595 | 0.595 | 1800 | 629 | 2
206 | 630 Tech. Work Rm. |  | 140 | 9 | 1260 |  |  | 7 | 20 | 1 | 0.98 | 0.98 | 3300 | 630 | 2
207 | 631 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 631 | 2
208 | 632 Tomography |  | 225 | 9 | 2025 | 6 |  | 20 | 20 | 5 | 4.5 | 4.5 | 6200 | 632 | 2
209 | 634 Dark Room |  | 90 | 9 | 810 | 10 |  |  | 0.5 | 0 | 0 | 0 | 2900 | 634 | 2
210 | 635 Fluoroscopy |  | 275 | 9 | 2475 | 6 |  | 20 | 15 | 6 | 5.5 | 5.5 | 4600 | 635 | 2
211 | 637 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 637 | 2
212 | 638 Directors Office |  | 90 | 9 | 810 |  |  | 7 | 20 | 1 | 0.63 | 0.63 | 2100 | 638 | 2
213 | 639 DEXA |  | 100 | 9 | 900 | 6 |  | 7 | 20 | 1 | 0.7 | 0.7 | 1800 | 639 | 2
214 | 640 Recept./Work Area |  | 100 | 9 | 900 |  |  | 60 | 20 | 6 | 6 | 6 | 1900 | 640 | 1
215 | 641 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 641 | 1
216 | 642 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 642 | 1
217 | 643 Registration |  | 55 | 9 | 495 | 12 | 2 | 60 | 15 | 3 | 3.3 | 3 | 1700 | 643 | 1
218 | 644 Waiting |  | 75 | 9 | 675 | 12 | 2 | 60 | 15 | 5 | 4.5 | 4.5 | 2000 | 644 | 1
219 | 645 Reception |  | 70 | 9 | 630 | 12 | 2 | 60 | 15 | 4 | 4.2 | 4 | 2300 | 645 | 1
220 | 646 Hall |  | 80 | 9 | 720 | 12 | 2 |  | 0.05 | 0 | 0 | 0 | 800 | 646 | 1
221 | 647 Hall |  | 370 | 9 | 3330 | 12 | 2 |  | 0.05 | 0 | 0 | 0 | 3700 | 647 | 1
222 | 648 Exam #1 |  | 132 | 9 | 1188 | 6 |  | 20 | 15 | 3 | 2.64 | 2.64 | 2200 | 648 | 1
223 | 649 Exam #2 |  | 132 | 9 | 1188 | 6 |  | 20 | 15 | 3 | 2.64 | 2.64 | 2200 | 649 | 1
224 | 650 Exam #3 |  | 132 | 9 | 1188 | 12 | 2 | 20 | 15 | 3 | 2.64 | 2.64 | 2200 | 650 | 1
225 | 651 Nurse Station |  | 330 | 9 | 2970 |  |  | 7 | 20 | 2 | 2.31 | 2 | 6300 | 651 | 1
226 | 652 Hall |  | 525 | 9 | 4725 | 2 |  |  | 0.05 | 0 | 0 | 0 | 5300 | 652 | 1
227 | 653 Toilet |  | 65 | 9 | 585 | 10 |  |  | 75 | 0 | 0 | 0 | 700 | 653 | 1
228 | 654 Trauma |  | 288 | 9 | 2592 | 15 | 3 | 20 | 30 | 6 | 5.76 | 5.76 | 5400 | 654 | 1
229 | 656 Decontam. Equip. |  | 56 | 9 | 504 |  |  |  | 0.15 | 0 | 0 | 0 | 1800 | 656 | 1
230 | 657 EMS |  | 84 | 9 | 756 |  |  | 20 | 25 | 2 | 1.68 | 1.68 | 2100 | 657 | 1
231 | 658 Soiled Utility |  | 80 | 9 | 720 | 10 |  |  | 0.15 | 0 | 0 | 0 | 800 | 658 | 1
232 | 659 Procedure Room |  | 168 | 9 | 1512 | 15 | 3 | 20 | 15 | 3 | 3.36 | 3 | 5600 | 659 | 1
233 | 660 Hot Office |  | 153 | 9 | 1377 |  |  | 7 | 20 | 1 | 1.071 | 1 | 4900 | 660 | 1
234 | 661 Toilet/Shower |  | 70 | 9 | 630 | 10 |  |  | 75 | 0 | 0 | 0 | 700 | 661 | 1
235 | 662 On Call |  | 77 | 9 | 693 |  |  | 7 | 20 | 1 | 0.539 | 0.539 | 1800 | 662 | 1
236 | 663 Hall |  | 300 | 9 | 2700 | 2 |  |  | 0.05 | 0 | 0 | 0 | 3000 | 663 | 1
237 | 664 Directors Office |  | 116 | 9 | 1044 |  |  | 7 | 20 | 1 | 0.812 | 0.812 | 4000 | 664 | 1
238 | 665 Clean Supply |  | 120 | 9 | 1080 | 4 |  |  | 0.15 | 0 | 0 | 0 | 1200 | 665 | 1
239 | 666 Phys. Chart |  | 45 | 9 | 405 |  |  | 7 | 20 | 0 | 0.315 | 0 | 1600 | 666 | 1
240 | 667 Equipment |  | 132 | 9 | 1188 |  |  |  | 0.15 | 0 | 0 | 0 | 1500 | 667 | 1
241 | 669 Lounge |  | 220 | 9 | 1980 | 4 |  | 70 | 20 | 15 | 15.4 | 15 | 6900 | 669 | 1
242 | 670 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 670 | 1
243 | 671 Elec. Closet |  | 80 | 9 | 720 |  |  |  |  | 0 | 0 | 0 | 1500 | 671 | 1
244 | 672 Consult. |  | 85 | 9 | 765 |  |  | 7 | 20 | 1 | 0.595 | 0.595 | 2000 | 672 | 1
245 | 673 Triage |  | 80 | 9 | 720 | 12 | 2 | 7 | 20 | 1 | 0.56 | 0.56 | 2200 | 673 | 1
246 | 700 Waiting |  | 275 | 9 | 2475 | 12 | 2 | 60 | 15 | 17 | 16.5 | 16.5 | 6200 | 700 | 1
247 | 701 Hall |  | 183 | 9 | 1647 | 2 |  |  | 0.05 | 0 | 0 | 0 | 1800 | 701 | 1
248 | 702 Spec Collection |  | 90 | 9 | 810 | 12 |  | 7 | 20 | 1 | 0.63 | 0.63 | 1700 | 702 | 1
249 | 703 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 703 | 1
250 | 704 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 704 | 1
251 | 705 Special Exam |  | 180 | 9 | 1620 |  |  | 7 | 15 | 1 | 1.26 | 1 | 5500 | 705 | 1
252 | 706 Hall |  | 146 | 9 | 1314 |  |  |  | 0.05 | 0 | 0 | 0 | 1500 | 706 | 1
253 | 707 Exam #1 |  | 100 | 9 | 900 | 6 |  | 7 | 15 | 1 | 0.7 | 0.7 | 4700 | 707 | 1
254 | 708 Exam #2 |  | 105 | 9 | 945 | 6 |  | 7 | 15 | 1 | 0.735 | 0.735 | 1900 | 708 | 1
255 | 709 Exam #3 |  | 100 | 9 | 900 | 6 |  | 7 | 15 | 1 | 0.7 | 0.7 | 3300 | 709 | 1
256 | 710 Exam #4 |  | 105 | 9 | 945 | 6 |  | 7 | 15 | 1 | 0.735 | 0.735 | 1900 | 710 | 1
257 | 711 Exam #5 |  | 100 | 9 | 900 | 6 |  | 7 | 15 | 1 | 0.7 | 0.7 | 4700 | 711 | 1
258 | 712 Testing |  | 165 | 9 | 1485 |  |  | 7 | 15 | 1 | 1.155 | 1 | 6000 | 712 | 1
259 | 713 Hall |  | 188 | 9 | 1692 | 2 |  |  | 0.05 | 0 | 0 | 0 | 1900 | 713 | 1
260 | 714 Phys. Office |  | 95 | 9 | 855 |  |  | 7 | 20 | 1 | 0.665 | 0.665 | 5900 | 714 | 1
261 | 715 Phys. Office |  | 95 | 9 | 855 |  |  | 7 | 20 | 1 | 0.665 | 0.665 | 4100 | 715 | 1
262 | 716 Soiled Utility |  | 80 | 9 | 720 | 10 |  |  | 0.15 | 0 | 0 | 0 | 800 | 716 | 1
263 | 717 Office |  | 85 | 9 | 765 |  |  | 7 | 20 | 1 | 0.595 | 0.595 | 5800 | 717 | 1
264 | 718 Janitors Office |  | 40 | 9 | 360 |  |  | 7 | 20 | 0 | 0.28 | 0 | 400 | 718 | 1
265 | 719 Office |  | 85 | 9 | 765 |  |  | 7 | 20 | 1 | 0.595 | 0.595 | 5800 | 719 | 1
266 | 720 Hall |  | 143 | 9 | 1287 | 2 |  |  | 0.05 | 0 | 0 | 0 | 1400 | 720 | 1
267 | 721 Control |  | 75 | 9 | 675 |  |  | 7 | 20 | 1 | 0.525 | 0.525 | 3400 | 721 | 1
268 | 722 Audio Booth |  | 64 | 9 | 576 |  |  | 7 | 20 | 0 | 0.448 | 0 | 3000 | 722 | 1
269 | 723 Equip. Storage |  | 78 | 9 | 702 |  |  |  | 0.15 | 0 | 0 | 0 | 800 | 723 | 1
270 | 724 Comm. Closet |  | 78 | 9 | 702 |  |  |  |  | 0 | 0 | 0 | 800 | 724 | 1
271 | 724 Work Area |  | 150 | 9 | 1350 |  |  | 7 | 20 | 1 | 1.05 | 1 | 4300 | 724 | 1
272 | 725 Stress Test |  | 165 | 9 | 1485 | 6 |  | 7 | 15 | 1 | 1.155 | 1 | 2500 | 725 | 1
273 | 726 Entry |  | 60 | 9 | 540 |  |  |  | 0.05 | 0 | 0 | 0 | 600 | 726 | 1
274 | 727 PT Gym |  | 1520 | 9 | 13680 | 6 |  | 20 | 15 | 30 | 30.4 | 30 | 33400 | 727 | 1
275 | 728 Group Office |  | 140 | 9 | 1260 |  |  | 7 | 20 | 1 | 0.98 | 0.98 | 7000 | 728 | 1
276 | 729 Directors Office |  | 100 | 9 | 900 |  |  | 7 | 20 | 1 | 0.7 | 0.7 | 2400 | 729 | 1
277 | 730 Cardiac Rehab. |  | 72 | 9 | 648 | 6 |  | 7 | 20 | 1 | 0.504 | 0.504 | 4100 | 730 | 1
278 | 731 Equip. Storage |  | 121 | 9 | 1089 |  |  |  | 0.15 | 0 | 0 | 0 | 1200 | 731 | 1
279 | 732 Exam #1 |  | 94 | 9 | 846 | 6 |  | 7 | 15 | 1 | 0.658 | 0.658 | 1800 | 732 | 1
280 | 733 Exam #2 |  | 96 | 9 | 864 | 6 |  | 7 | 15 | 1 | 0.672 | 0.672 | 1800 | 733 | 1
281 | 734 Exam #3 |  | 130 | 9 | 1170 | 6 |  | 7 | 15 | 1 | 0.91 | 0.91 | 2100 | 734 | 1
282 | 735 Exam #4 |  | 85 | 9 | 765 | 6 |  | 7 | 15 | 1 | 0.595 | 0.595 | 1700 | 735 | 1
283 | 736 Exam #5 |  | 90 | 9 | 810 | 6 |  | 7 | 15 | 1 | 0.63 | 0.63 | 1700 | 736 | 1
284 | 737 Wound Exam #6 |  | 90 | 9 | 810 | 6 |  | 7 | 15 | 1 | 0.63 | 0.63 | 1700 | 737 | 1
285 | 738 Toilet |  | 50 | 9 | 450 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 738 | 1
286 | 740 Vending |  | 60 | 9 | 540 |  |  | 60 | 20 | 4 | 3.6 | 3.6 | 600 | 740 | 1
287 | 800 Finance Offices |  | 790 | 9 | 7110 |  |  | 7 | 20 | 6 | 5.53 | 5.53 | 13500 | 800 | 1
288 | 801 Office |  | 110 | 9 | 990 |  |  | 7 | 20 | 1 | 0.77 | 0.77 | 2300 | 801 | 1
289 | 802 Private Registr. |  | 85 | 9 | 765 |  |  | 7 | 20 | 1 | 0.595 | 0.595 | 2000 | 802 | 1
290 | 803 Private Registr. |  | 80 | 9 | 720 |  |  | 7 | 20 | 1 | 0.56 | 0.56 | 2000 | 803 | 1
291 | 804 Information |  | 160 | 9 | 1440 |  |  | 7 | 20 | 1 | 1.12 | 1 | 3500 | 804 | 1
292 | 805 Chapel |  | 204 | 9 | 1836 |  |  | 60 | 20 | 4 | 12.24 | 4 | 3500 | 805 | 1
293 | 806 Waiting |  | 130 | 9 | 1170 | 12 | 2 | 60 | 20 | 8 | 7.8 | 7.8 | 3100 | 806 | 1
294 | 807 Hall |  | 150 | 9 | 1350 |  |  |  | 0.05 | 0 | 0 | 0 | 1500 | 807 | 1
295 | 808 Office Patty |  | 135 | 9 | 1215 |  |  | 7 | 20 | 1 | 0.945 | 0.945 | 3000 | 808 | 1
296 | 809 HR File |  | 80 | 9 | 720 |  |  | 7 | 20 | 1 | 0.56 | 0.56 | 1700 | 809 | 1
297 | 810 Foundation P.R. |  | 90 | 9 | 810 |  |  | 7 | 20 | 1 | 0.63 | 0.63 | 2300 | 810 | 1
298 | 811 Office Deb O. |  | 200 | 9 | 1800 |  |  | 7 | 20 | 1 | 1.4 | 1 | 3100 | 811 | 1
299 | 812 Office Scott |  | 217 | 9 | 1953 |  |  | 7 | 20 | 2 | 1.519 | 1.519 | 9900 | 812 | 1
300 | 815 Hall |  | 75 | 9 | 675 |  |  |  | 0.05 | 0 | 0 | 0 | 800 | 815 | 1
301 | 816 Work/File |  | 110 | 9 | 990 |  |  | 7 | 20 | 1 | 0.77 | 0.77 | 4500 | 816 | 1
302 | 817 Office Deb K. |  | 175 | 9 | 1575 |  |  | 7 | 20 | 1 | 1.225 | 1 | 9100 | 817 | 1
303 | 818 Hall |  | 150 | 9 | 1350 |  |  |  | 0.05 | 0 | 0 | 0 | 1500 | 818 | 1
304 | 819 Office Joyce |  | 120 | 9 | 1080 |  |  | 7 | 20 | 1 | 0.84 | 0.84 | 6300 | 819 | 1
305 | 820 Office Linda |  | 140 | 9 | 1260 |  |  | 7 | 20 | 1 | 0.98 | 0.98 | 6500 | 820 | 1
306 | 821 Office Barb |  | 120 | 9 | 1080 |  |  | 7 | 20 | 1 | 0.84 | 0.84 | 6200 | 821 | 1
307 | 822 Hall |  | 75 | 9 | 675 |  |  |  | 0.05 | 0 | 0 | 0 | 800 | 822 | 1
308 | 823 Office Gretchen |  | 106 | 9 | 954 |  |  | 7 | 20 | 1 | 0.742 | 0.742 | 2000 | 823 | 1
309 | 824 Hall |  | 125 | 9 | 1125 |  |  |  | 0.05 | 0 | 0 | 0 | 1300 | 824 | 1
310 | 825 Office Andrea |  | 140 | 9 | 1260 |  |  | 7 | 20 | 1 | 0.98 | 0.98 | 6500 | 825 | 1
311 | 826 Toilet |  | 45 | 9 | 405 | 10 |  |  | 75 | 0 | 0 | 0 | 500 | 826 | 1
312 | 827 Board Room |  | 248 | 9 | 2232 |  |  | 50 | 20 | 12 | 12.4 | 12 | 11300 | 827 | 1
313 | 828 Storage |  | 42 | 9 | 378 |  |  |  | 0.15 | 0 | 0 | 0 | 400 | 828 | 1
314 | 829 Conf. Room |  | 180 | 9 | 1620 |  |  | 50 | 20 | 20 | 9 | 9 | 5100 | 829 | 1
315 | 830 Storage |  | 32 | 9 | 288 |  |  |  | 0.15 | 0 | 0 | 0 | 300 | 830 | 1
316 | 831 Conference Room. |  | 190 | 9 | 1710 |  |  | 50 | 20 | 20 | 9.5 | 9.5 | 5300 | 831 | 1
317 | 900 Café |  | 110 | 9 | 990 |  |  | 70 | 20 | 8 | 7.7 | 7.7 | 3800 | 900 | 1
318 | 901 Dining |  | 783 | 9 | 7047 |  |  | 70 | 20 | 30 | 54.81 | 30 | 30800 | 901 | 1
319 | 908 Janitor |  | 40 | 9 | 360 | 10 |  |  | 0.15 | 0 | 0 | 0 | 400 | 908 | 1
[14 empty] | 633 | 2
[14 empty] | 636 | 2
[14 empty] | 007 | 2
[14 empty] | 5-1 | 2
[14 empty] | 5-2 | 2
[14 empty] | 6-1 | 2
[14 empty] | 6-2 | 2
[14 empty] | 905 | 1
[14 empty] | 904 | 1
[14 empty] | 604 | 2
[14 empty] | 319 | 3
[14 empty] | 908 | 1
[14 empty] | 903 | 1
[14 empty] | 9-1 | 4
[14 empty] | 9-2 | 4
[14 empty] | 528 | 2
[14 empty] | 427 | 4
[14 empty] | 530 | 2
[14 empty] | 907 | 1
[14 empty] | 902 | 1
[14 empty] | 426 | 4
[14 empty] | 906 | 1
[14 empty] | 5-1 | 1
[14 empty] | 5-2 | 1

## IssaquahInfo (hidden)
|  | [ft2] | [W/ft2] | [W] | [W/ft2] | [W] | [ft2/occ] | [occ] | [% CLG AIR] | [% HTG AIR] | [cfm/ft2] | [cfm] | [ach] | [cfm] | [ft] | [ach] | [ach]
ROOM NAME | ZONE CATEGORY | FLOOR AREA | LPD | LPD | PLUG LOAD | PLUG LOAD | OCC DENSITY | OCC DENSITY | VENTILATION |  | INFILTRATION | INFILTRATION | SUPPLY | SUPPLY | CEILING | VENT | EXHAUST
1000 LOBBY #1 | Lobby | 112 | 1.3 | 145.6 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0.86607 | 97
1000 LOBBY #2 | Lobby | 730 | 1.3 | 949 | 0 | 0 | 66.3636 | 11 | 33% | 33% | 0 | 0
1001 CAFÉ | Cafeteria | 190 | 1.2 | 228 | 14.6316 | 2780 | 31.6667 | 6 | 33% | 33% | 0 | 0
1058 TLT | Restroom | 48 | 0.9 | 43.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
110 STAIR | Corridor | 220 | 0.6 | 132 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0.57273 | 126
1055 MRI | MRI | 405 | 1.5 | 607.5 | 8.3951 | 3400 | 202.5 | 2 | 33% | 33% | 0 | 0 | 6 | 405 | 10 | 1.98
1050 DRESS | Restroom | 74 | 0.6 | 44.4 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1051 READ | Office Space | 56 | 1.1 | 61.6 | 2.6786 | 150 | 56 | 1 | 33% | 33% | 0 | 0
1052 CLOSET | Storage | 16 | 0.9 | 14.4 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1053 HALL | Corridor | 205 | 1 | 205 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1056 CONTROL | Control | 216 | 1.1 | 237.6 | 28.3796 | 6130 | 108 | 2 | 33% | 33% | 0 | 0
1049 PROC | Operating Room | 311 | 1.5 | 466.5 | 0.083601 | 26 | 77.75 | 4 | 33% | 33% | 0 | 0 | 15 | 738.625 | 9.5 | 4.95
1002 RECEPTION | Reception Area | 380 | 1.2 | 456 | 0.26316 | 100 | 29.2308 | 13 | 33% | 33% | 0.026316 | 10
1003 SCHEDULE | Office Space | 101 | 1.1 | 111.1 | 1.7426 | 176 | 101 | 1 | 33% | 33% | 0 | 0
1041 HALL | Corridor | 338 | 1 | 338 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1042 HALL | Corridor | 182 | 1 | 182 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1043 MAN | Office Space | 117 | 1.1 | 128.7 | 1.5043 | 176 | 117 | 1 | 33% | 33% | 0 | 0
1044 RECEPT | Reception Area | 117 | 1.2 | 140.4 | 2.5641 | 300 | 58.5 | 2 | 33% | 33% | 0 | 0
1045 RECEPT | Reception Area | 74 | 1.2 | 88.8 | 2.027 | 150 | 74 | 1 | 33% | 33% | 0 | 0
1046 DRESS | Restroom | 50 | 0.6 | 30 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1047 WORK | Office Space | 192 | 1.1 | 211.2 | 3 | 576 | 96 | 2 | 33% | 33% | 0 | 0
1048 HALL | Corridor | 101 | 0.9 | 90.9 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1054 RECEPTION | Reception Area | 146 | 1.2 | 175.2 | 0 | 0 | 73 | 2 | 33% | 33% | 0 | 0
1038 LOUNGE | Lounge | 466 | 1.2 | 559.2 | 4.4549 | 2076 | 58.25 | 8 | 33% | 33% | 0.01073 | 5
1039 WOMEN'S LOCKER | Locker Room | 352 | 0.6 | 211.2 | 0 | 0 | 176 | 2 | 33% | 33% | 0 | 0 | 8.4162 | 395 | 8 | 2.7773
1040 MEN'S LOCKER | Locker Room | 315 | 0.6 | 189 | 0 | 0 | 157.5 | 2 | 33% | 33% | 0 | 0 | 8.2143 | 345 | 8 | 2.7107
1004 PRE-OP #1 | Pre-Op | 88 | 1.5 | 132 | 0 | 0 | 88 | 1 | 33% | 33% | 0 | 0 | 6 | 70.4 | 8 | 1.98
1004 PRE-OP #2 | Pre-Op | 88 | 1.5 | 132 | 0 | 0 | 88 | 1 | 33% | 33% | 0 | 0 | 6 | 70.4 | 8 | 1.98
1004 PRE-OP #3 | Pre-Op | 81 | 1.5 | 121.5 | 0 | 0 | 81 | 1 | 33% | 33% | 0 | 0 | 6 | 64.8 | 8 | 1.98
1004 PRE-OP #4 | Pre-Op | 81 | 1.5 | 121.5 | 0 | 0 | 81 | 1 | 33% | 33% | 0 | 0 | 6 | 64.8 | 8 | 1.98
1004 PRE-OP #5 | Pre-Op | 81 | 1.5 | 121.5 | 0 | 0 | 81 | 1 | 33% | 33% | 0 | 0 | 6 | 64.8 | 8 | 1.98
1005 VEST | Entry | 95 | 0.3 | 28.5 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0.14737 | 14 | 7.1053 | 90 | 8 | 2.3447
1006 TLT | Restroom | 54 | 0.9 | 48.6 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 4.8611 | 35 | 8 | 1.6042
1007 STEP-DN #1 | Step-Down | 126 | 0.8 | 100.8 | 0 | 0 | 126 | 1 | 33% | 33% | 0.19048 | 24 | 6 | 113.4 | 9 | 1.98
1004 PRE-OP | Pre-Op | 244 | 1.5 | 366 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 2.1858 | 80 | 9 | 0.72131
1007 STEP-DN | Step-Down | 277 | 0.8 | 221.6 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 1.9254 | 80 | 9 | 0.63538
1007 STEP-DN #2 | Step-Down | 108 | 0.8 | 86.4 | 0 | 0 | 108 | 1 | 33% | 33% | 0.046296 | 5 | 8.9506 | 145 | 9 | 2.9537
1007 STEP-DN #3 | Step-Down | 108 | 0.8 | 86.4 | 0 | 0 | 108 | 1 | 33% | 33% | 0.046296 | 5 | 8.9506 | 145 | 9 | 2.9537
1007 STEP-DN #4 | Step-Down | 108 | 0.8 | 86.4 | 0 | 0 | 108 | 1 | 33% | 33% | 0.17593 | 19 | 19.1358 | 310 | 9 | 6.3148
1008 NS | Office Space | 115 | 1 | 115 | 2.6087 | 300 | 57.5 | 2 | 33% | 33% | 0 | 0
1009 NOUR | Office Space | 180 | 1.2 | 216 | 4.4889 | 808 | 90 | 2 | 33% | 33% | 0 | 0
1010 JAN | Storage | 54 | 0.8 | 43.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1011 HUMID | Storage | 54 | 0.8 | 43.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1012 CLEAN | Operating Room | 58 | 1.4 | 81.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 9.6983 | 75 | 8 | 3.2004
1013 DICT | Office Space | 70 | 1.1 | 77 | 6.4286 | 450 | 23.3333 | 3 | 33% | 33% | 0 | 0
1014 PACU | PACU | 189 | 1.5 | 283.5 | 5.4286 | 1026 | 94.5 | 2 | 33% | 33% | 0 | 0
1015 TLT | Restroom | 50 | 0.9 | 45 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1019 SOIL | Science Laboratories | 75 | 1.4 | 105 | 0.34667 | 26 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 2.5 | 25 | 8 | 0.825 | 10
1014 PACU #1 | PACU | 108 | 1.5 | 162 | 0 | 0 | 108 | 1 | 33% | 33% | 0 | 0 | 5.8642 | 95 | 9 | 1.9352
1014 PACU #2 | PACU | 108 | 1.5 | 162 | 0 | 0 | 108 | 1 | 33% | 33% | 0.046296 | 5 | 5.5556 | 90 | 9 | 1.8333
1014 PACU #3 | PACU | 108 | 1.5 | 162 | 0 | 0 | 108 | 1 | 33% | 33% | 0.092593 | 10 | 7.4074 | 120 | 9 | 2.4444
1014 PACU #4 | PACU | 108 | 1.5 | 162 | 0 | 0 | 108 | 1 | 33% | 33% | 0.092593 | 10 | 7.4074 | 120 | 9 | 2.4444
1018 STAGE 1 RECOVERY | Recovery | 324 | 0.8 | 259.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 1.0288 | 50 | 9 | 0.33951
1020 ANES | Operating Room | 108 | 1.5 | 162 | 1.8704 | 202 | 54 | 2 | 33% | 33% | 0.17593 | 19 | 19.1358 | 310 | 9 | 6.3148
1021 OR-2 | Operating Room | 536 | 2.2 | 1179.2 | 0.65485 | 351 | 107.2 | 5 | 33% | 33% | 0 | 0 | 20.1493 | 1800 | 10 | 6.6493
1016 CLEAN WORK | Science Laboratories | 198 | 1.4 | 277.2 | 0.13131 | 26 | 198 | 1 | 33% | 33% | 0 | 0 | 5.2189 | 155 | 9 | 1.7222
1023 SCRUB | Pre-Op | 85 | 2.2 | 187 | 0 | 0 | 85 | 1 | 33% | 33% | 0 | 0 | 7.0588 | 80 | 8 | 2.3294
1024 STERILE CORR | Medical Storage | 882 | 1 | 882 | 0.19955 | 176 | 882 | 1 | 33% | 33% | 0 | 0 | 3.7037 | 490 | 9 | 1.2222
1025 STOR | Medical Storage | 180 | 0.8 | 144 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 3.5185 | 95 | 9 | 1.1611
1027 JAN | Storage | 45 | 0.8 | 36 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1034 STERILE CORR | Step-Down | 258 | 1 | 258 | 2.7132 | 700 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 10.8527 | 420 | 9 | 3.5814
1035 STOR | Medical Storage | 216 | 0.8 | 172.8 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 3.0864 | 100 | 9 | 1.0185
1017 SOIL WORK | Office Space | 176 | 1.4 | 246.4 | 5.6818 | 1000 | 176 | 1 | 33% | 33% | 0 | 0
1022 SUB-STERILE | Pre-Op | 178 | 2.2 | 391.6 | 13.2135 | 2352 | 178 | 1 | 33% | 33% | 0 | 0
1026 OR-1 | Operating Room | 530 | 2.2 | 1166 | 0.66226 | 351 | 106 | 5 | 33% | 33% | 0 | 0 | 20.3774 | 1800 | 10 | 6.7245
1028 ELEC | Electrical | 124 | 1.5 | 186 | 3.629 | 450 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 3.2258 | 100 | 15 | 1.0645
1029 UTILITY | Utility | 442 | 1.2 | 530.4 | 11.8404 | 5233.4635 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 7.2398 | 800 | 15 | 2.3891
1030 HALL | Corridor | 425 | 1.5 | 637.5 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0.061176 | 26 | 2.3529 | 150 | 9 | 0.77647
1031 BIO HAZ | Storage | 54 | 1.4 | 75.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
1033 STORAGE | Storage | 759 | 0.8 | 607.2 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
1037 SOILED HOLD | Storage | 56 | 1.4 | 78.4 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0 |  |  | 8 |  | 8
1060 STORAGE | Storage | 207 | 0.8 | 165.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
1057 ELEV | Elevator | 161 | 1.5 | 241.5 | 20.5696 | 3311.7031 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1036 OR 3 | Operating Room | 428 | 2.2 | 941.6 | 0.35047 | 150 | 85.6 | 5 | 33% | 33% | 0 | 0 | 21.028 | 1500 | 10 | 6.9393
1032 MED GAS | Storage | 60 | 0.9 | 54 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 3.3333 | 200
2068 RECORDS | Office Space | 240 | 1.1 | 264 | 0.625 | 150 | 240 | 1 | 0% | 0% | 0 | 0
2071 WORK | Office Space | 140 | 1.1 | 154 | 3.9286 | 550 | 140 | 1 | 0% | 0% | 0 | 0
2072 CHECK IN-OUT | Reception Area | 456 | 1.1 | 501.6 | 1.9737 | 900 | 76 | 6 | 0% | 0% | 0 | 0
2074 PRE-REGIS | Office Space | 268 | 1.1 | 294.8 | 1.1194 | 300 | 134 | 2 | 0% | 0% | 0 | 0
2075 JAN | Storage | 51 | 0.8 | 40.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2076 TLT | Restroom | 48 | 0.9 | 43.2 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2069 PHONE | Office Space | 200 | 1.1 | 220 | 3 | 600 | 66.6667 | 3 | 0% | 0% | 0.05 | 10
2070 MAN | Office Space | 114 | 1.1 | 125.4 | 1.3158 | 150 | 114 | 1 | 0% | 0% | 0.23684 | 27
2073 FIN CON | Office Space | 84 | 1.1 | 92.4 | 1.7857 | 150 | 84 | 1 | 0% | 0% | 0.32143 | 27
2054 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2061 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.081967 | 10
2062 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.081967 | 10
2065 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2055 EXAM | Exam | 117 | 1.5 | 175.5 | 1.2821 | 150 | 117 | 1 | 0% | 0% | 0 | 0
2056 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2058 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | 190 | 1 | 0% | 0% | 0.052632 | 10
2059 NS | Office Space | 220 | 1 | 220 | 2.9636 | 652 | 55 | 4 | 0% | 0% | 0 | 0
2060 STOR | Storage | 36 | 0.8 | 28.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2063 STOR | Storage | 36 | 0.8 | 28.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2064 HALL | Corridor | 190 | 1 | 190 | 0.78947 | 150 | 190 | 1 | 0% | 0% | 0.052632 | 10
2066 EXAM | Exam | 108 | 1.5 | 162 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
2067 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2048 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.081967 | 10
2053 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2043 EXAM | Exam | 124 | 1.5 | 186 | 1.2097 | 150 | 124 | 1 | 0% | 0% | 0 | 0
2044 HALL | Corridor | 136 | 1 | 136 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2045 NS | Office Space | 220 | 1 | 220 | 2.9636 | 652 | 55 | 4 | 0% | 0% | 0 | 0
2046 STOR | Storage | 36 | 0.8 | 28.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2047 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.081967 | 10
2049 STOR | Storage | 36 | 0.8 | 28.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2050 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | 190 | 1 | 0% | 0% | 0.052632 | 10
2051 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2052 EXAM | Exam | 117 | 1.5 | 175.5 | 1.2821 | 150 | 117 | 1 | 0% | 0% | 0 | 0
2040 UTIL | Utility | 90 | 1.5 | 135 | 0.28889 | 26 | 90 | 1 | 0% | 0% | 0.11111 | 10
2041 CAST | Cast | 130 | 1.5 | 195 | 0.2 | 26 | 130 | 1 | 0% | 0% | 0.076923 | 10 | 6 | 104 | 8 | 0 | 6
2042 EXAM | Exam | 110 | 1.5 | 165 | 1.3636 | 150 | 110 | 1 | 0% | 0% | 0.16364 | 18
2029 TLT | Restroom | 54 | 0.9 | 48.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2031 OFFICE | Office Space | 586 | 1.1 | 644.6 | 3.5154 | 2060 | 58.6 | 10 | 0% | 0% | 0.061433 | 36
2030 CONF | Conference | 360 | 1.3 | 468 | 0.41667 | 150 | 30 | 12 | 0% | 0% | 0 | 0
2030 CONF-STOR | Storage | 75 | 0.8 | 60 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2019 HALL-E | Corridor | 250 | 1 | 250 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2028 LOUNGE | Lounge | 81 | 1.2 | 97.2 | 1.8519 | 150 | 81 | 1 | 0% | 0% | 0 | 0
2032 SCHED | Office Space | 81 | 1.1 | 89.1 | 1.8519 | 150 | 81 | 1 | 0% | 0% | 0 | 0
2033 DATA | Office Space | 81 | 1.5 | 121.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2038 SCHED | Office Space | 81 | 1.1 | 89.1 | 1.8519 | 150 | 81 | 1 | 0% | 0% | 0 | 0
2039 HALL | Corridor | 108 | 1 | 108 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2057 HALL-E | Corridor | 252 | 1 | 252 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2020 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2021 EXAM | Exam | 117 | 1.5 | 175.5 | 1.2821 | 150 | 117 | 1 | 0% | 0% | 0 | 0
2023 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2025 STOR | Storage | 40 | 0.8 | 32 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2026 DICT | Office Space | 48 | 1.1 | 52.8 | 3.6667 | 176 | 48 | 1 | 0% | 0% | 0 | 0
2027 NS | Office Space | 68 | 1 | 68 | 2.2059 | 150 | 68 | 1 | 0% | 0% | 0 | 0
2013 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.14754 | 18
2016 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2022 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2024 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.14754 | 18
2010 NS | Office Space | 220 | 1 | 220 | 2.9636 | 652 | 55 | 4 | 0% | 0% | 0 | 0
2014 STOR | Storage | 54 | 0.8 | 43.2 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2015 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2017 EXAM | Exam | 117 | 1.5 | 175.5 | 1.2821 | 150 | 117 | 1 | 0% | 0% | 0 | 0
2018 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2006 CAST | Cast | 144 | 1.5 | 216 | 0.18056 | 26 | 144 | 1 | 0% | 0% | 0 | 0 | 6 | 115.2 | 8 | 0 | 6
2007 EXAM | Exam | 110 | 1.5 | 165 | 1.3636 | 150 | 110 | 1 | 0% | 0% | 0.045455 | 5
2009 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2011 STOR | Storage | 54 | 0.8 | 43.2 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2012 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0 | 0
2008 EXAM | Exam | 152 | 1.5 | 228 | 0.98684 | 150 | 152 | 1 | 0% | 0% | 0.26974 | 41
2001 TLT | Restroom | 50 | 0.9 | 45 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2002 TLT | Restroom | 50 | 0.9 | 45 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2004 SCHED | Office Space | 108 | 1.1 | 118.8 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
2005 SCHED | Office Space | 108 | 1.1 | 118.8 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
2019 HALL-W | Corridor | 450 | 1 | 450 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2057 HALL-W | Corridor | 364 | 1 | 364 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2068 SUBWAIT | Corridor | 148 | 1.2 | 177.6 | 0 | 0 | 18.5 | 8 | 0% | 0% | 0 | 0
2036 X-RAY | X-Ray | 192 | 0.4 | 76.8 | 2.9427 | 565 | 96 | 2 | 0% | 0% | 0 | 0
2035 TECH | Office Space | 176 | 1.1 | 193.6 | 9.4886 | 1670 | 176 | 1 | 0% | 0% | 0 | 0
2037 FILM STOR | Storage | 180 | 0.8 | 144 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2034 X-RAY | X-Ray | 250 | 0.4 | 100 | 2.26 | 565 | 125 | 2 | 0% | 0% | 0 | 0
2000 RECEPTION #1 | Reception Area | 75 | 1.1 | 82.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2000 RECEPTION #2 | Reception Area | 950 | 1.2 | 1140 | 0.15789 | 150 | 21.1111 | 45 | 0% | 0% | 0 | 0
2003 PLAY | Corridor | 43 | 1.2 | 51.6 | 3.4884 | 150 | 43 | 1 | 0% | 0% | 0 | 0
210 STAIR | Corridor | 420 | 0.6 | 252 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0.13333 | 56
310 STAIR | Corridor | 330 | 0.6 | 198 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0.1697 | 56
3030 HALL-W | Corridor | 330 | 1 | 330 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3032 FILES | Office Space | 149 | 1.1 | 163.9 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3033 OFFICE | Office Space | 81 | 1.1 | 89.1 | 1.8519 | 150 | 81 | 1 | 0% | 0% | 0 | 0
3036 RECEPT | Reception Area | 295 | 1.2 | 354 | 0.50847 | 150 | 147.5 | 2 | 0% | 0% | 0 | 0
3037 HALL | Corridor | 255 | 1 | 255 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3038 JAN | Storage | 51 | 0.8 | 40.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3039 TLT | Restroom | 54 | 0.9 | 48.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3034 CONF | Conference | 144 | 1.3 | 187.2 | 1.0417 | 150 | 48 | 3 | 0% | 0% | 0.1875 | 27
3035 MAN | Office Space | 144 | 1.1 | 158.4 | 2.0833 | 300 | 144 | 1 | 0% | 0% | 0.1875 | 27
3026 BILLING #1-3 | Office Space | 230 | 1.1 | 253 | 1.9565 | 450 | 76.6667 | 3 | 0% | 0% | 0.15652 | 36
3024 TLT | Restroom | 54 | 0.9 | 48.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0.18519 | 10
3026 BILLING #4-7 | Office Space | 306 | 1.1 | 336.6 | 1.9608 | 600 | 76.5 | 4 | 0% | 0% | 0.088235 | 27
3022 TLT | Restroom | 45 | 0.9 | 40.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3023 HALL | Corridor | 50 | 1 | 50 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3026 BILLING | Office Space | 340 | 1 | 340 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3026 BILLING #8-9 | Office Space | 165 | 1.1 | 181.5 | 1.8182 | 300 | 82.5 | 2 | 0% | 0% | 0 | 0
3027 CLOS | Storage | 18 | 0.8 | 14.4 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3028 OFFICE | Office Space | 108 | 1.1 | 118.8 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
3029 COPY | Office Space | 108 | 1.1 | 118.8 | 5.3333 | 576 | 108 | 1 | 0% | 0% | 0 | 0
3030 HALL-E | Corridor | 650 | 1 | 650 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3031 HUMID | Storage | 36 | 1.5 | 54 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3025 DATA | Office Space | 83 | 1.5 | 124.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3019 HALL | Corridor | 155 | 1 | 155 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3020 LOUNGE | Lounge | 430 | 1.2 | 516 | 2.507 | 1078 | 35.8333 | 12 | 0% | 0% | 0.04186 | 18
3021 LOCKERS | Restroom | 68 | 0.6 | 40.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3014 LOUNGE | Lounge | 168 | 1.2 | 201.6 | 2.6905 | 452 | 84 | 2 | 0% | 0% | 0 | 0
3015 UTILITY | Utility | 215 | 1.5 | 322.5 | 1.0605 | 228 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3016 TLT | Restroom | 66 | 0.9 | 59.4 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3000 MECH | Mechanical | 345 | 1.5 | 517.5 | 5.5216 | 1904.962 | #DIV/0! | 0 | 0% | 0% | 0.028986 | 10
3001 RECEPTION | Reception Area | 180 | 1.2 | 216 | 0 | 0 | 22.5 | 8 | 0% | 0% | 0.055556 | 10
3002 RECEPT | Reception Area | 70 | 1.1 | 77 | 4.2857 | 300 | 35 | 2 | 0% | 0% | 0.14286 | 10
3003 WORK | Office Space | 170 | 1.1 | 187 | 3.5412 | 602 | 170 | 1 | 0% | 0% | 0.10588 | 18
3005 OFFICE | Office Space | 115 | 1.1 | 126.5 | 1.3043 | 150 | 115 | 1 | 0% | 0% | 0.086957 | 10
3006 CHART | Office Space | 215 | 1.1 | 236.5 | 4.5488 | 978 | 53.75 | 4 | 0% | 0% | 0.083721 | 18
3007 GYM-C | Physical Therapy | 500 | 1.4 | 700 | 0.6 | 300 | 125 | 4 | 0% | 0% | 0.108 | 54
3004 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3007 GYM-A | Physical Therapy | 646 | 1.4 | 904.4 | 0 | 0 | 80.75 | 8 | 0% | 0% | 0 | 0
3008 HAND | Physical Therapy | 310 | 1.4 | 434 | 1.3032 | 404 | 77.5 | 4 | 0% | 0% | 0 | 0
3009 HALL | Corridor | 130 | 1 | 130 | 7.9231 | 1030 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3017 TLT | Restroom | 65 | 0.9 | 58.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3018 DRESS | Restroom | 34 | 0.6 | 20.4 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3007 GYM-B | Physical Therapy | 770 | 1.4 | 1078 | 0.38961 | 300 | 77 | 10 | 0% | 0% | 0.07013 | 54
3010 TREAT | Exam | 108 | 1.5 | 162 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
3011 TREAT | Exam | 108 | 1.5 | 162 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
3012 TREAT | Exam | 108 | 1.5 | 162 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
3013 TREAT | Exam | 108 | 1.5 | 162 | 1.8704 | 202 | 108 | 1 | 0% | 0% | 0 | 0
3100 UNDEVELOPED #4A | Undeveloped | 750 | 1.2 | 900 | 1.4 | 1050 | 143 | 5.2448 | 0% | 0% | 0 | 0
3100 UNDEVELOPED #4B | Undeveloped | 400 | 1.2 | 480 | 1.4 | 560 | 143 | 2.7972 | 0% | 0% | 0.135 | 54
3100 UNDEVELOPED #8 | Undeveloped | 1260 | 1.2 | 1512 | 1.4 | 1764 | 143 | 8.8112 | 0% | 0% | 0 | 0
3100 UNDEVELOPED #9A | Undeveloped | 693 | 1.2 | 831.6 | 1.4 | 970.2 | 143 | 4.8462 | 0% | 0% | 0 | 0
3100 UNDEVELOPED #9B | Undeveloped | 665 | 1.2 | 798 | 1.4 | 931 | 143 | 4.6503 | 0% | 0% | 0.1218 | 81

## OldRoomInformation (hidden)
|  | [ft2] | [W/ft2] | [W] | [W/ft2] | [W] | [ft2/occ] | [occ] | [% CLG AIR] | [% HTG AIR] | [cfm/ft2] | [cfm] | [ach] | [cfm] | [ft] | [ach] | [ach]
ROOM NAME | ZONE CATEGORY | FLOOR AREA | LPD | LPD | PLUG LOAD | PLUG LOAD | OCC DENSITY | OCC DENSITY | VENTILATION |  | INFILTRATION | INFILTRATION | SUPPLY | SUPPLY | CEILING | VENT | EXHAUST
1000 LOBBY #1 | Lobby | 112 | 1.3 | 145.6 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0.86607 | 97
1000 LOBBY #2 | Lobby | 730 | 1.3 | 949 | 0 | 0 | 66.3636 | 11 | 33% | 33% | 0 | 0
1001 CAFÉ | Cafeteria | 190 | 1.2 | 228 | 14.6316 | 2780 | 31.6667 | 6 | 33% | 33% | 0 | 0
1058 TLT | Restroom | 48 | 0.9 | 43.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
110 STAIR | Corridor | 220 | 0.6 | 132 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0.57273 | 126
1055 MRI | MRI | 405 | 1.5 | 607.5 | 8.3951 | 3400 | 202.5 | 2 | 33% | 33% | 0 | 0 | 6 | 405 | 10 | 1.98
1050 DRESS | Restroom | 74 | 0.6 | 44.4 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1051 READ | Office Space | 56 | 1.1 | 61.6 | 2.6786 | 150 | 56 | 1 | 33% | 33% | 0 | 0
1052 CLOSET | Storage | 16 | 0.9 | 14.4 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1053 HALL | Corridor | 205 | 1 | 205 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1056 CONTROL | Control | 216 | 1.1 | 237.6 | 28.3796 | 6130 | 108 | 2 | 33% | 33% | 0 | 0
1049 PROC | Operating Room | 311 | 1.5 | 466.5 | 0.083601 | 26 | 77.75 | 4 | 33% | 33% | 0 | 0 | 15 | 738.625 | 9.5 | 4.95
1002 RECEPTION | Reception Area | 380 | 1.2 | 456 | 0.26316 | 100 | 29.2308 | 13 | 33% | 33% | 0.026316 | 10
1003 SCHEDULE | Office Space | 101 | 1.1 | 111.1 | 1.7426 | 176 | 101 | 1 | 33% | 33% | 0 | 0
1041 HALL | Corridor | 338 | 1 | 338 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1042 HALL | Corridor | 182 | 1 | 182 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1043 MAN | Office Space | 117 | 1.1 | 128.7 | 1.5043 | 176 | 117 | 1 | 33% | 33% | 0 | 0
1044 RECEPT | Reception Area | 117 | 1.2 | 140.4 | 2.5641 | 300 | 58.5 | 2 | 33% | 33% | 0 | 0
1045 RECEPT | Reception Area | 74 | 1.2 | 88.8 | 2.027 | 150 | 74 | 1 | 33% | 33% | 0 | 0
1046 DRESS | Restroom | 50 | 0.6 | 30 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1047 WORK | Office Space | 192 | 1.1 | 211.2 | 3 | 576 | 96 | 2 | 33% | 33% | 0 | 0
1048 HALL | Corridor | 101 | 0.9 | 90.9 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1054 RECEPTION | Reception Area | 146 | 1.2 | 175.2 | 0 | 0 | 73 | 2 | 33% | 33% | 0 | 0
1038 LOUNGE | Lounge | 466 | 1.2 | 559.2 | 4.4549 | 2076 | 58.25 | 8 | 33% | 33% | 0.01073 | 5
1039 WOMEN'S LOCKER | Locker Room | 352 | 0.6 | 211.2 | 0 | 0 | 176 | 2 | 33% | 33% | 0 | 0 | 8.4162 | 395 | 8 | 2.7773
1040 MEN'S LOCKER | Locker Room | 315 | 0.6 | 189 | 0 | 0 | 157.5 | 2 | 33% | 33% | 0 | 0 | 8.2143 | 345 | 8 | 2.7107
1004 PRE-OP #1 | Pre-Op | 88 | 1.5 | 132 | 0 | 0 | 88 | 1 | 33% | 33% | 0 | 0 | 6 | 70.4 | 8 | 1.98
1004 PRE-OP #2 | Pre-Op | 88 | 1.5 | 132 | 0 | 0 | 88 | 1 | 33% | 33% | 0 | 0 | 6 | 70.4 | 8 | 1.98
1004 PRE-OP #3 | Pre-Op | 81 | 1.5 | 121.5 | 0 | 0 | 81 | 1 | 33% | 33% | 0 | 0 | 6 | 64.8 | 8 | 1.98
1004 PRE-OP #4 | Pre-Op | 81 | 1.5 | 121.5 | 0 | 0 | 81 | 1 | 33% | 33% | 0 | 0 | 6 | 64.8 | 8 | 1.98
1004 PRE-OP #5 | Pre-Op | 81 | 1.5 | 121.5 | 0 | 0 | 81 | 1 | 33% | 33% | 0 | 0 | 6 | 64.8 | 8 | 1.98
1005 VEST | Entry | 95 | 0.3 | 28.5 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0.14737 | 14 | 7.1053 | 90 | 8 | 2.3447
1006 TLT | Restroom | 54 | 0.9 | 48.6 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 4.8611 | 35 | 8 | 1.6042
1007 STEP-DN #1 | Step-Down | 126 | 0.8 | 100.8 | 0 | 0 | 126 | 1 | 33% | 33% | 0.19048 | 24 | 6 | 113.4 | 9 | 1.98
1004 PRE-OP | Pre-Op | 244 | 1.5 | 366 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 2.1858 | 80 | 9 | 0.72131
1007 STEP-DN | Step-Down | 277 | 0.8 | 221.6 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 1.9254 | 80 | 9 | 0.63538
1007 STEP-DN #2 | Step-Down | 108 | 0.8 | 86.4 | 0 | 0 | 108 | 1 | 33% | 33% | 0.046296 | 5 | 8.9506 | 145 | 9 | 2.9537
1007 STEP-DN #3 | Step-Down | 108 | 0.8 | 86.4 | 0 | 0 | 108 | 1 | 33% | 33% | 0.046296 | 5 | 8.9506 | 145 | 9 | 2.9537
1007 STEP-DN #4 | Step-Down | 108 | 0.8 | 86.4 | 0 | 0 | 108 | 1 | 33% | 33% | 0.17593 | 19 | 19.1358 | 310 | 9 | 6.3148
1008 NS | Office Space | 115 | 1 | 115 | 2.6087 | 300 | 57.5 | 2 | 33% | 33% | 0 | 0
1009 NOUR | Office Space | 180 | 1.2 | 216 | 4.4889 | 808 | 90 | 2 | 33% | 33% | 0 | 0
1010 JAN | Storage | 54 | 0.8 | 43.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1011 HUMID | Storage | 54 | 0.8 | 43.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1012 CLEAN | Operating Room | 58 | 1.4 | 81.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 9.6983 | 75 | 8 | 3.2004
1013 DICT | Office Space | 70 | 1.1 | 77 | 6.4286 | 450 | 23.3333 | 3 | 33% | 33% | 0 | 0
1014 PACU | PACU | 189 | 1.5 | 283.5 | 5.4286 | 1026 | 94.5 | 2 | 33% | 33% | 0 | 0
1015 TLT | Restroom | 50 | 0.9 | 45 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1019 SOIL | Science Laboratories | 75 | 1.4 | 105 | 0.34667 | 26 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 2.5 | 25 | 8 | 0.825 | 10
1014 PACU #1 | PACU | 108 | 1.5 | 162 | 0 | 0 | 108 | 1 | 33% | 33% | 0 | 0 | 5.8642 | 95 | 9 | 1.9352
1014 PACU #2 | PACU | 108 | 1.5 | 162 | 0 | 0 | 108 | 1 | 33% | 33% | 0.046296 | 5 | 5.5556 | 90 | 9 | 1.8333
1014 PACU #3 | PACU | 108 | 1.5 | 162 | 0 | 0 | 108 | 1 | 33% | 33% | 0.092593 | 10 | 7.4074 | 120 | 9 | 2.4444
1014 PACU #4 | PACU | 108 | 1.5 | 162 | 0 | 0 | 108 | 1 | 33% | 33% | 0.092593 | 10 | 7.4074 | 120 | 9 | 2.4444
1018 STAGE 1 RECOVERY | Recovery | 324 | 0.8 | 259.2 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 1.0288 | 50 | 9 | 0.33951
1020 ANES | Operating Room | 108 | 1.5 | 162 | 1.8704 | 202 | 54 | 2 | 33% | 33% | 0.17593 | 19 | 19.1358 | 310 | 9 | 6.3148
1021 OR-2 | Operating Room | 536 | 2.2 | 1179.2 | 0.65485 | 351 | 107.2 | 5 | 33% | 33% | 0 | 0 | 20.1493 | 1800 | 10 | 6.6493
1016 CLEAN WORK | Science Laboratories | 198 | 1.4 | 277.2 | 0.13131 | 26 | 198 | 1 | 33% | 33% | 0 | 0 | 5.2189 | 155 | 9 | 1.7222
1023 SCRUB | Pre-Op | 85 | 2.2 | 187 | 0 | 0 | 85 | 1 | 33% | 33% | 0 | 0 | 7.0588 | 80 | 8 | 2.3294
1024 STERILE CORR | Medical Storage | 882 | 1 | 882 | 0.19955 | 176 | 882 | 1 | 33% | 33% | 0 | 0 | 3.7037 | 490 | 9 | 1.2222
1025 STOR | Medical Storage | 180 | 0.8 | 144 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 3.5185 | 95 | 9 | 1.1611
1027 JAN | Storage | 45 | 0.8 | 36 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1034 STERILE CORR | Step-Down | 258 | 1 | 258 | 2.7132 | 700 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 10.8527 | 420 | 9 | 3.5814
1035 STOR | Medical Storage | 216 | 0.8 | 172.8 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 3.0864 | 100 | 9 | 1.0185
1017 SOIL WORK | Office Space | 176 | 1.4 | 246.4 | 5.6818 | 1000 | 176 | 1 | 33% | 33% | 0 | 0
1022 SUB-STERILE | Pre-Op | 178 | 2.2 | 391.6 | 13.2135 | 2352 | 178 | 1 | 33% | 33% | 0 | 0
1026 OR-1 | Operating Room | 530 | 2.2 | 1166 | 0.66226 | 351 | 106 | 5 | 33% | 33% | 0 | 0 | 20.3774 | 1800 | 10 | 6.7245
1028 ELEC | Electrical | 124 | 1.5 | 186 | 3.629 | 450 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 3.2258 | 100 | 15 | 1.0645
1029 UTILITY | Utility | 442 | 1.2 | 530.4 | 11.8404 | 5233.4635 | #DIV/0! | 0 | 33% | 33% | 0 | 0 | 7.2398 | 800 | 15 | 2.3891
1030 HALL | Corridor | 425 | 1.5 | 637.5 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 0.061176 | 26 | 2.3529 | 150 | 9 | 0.77647
1031 BIO HAZ | Storage | 54 | 1.4 | 75.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
1033 STORAGE | Storage | 759 | 0.8 | 607.2 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
1037 SOILED HOLD | Storage | 56 | 1.4 | 78.4 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0 |  |  | 8 |  | 8
1060 STORAGE | Storage | 207 | 0.8 | 165.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
1057 ELEV | Elevator | 161 | 1.5 | 241.5 | 20.5696 | 3311.7031 | #DIV/0! | 0 | 33% | 33% | 0 | 0
1036 OR 3 | Operating Room | 428 | 2.2 | 941.6 | 0.35047 | 150 | 85.6 | 5 | 33% | 33% | 0 | 0 | 21.028 | 1500 | 10 | 6.9393
1032 MED GAS | Storage | 60 | 0.9 | 54 | 0 | 0 | #DIV/0! | 0 | 33% | 33% | 3.3333 | 200
2068 RECORDS | Office Space | 240 | 1.1 | 264 | 0.625 | 150 | 240 | 1 | 0% | 0% | 0 | 0
2071 WORK | Office Space | 140 | 1.1 | 154 | 3.9286 | 550 | 140 | 1 | 0% | 0% | 0 | 0
2072 CHECK IN-OUT | Reception Area | 456 | 1.1 | 501.6 | 1.9737 | 900 | 76 | 6 | 0% | 0% | 0 | 0
2074 PRE-REGIS | Office Space | 268 | 1.1 | 294.8 | 1.1194 | 300 | 134 | 2 | 0% | 0% | 0 | 0
2075 JAN | Storage | 51 | 0.8 | 40.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2076 TLT | Restroom | 48 | 0.9 | 43.2 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2069 PHONE | Office Space | 200 | 1.1 | 220 | 3 | 600 | 66.6667 | 3 | 0% | 0% | 0.05 | 10
2070 MAN | Office Space | 114 | 1.1 | 125.4 | 1.3158 | 150 | 114 | 1 | 0% | 0% | 0.23684 | 27
2073 FIN CON | Office Space | 84 | 1.1 | 92.4 | 1.7857 | 150 | 84 | 1 | 0% | 0% | 0.32143 | 27
2054 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2061 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.081967 | 10
2062 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.081967 | 10
2065 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2055 EXAM | Exam | 117 | 1.5 | 175.5 | 1.2821 | 150 | 117 | 1 | 0% | 0% | 0 | 0
2056 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2058 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | 190 | 1 | 0% | 0% | 0.052632 | 10
2059 NS | Office Space | 220 | 1 | 220 | 2.9636 | 652 | 55 | 4 | 0% | 0% | 0 | 0
2060 STOR | Storage | 36 | 0.8 | 28.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2063 STOR | Storage | 36 | 0.8 | 28.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2064 HALL | Corridor | 190 | 1 | 190 | 0.78947 | 150 | 190 | 1 | 0% | 0% | 0.052632 | 10
2066 EXAM | Exam | 108 | 1.5 | 162 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
2067 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2048 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.081967 | 10
2053 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2043 EXAM | Exam | 124 | 1.5 | 186 | 1.2097 | 150 | 124 | 1 | 0% | 0% | 0 | 0
2044 HALL | Corridor | 136 | 1 | 136 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2045 NS | Office Space | 220 | 1 | 220 | 2.9636 | 652 | 55 | 4 | 0% | 0% | 0 | 0
2046 STOR | Storage | 36 | 0.8 | 28.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2047 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.081967 | 10
2049 STOR | Storage | 36 | 0.8 | 28.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2050 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | 190 | 1 | 0% | 0% | 0.052632 | 10
2051 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2052 EXAM | Exam | 117 | 1.5 | 175.5 | 1.2821 | 150 | 117 | 1 | 0% | 0% | 0 | 0
2040 UTIL | Utility | 90 | 1.5 | 135 | 0.28889 | 26 | 90 | 1 | 0% | 0% | 0.11111 | 10
2041 CAST | Cast | 130 | 1.5 | 195 | 0.2 | 26 | 130 | 1 | 0% | 0% | 0.076923 | 10 | 6 | 104 | 8 | 0 | 6
2042 EXAM | Exam | 110 | 1.5 | 165 | 1.3636 | 150 | 110 | 1 | 0% | 0% | 0.16364 | 18
2029 TLT | Restroom | 54 | 0.9 | 48.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2031 OFFICE | Office Space | 586 | 1.1 | 644.6 | 3.5154 | 2060 | 58.6 | 10 | 0% | 0% | 0.061433 | 36
2030 CONF | Conference | 360 | 1.3 | 468 | 0.41667 | 150 | 30 | 12 | 0% | 0% | 0 | 0
2030 CONF-STOR | Storage | 75 | 0.8 | 60 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2019 HALL-E | Corridor | 250 | 1 | 250 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2028 LOUNGE | Lounge | 81 | 1.2 | 97.2 | 1.8519 | 150 | 81 | 1 | 0% | 0% | 0 | 0
2032 SCHED | Office Space | 81 | 1.1 | 89.1 | 1.8519 | 150 | 81 | 1 | 0% | 0% | 0 | 0
2033 DATA | Office Space | 81 | 1.5 | 121.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2038 SCHED | Office Space | 81 | 1.1 | 89.1 | 1.8519 | 150 | 81 | 1 | 0% | 0% | 0 | 0
2039 HALL | Corridor | 108 | 1 | 108 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2057 HALL-E | Corridor | 252 | 1 | 252 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2020 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2021 EXAM | Exam | 117 | 1.5 | 175.5 | 1.2821 | 150 | 117 | 1 | 0% | 0% | 0 | 0
2023 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2025 STOR | Storage | 40 | 0.8 | 32 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2026 DICT | Office Space | 48 | 1.1 | 52.8 | 3.6667 | 176 | 48 | 1 | 0% | 0% | 0 | 0
2027 NS | Office Space | 68 | 1 | 68 | 2.2059 | 150 | 68 | 1 | 0% | 0% | 0 | 0
2013 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.14754 | 18
2016 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2022 EXAM | Exam | 144 | 1.5 | 216 | 1.0417 | 150 | 144 | 1 | 0% | 0% | 0.069444 | 10
2024 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0.14754 | 18
2010 NS | Office Space | 220 | 1 | 220 | 2.9636 | 652 | 55 | 4 | 0% | 0% | 0 | 0
2014 STOR | Storage | 54 | 0.8 | 43.2 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2015 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2017 EXAM | Exam | 117 | 1.5 | 175.5 | 1.2821 | 150 | 117 | 1 | 0% | 0% | 0 | 0
2018 CAST | Cast | 128 | 1.5 | 192 | 0.20312 | 26 | 128 | 1 | 0% | 0% | 0 | 0 | 6 | 102.4 | 8 | 0 | 6
2006 CAST | Cast | 144 | 1.5 | 216 | 0.18056 | 26 | 144 | 1 | 0% | 0% | 0 | 0 | 6 | 115.2 | 8 | 0 | 6
2007 EXAM | Exam | 110 | 1.5 | 165 | 1.3636 | 150 | 110 | 1 | 0% | 0% | 0.045455 | 5
2009 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2011 STOR | Storage | 54 | 0.8 | 43.2 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2012 EXAM | Exam | 122 | 1.5 | 183 | 1.2295 | 150 | 122 | 1 | 0% | 0% | 0 | 0
2008 EXAM | Exam | 152 | 1.5 | 228 | 0.98684 | 150 | 152 | 1 | 0% | 0% | 0.26974 | 41
2001 TLT | Restroom | 50 | 0.9 | 45 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2002 TLT | Restroom | 50 | 0.9 | 45 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2004 SCHED | Office Space | 108 | 1.1 | 118.8 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
2005 SCHED | Office Space | 108 | 1.1 | 118.8 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
2019 HALL-W | Corridor | 450 | 1 | 450 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2057 HALL-W | Corridor | 364 | 1 | 364 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2068 SUBWAIT | Corridor | 148 | 1.2 | 177.6 | 0 | 0 | 18.5 | 8 | 0% | 0% | 0 | 0
2036 X-RAY | X-Ray | 192 | 0.4 | 76.8 | 2.9427 | 565 | 96 | 2 | 0% | 0% | 0 | 0
2035 TECH | Office Space | 176 | 1.1 | 193.6 | 9.4886 | 1670 | 176 | 1 | 0% | 0% | 0 | 0
2037 FILM STOR | Storage | 180 | 0.8 | 144 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2034 X-RAY | X-Ray | 250 | 0.4 | 100 | 2.26 | 565 | 125 | 2 | 0% | 0% | 0 | 0
2000 RECEPTION #1 | Reception Area | 75 | 1.1 | 82.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
2000 RECEPTION #2 | Reception Area | 950 | 1.2 | 1140 | 0.15789 | 150 | 21.1111 | 45 | 0% | 0% | 0 | 0
2003 PLAY | Corridor | 43 | 1.2 | 51.6 | 3.4884 | 150 | 43 | 1 | 0% | 0% | 0 | 0
210 STAIR | Corridor | 420 | 0.6 | 252 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0.13333 | 56
310 STAIR | Corridor | 330 | 0.6 | 198 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0.1697 | 56
3030 HALL-W | Corridor | 330 | 1 | 330 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3032 FILES | Office Space | 149 | 1.1 | 163.9 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3033 OFFICE | Office Space | 81 | 1.1 | 89.1 | 1.8519 | 150 | 81 | 1 | 0% | 0% | 0 | 0
3036 RECEPT | Reception Area | 295 | 1.2 | 354 | 0.50847 | 150 | 147.5 | 2 | 0% | 0% | 0 | 0
3037 HALL | Corridor | 255 | 1 | 255 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3038 JAN | Storage | 51 | 0.8 | 40.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3039 TLT | Restroom | 54 | 0.9 | 48.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3034 CONF | Conference | 144 | 1.3 | 187.2 | 1.0417 | 150 | 48 | 3 | 0% | 0% | 0.1875 | 27
3035 MAN | Office Space | 144 | 1.1 | 158.4 | 2.0833 | 300 | 144 | 1 | 0% | 0% | 0.1875 | 27
3026 BILLING #1-3 | Office Space | 230 | 1.1 | 253 | 1.9565 | 450 | 76.6667 | 3 | 0% | 0% | 0.15652 | 36
3024 TLT | Restroom | 54 | 0.9 | 48.6 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0.18519 | 10
3026 BILLING #4-7 | Office Space | 306 | 1.1 | 336.6 | 1.9608 | 600 | 76.5 | 4 | 0% | 0% | 0.088235 | 27
3022 TLT | Restroom | 45 | 0.9 | 40.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3023 HALL | Corridor | 50 | 1 | 50 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3026 BILLING | Office Space | 340 | 1 | 340 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3026 BILLING #8-9 | Office Space | 165 | 1.1 | 181.5 | 1.8182 | 300 | 82.5 | 2 | 0% | 0% | 0 | 0
3027 CLOS | Storage | 18 | 0.8 | 14.4 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3028 OFFICE | Office Space | 108 | 1.1 | 118.8 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
3029 COPY | Office Space | 108 | 1.1 | 118.8 | 5.3333 | 576 | 108 | 1 | 0% | 0% | 0 | 0
3030 HALL-E | Corridor | 650 | 1 | 650 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3031 HUMID | Storage | 36 | 1.5 | 54 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3025 DATA | Office Space | 83 | 1.5 | 124.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3019 HALL | Corridor | 155 | 1 | 155 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3020 LOUNGE | Lounge | 430 | 1.2 | 516 | 2.507 | 1078 | 35.8333 | 12 | 0% | 0% | 0.04186 | 18
3021 LOCKERS | Restroom | 68 | 0.6 | 40.8 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3014 LOUNGE | Lounge | 168 | 1.2 | 201.6 | 2.6905 | 452 | 84 | 2 | 0% | 0% | 0 | 0
3015 UTILITY | Utility | 215 | 1.5 | 322.5 | 1.0605 | 228 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3016 TLT | Restroom | 66 | 0.9 | 59.4 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3000 MECH | Mechanical | 345 | 1.5 | 517.5 | 5.5216 | 1904.962 | #DIV/0! | 0 | 0% | 0% | 0.028986 | 10
3001 RECEPTION | Reception Area | 180 | 1.2 | 216 | 0 | 0 | 22.5 | 8 | 0% | 0% | 0.055556 | 10
3002 RECEPT | Reception Area | 70 | 1.1 | 77 | 4.2857 | 300 | 35 | 2 | 0% | 0% | 0.14286 | 10
3003 WORK | Office Space | 170 | 1.1 | 187 | 3.5412 | 602 | 170 | 1 | 0% | 0% | 0.10588 | 18
3005 OFFICE | Office Space | 115 | 1.1 | 126.5 | 1.3043 | 150 | 115 | 1 | 0% | 0% | 0.086957 | 10
3006 CHART | Office Space | 215 | 1.1 | 236.5 | 4.5488 | 978 | 53.75 | 4 | 0% | 0% | 0.083721 | 18
3007 GYM-C | Physical Therapy | 500 | 1.4 | 700 | 0.6 | 300 | 125 | 4 | 0% | 0% | 0.108 | 54
3004 HALL | Corridor | 190 | 1 | 190 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3007 GYM-A | Physical Therapy | 646 | 1.4 | 904.4 | 0 | 0 | 80.75 | 8 | 0% | 0% | 0 | 0
3008 HAND | Physical Therapy | 310 | 1.4 | 434 | 1.3032 | 404 | 77.5 | 4 | 0% | 0% | 0 | 0
3009 HALL | Corridor | 130 | 1 | 130 | 7.9231 | 1030 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3017 TLT | Restroom | 65 | 0.9 | 58.5 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3018 DRESS | Restroom | 34 | 0.6 | 20.4 | 0 | 0 | #DIV/0! | 0 | 0% | 0% | 0 | 0
3007 GYM-B | Physical Therapy | 770 | 1.4 | 1078 | 0.38961 | 300 | 77 | 10 | 0% | 0% | 0.07013 | 54
3010 TREAT | Exam | 108 | 1.5 | 162 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
3011 TREAT | Exam | 108 | 1.5 | 162 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
3012 TREAT | Exam | 108 | 1.5 | 162 | 1.3889 | 150 | 108 | 1 | 0% | 0% | 0 | 0
3013 TREAT | Exam | 108 | 1.5 | 162 | 1.8704 | 202 | 108 | 1 | 0% | 0% | 0 | 0
3100 UNDEVELOPED #4A | Undeveloped | 750 | 1.2 | 900 | 1.4 | 1050 | 143 | 5.2448 | 0% | 0% | 0 | 0
3100 UNDEVELOPED #4B | Undeveloped | 400 | 1.2 | 480 | 1.4 | 560 | 143 | 2.7972 | 0% | 0% | 0.135 | 54
3100 UNDEVELOPED #8 | Undeveloped | 1260 | 1.2 | 1512 | 1.4 | 1764 | 143 | 8.8112 | 0% | 0% | 0 | 0
3100 UNDEVELOPED #9A | Undeveloped | 693 | 1.2 | 831.6 | 1.4 | 970.2 | 143 | 4.8462 | 0% | 0% | 0 | 0
3100 UNDEVELOPED #9B | Undeveloped | 665 | 1.2 | 798 | 1.4 | 931 | 143 | 4.6503 | 0% | 0% | 0.1218 | 81