## Intro
| PNNL | 2021-04-12 | PNNL Codes Team
This spreadsheet contains detailed end use data results from the Progress Indicator analysis
of ASHRAE Standard 90.1 conducted by PNNL.
The spreadsheet includes a list (DetPri tab) of all detailed ECIs by end use and prototype,
sorted by remaining use after 90.1-2019 and sorted by savings of 90.1-2019 vs. 90.1-2004.
Data includes detailed results for each of the prototypes at the detailed end use level. A tab
for each prototype includes a matrix of tables with a summary and detail for each climate
zone. In addition to ECI, both site and source energy use index (EUI) results are included as is
end use for gas and electric. Vertically, tables are included for:
US average summary results, based on construction weighting
Separate climate zone detail tables for energy cost and use after Standard 90.1 in 2004, 2007, 2010, 2013, 2016 and 2019.
Percentage savings from Standard 90.1-2004 to 90.1-2019
End uses are from energy plus simulation of the prototype models, and are defined as follows:
| Simple Breakdown | Detailed Breakdown | End Use Description
| Light.int | Light.int | Interior Lighting
| Light.ext | Light.ext | Exterior Lighting
| SHW | SHW | Service Hot Water
| Heat | Heat | Space Heating
|  | Humidify | Humidification (Dehumidification in Heat and Cool)
| Cool | Cool | Mechanical Cooling (including unitary heat rejection)
|  | Ht.Rej | Heat rejection, cooling towers (unitary is in cool)
| Fan.Aux | Fans | HVAC supply, return and exhaust fans
|  | Ht.Rcvy | Heat recovery fan and wheel energy
|  | Pumps | Hydronic pumping, including SHW recirculation
| Misc | Refrig | Refrigeration equipment and kitchen refrigerators and freezers
|  | Elevator | Elevators
|  | Txfmr | In-building transformers
| Equip | Cook | Cooking and Laundry Equipment
|  | IT | Computer room IT equipment and telephone equipment
|  | Equip | Other plug loads and equipment
The 16 building prototypes are listed below and further detail and description can be found at:
http://www.energycodes.gov/commercial-prototype-building-models
(Rounded)
|  |  |  | TSD | E+
|  |  |  | Floor area | Floor area
|  | Tab Name | Building Prototype | (ft²) | (ft²)
|  | OffS | Small Office | 5500 | 5502
|  | OffM | Medium Office | 53630 | 53628
|  | OffL | Large Office | 498640 | 498588
|  | RtlStA | Standalone Retail | 24690 | 24692
|  | RtlMall | Strip Mall | 22500 | 22500
|  | SchPri | Primary School | 73970 | 73959
|  | SchSec | Secondary School | 210910 | 210887
|  | MedOP | Outpatient Healthcare | 40950 | 40946
|  | MedHos | Hospital | 241410 | 241501
|  | HotSml | Small Hotel | 43210 | 43202
|  | HotLrg | Large Hotel | 122120 | 122120
|  | Whse | Warehouse | 52050 | 52045
|  | RestQS | Quick-service Restaurant | 2500 | 2501
|  | RestFS | Full-service Restaurant | 5500 | 5502
|  | AptMR | Mid-rise Apartment | 33740 | 33741
|  | AptHR | High-rise Apartment | 84360 | 84352

## DetPri
Priority sort by remaining ECI (after 90.1-2019) by end use and Prototype |  |  |  |  | Priority sort by past cost savings (90.1-2019 vs. 90.1-2004) by end use and Prototype
Prototype | End Use | ECI | Bar - Remaining ECI |  | Prototype | End Use | ECI Savings | Bar - unsaved
Quick-service Restaurant | Cook | 4.5293 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | +++++ | Primary School | Ht.Rcvy | -29.35%
Full-service Restaurant | Cook | 3.0318 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | +++ | Large Hotel | Ht.Rcvy | -15.85% | XXXXXXXXXXXXXXXXXXXXXXX
Quick-service Restaurant | Cool | 1.0467 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Small Hotel | Heat | -0.2829% | XXXXXXXXXXXXXXXXXXXX
Full-service Restaurant | SHW | 0.92483 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Small Office | Heat | 0% | XXXXXXXXXXXXXXXXXXXX
Full-service Restaurant | Cool | 0.9176 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Small Office | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Equip | 0.90123 | XXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXXX | + | Small Office | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Quick-service Restaurant | Refrig | 0.67217 | XXXXXXXXXXXXXXXXXXXXXXXXXX |  | Small Office | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Equip | 0.66831 | XXXXXXXXXXXXXXXXXXXXXXXXXX |  | Small Office | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Quick-service Restaurant | SHW | 0.65808 | XXXXXXXXXXXXXXXXXXXXXXXXXX |  | Small Office | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Quick-service Restaurant | Heat | 0.6553 | XXXXXXXXXXXXXXXXXXXXXXXXXX |  | Small Office | Elevator | 0% | XXXXXXXXXXXXXXXXXXXX
Quick-service Restaurant | Fans | 0.65509 | XXXXXXXXXXXXXXXXXXXXXXXXXX |  | Small Office | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
Full-service Restaurant | Fans | 0.56104 | XXXXXXXXXXXXXXXXXXXXXX |  | Small Office | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Large Office | IT | 0.55338 | XXXXXXXXXXXXXXXXXXXXXX |  | Small Office | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | Light.Int | 0.52845 | XXXXXXXXXXXXXXXXXXXXX |  | Medium Office | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Cool | 0.51799 | XXXXXXXXXXXXXXXXXXXX |  | Medium Office | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Full-service Restaurant | Heat | 0.46682 | XXXXXXXXXXXXXXXXXX |  | Medium Office | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Elevator | 0.46113 | XXXXXXXXXXXXXXXXXX |  | Medium Office | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Light.Int | 0.40087 | XXXXXXXXXXXXXXXX |  | Medium Office | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Primary School | Equip | 0.37841 | XXXXXXXXXXXXXXX |  | Medium Office | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Fans | 0.35447 | XXXXXXXXXXXXXX |  | Medium Office | IT | 0% | XXXXXXXXXXXXXXXXXXXX
High-rise Apartment | Equip | 0.34047 | XXXXXXXXXXXXX |  | Large Office | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Cool | 0.34032 | XXXXXXXXXXXXX |  | Large Office | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Mid-rise Apartment | Equip | 0.338 | XXXXXXXXXXXXX |  | Large Office | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Mid-rise Apartment | SHW | 0.33122 | XXXXXXXXXXXXX |  | Large Office | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Medium Office | Equip | 0.32202 | XXXXXXXXXXXX |  | Standalone Retail | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Large Hotel | Cook | 0.32037 | XXXXXXXXXXXX |  | Standalone Retail | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Large Office | Equip | 0.31604 | XXXXXXXXXXXX |  | Standalone Retail | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Large Hotel | Cool | 0.31212 | XXXXXXXXXXXX |  | Standalone Retail | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Elevator | 0.30666 | XXXXXXXXXXXX |  | Standalone Retail | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Quick-service Restaurant | Light.Int | 0.29915 | XXXXXXXXXXX |  | Standalone Retail | Elevator | 0% | XXXXXXXXXXXXXXXXXXXX
Full-service Restaurant | Refrig | 0.29892 | XXXXXXXXXXX |  | Standalone Retail | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
Standalone Retail | Light.Int | 0.28499 | XXXXXXXXXXX |  | Standalone Retail | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Cook | 0.27812 | XXXXXXXXXXX |  | Standalone Retail | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Light.Int | 0.27495 | XXXXXXXXXX |  | Strip Mall | Heat | 0% | XXXXXXXXXXXXXXXXXXXX
Full-service Restaurant | Light.Int | 0.26975 | XXXXXXXXXX |  | Strip Mall | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Secondary School | Equip | 0.26878 | XXXXXXXXXX |  | Strip Mall | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Small Office | Equip | 0.25923 | XXXXXXXXXX |  | Strip Mall | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Fans | 0.24466 | XXXXXXXXX |  | Strip Mall | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Heat | 0.23478 | XXXXXXXXX |  | Strip Mall | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Standalone Retail | Equip | 0.23242 | XXXXXXXXX |  | Strip Mall | Elevator | 0% | XXXXXXXXXXXXXXXXXXXX
Secondary School | Cool | 0.23127 | XXXXXXXXX |  | Strip Mall | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
Large Hotel | Elevator | 0.22988 | XXXXXXXXX |  | Strip Mall | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | Cool | 0.22672 | XXXXXXXXX |  | Strip Mall | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Standalone Retail | Cool | 0.21956 | XXXXXXXX |  | Primary School | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Large Hotel | Equip | 0.21108 | XXXXXXXX |  | Primary School | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Small Hotel | Cool | 0.20535 | XXXXXXXX |  | Primary School | Elevator | 0% | XXXXXXXXXXXXXXXXXXXX
Primary School | Cool | 0.20435 | XXXXXXXX |  | Primary School | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Small Hotel | Equip | 0.19094 | XXXXXXX |  | Primary School | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Large Hotel | SHW | 0.17838 | XXXXXXX |  | Secondary School | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Standalone Retail | Fans | 0.17285 | XXXXXX |  | Secondary School | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Small Hotel | Elevator | 0.17086 | XXXXXX |  | Secondary School | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Large Hotel | Fans | 0.16888 | XXXXXX |  | Secondary School | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | Equip | 0.16822 | XXXXXX |  | Outpatient Healthcare | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Large Office | Cool | 0.16797 | XXXXXX |  | Outpatient Healthcare | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Medium Office | Cool | 0.15767 | XXXXXX |  | Outpatient Healthcare | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Large Office | Light.Int | 0.15298 | XXXXXX |  | Outpatient Healthcare | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | Fans | 0.14392 | XXXXX |  | Outpatient Healthcare | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
High-rise Apartment | Cool | 0.14132 | XXXXX |  | Outpatient Healthcare | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Small Office | Light.Int | 0.13866 | XXXXX |  | Outpatient Healthcare | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Medium Office | Light.Int | 0.13597 | XXXXX |  | Hospital | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Large Hotel | Light.Int | 0.12731 | XXXXX |  | Hospital | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Small Hotel | Light.Int | 0.12596 | XXXXX |  | Hospital | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Small Hotel | SHW | 0.12352 | XXXX |  | Small Hotel | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Primary School | Fans | 0.1231 | XXXX |  | Small Hotel | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Large Office | Fans | 0.12304 | XXXX |  | Small Hotel | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Standalone Retail | Heat | 0.11616 | XXXX |  | Small Hotel | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
High-rise Apartment | SHW | 0.11595 | XXXX |  | Small Hotel | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Small Office | Cool | 0.11542 | XXXX |  | Small Hotel | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
Secondary School | Light.Int | 0.11484 | XXXX |  | Small Hotel | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Primary School | Light.Int | 0.11461 | XXXX |  | Small Hotel | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | Heat | 0.11357 | XXXX |  | Large Hotel | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Large Office | Elevator | 0.11261 | XXXX |  | Large Hotel | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Secondary School | Fans | 0.11076 | XXXX |  | Large Hotel | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Small Hotel | Fans | 0.11032 | XXXX |  | Large Hotel | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Small Hotel | Cook | 0.11009 | XXXX |  | Quick-service Restaurant | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Mid-rise Apartment | Elevator | 0.10939 | XXXX |  | Quick-service Restaurant | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Heat | 0.10909 | XXXX |  | Quick-service Restaurant | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Mid-rise Apartment | Cool | 0.1076 | XXXX |  | Quick-service Restaurant | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Primary School | Cook | 0.10513 | XXXX |  | Quick-service Restaurant | Elevator | 0% | XXXXXXXXXXXXXXXXXXXX
Quick-service Restaurant | Light.Ext | 0.10383 | XXXX |  | Quick-service Restaurant | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
Full-service Restaurant | Light.Ext | 0.10005 | XXXX |  | Quick-service Restaurant | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Small Office | SHW | 0.096682 | XXX |  | Quick-service Restaurant | Equip | 0% | XXXXXXXXXXXXXXXXXXXX
Warehouse | Light.Int | 0.095425 | XXX |  | Full-service Restaurant | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Humidfy | 0.094266 | XXX |  | Full-service Restaurant | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Humidfy | 0.092557 | XXX |  | Full-service Restaurant | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Small Office | Fans | 0.092015 | XXX |  | Full-service Restaurant | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Medium Office | Elevator | 0.09109 | XXX |  | Full-service Restaurant | Elevator | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | SHW | 0.081896 | XXX |  | Full-service Restaurant | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
High-rise Apartment | Fans | 0.079609 | XXX |  | Full-service Restaurant | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Strip Mall | Light.Ext | 0.078047 | XXX |  | Full-service Restaurant | Equip | 0% | XXXXXXXXXXXXXXXXXXXX
Warehouse | Equip | 0.077465 | XXX |  | Mid-rise Apartment | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Secondary School | Cook | 0.07431 | XX |  | Mid-rise Apartment | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Mid-rise Apartment | Light.Int | 0.073032 | XX |  | Mid-rise Apartment | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
High-rise Apartment | Light.Int | 0.0721 | XX |  | Mid-rise Apartment | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Mid-rise Apartment | Fans | 0.069285 | XX |  | Mid-rise Apartment | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Small Hotel | Heat | 0.068337 | XX |  | Mid-rise Apartment | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
Warehouse | Heat | 0.067865 | XX |  | Mid-rise Apartment | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
High-rise Apartment | Heat | 0.066847 | XX |  | Mid-rise Apartment | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Medium Office | Heat | 0.05761 | XX |  | High-rise Apartment | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Large Office | Ht.Rej | 0.056842 | XX |  | High-rise Apartment | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
High-rise Apartment | Elevator | 0.055468 | XX |  | High-rise Apartment | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Large Office | Humidfy | 0.055024 | XX |  | High-rise Apartment | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | SHW | 0.049662 | X |  | High-rise Apartment | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | SHW | 0.049217 | X |  | Warehouse | Humidfy | 0% | XXXXXXXXXXXXXXXXXXXX
Small Office | Heat | 0.047588 | X |  | Warehouse | Ht.Rej | 0% | XXXXXXXXXXXXXXXXXXXX
Standalone Retail | Light.Ext | 0.046105 | X |  | Warehouse | Ht.Rcvy | 0% | XXXXXXXXXXXXXXXXXXXX
Hospital | Pumps | 0.045344 | X |  | Warehouse | Pumps | 0% | XXXXXXXXXXXXXXXXXXXX
Large Hotel | Light.Ext | 0.044207 | X |  | Warehouse | Refrig | 0% | XXXXXXXXXXXXXXXXXXXX
Secondary School | SHW | 0.04253 | X |  | Warehouse | Elevator | 0% | XXXXXXXXXXXXXXXXXXXX
High-rise Apartment | Light.Ext | 0.041287 | X |  | Warehouse | Txfmr | 0% | XXXXXXXXXXXXXXXXXXXX
Medium Office | Fans | 0.039715 | X |  | Warehouse | Cook | 0% | XXXXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Light.Ext | 0.039444 | X |  | Warehouse | IT | 0% | XXXXXXXXXXXXXXXXXXXX
Primary School | Heat | 0.037767 | X |  | Quick-service Restaurant | SHW | 0.04713% | XXXXXXXXXXXXXXXXXXX
Standalone Retail | SHW | 0.034911 | X |  | Quick-service Restaurant | Cook | 0.07556% | XXXXXXXXXXXXXXXXXXX
Warehouse | Light.Ext | 0.032254 | X |  | Mid-rise Apartment | Heat | 0.08601% | XXXXXXXXXXXXXXXXXXX
Hospital | Ht.Rej | 0.031314 | X |  | Secondary School | SHW | 0.08651% | XXXXXXXXXXXXXXXXXXX
Small Office | Light.Ext | 0.030618 | X |  | Full-service Restaurant | Cook | 0.09906% | XXXXXXXXXXXXXXXXXXX
Secondary School | Ht.Rcvy | 0.03057 | X |  | Mid-rise Apartment | SHW | 0.1028% | XXXXXXXXXXXXXXXXXXX
Small Hotel | Light.Ext | 0.030289 | X |  | Small Office | SHW | 0.1663% | XXXXXXXXXXXXXXXXXXX
Secondary School | Heat | 0.029356 | X |  | High-rise Apartment | Equip | 0.2001% | XXXXXXXXXXXXXXXXXXX
Primary School | Refrig | 0.028908 | X |  | High-rise Apartment | SHW | 0.2214% | XXXXXXXXXXXXXXXXXXX
Warehouse | Fans | 0.027909 | X |  | Standalone Retail | Equip | 0.4407% | XXXXXXXXXXXXXXXXXXX
Mid-rise Apartment | Heat | 0.027212 | X |  | Strip Mall | Equip | 0.4428% | XXXXXXXXXXXXXXXXXXX
Primary School | Ht.Rcvy | 0.026866 | X |  | Standalone Retail | Heat | 0.4586% | XXXXXXXXXXXXXXXXXXX
Medium Office | Light.Ext | 0.025854 | X |  | Mid-rise Apartment | Equip | 0.4999% | XXXXXXXXXXXXXXXXXXX
Primary School | SHW | 0.024644 |  |  | High-rise Apartment | Heat | 0.6522% | XXXXXXXXXXXXXXXXXXX
Large Hotel | Ht.Rcvy | 0.024576 |  |  | Quick-service Restaurant | Heat | 0.6598% | XXXXXXXXXXXXXXXXXXX
Large Hotel | Heat | 0.023014 |  |  | Full-service Restaurant | Heat | 0.7057% | XXXXXXXXXXXXXXXXXXX
Mid-rise Apartment | Light.Ext | 0.022706 |  |  | Outpatient Healthcare | Equip | 0.9089% | XXXXXXXXXXXXXXXXXXX
Large Office | Pumps | 0.021646 |  |  | Primary School | Pumps | 1.282% | XXXXXXXXXXXXXXXXXXX
Hospital | Ht.Rcvy | 0.020866 |  |  | Hospital | Elevator | 1.297% | XXXXXXXXXXXXXXXXXXX
Large Office | Light.Ext | 0.020384 |  |  | Large Hotel | SHW | 1.439% | XXXXXXXXXXXXXXXXXXX
Warehouse | Cool | 0.019223 |  |  | Full-service Restaurant | SHW | 1.44% | XXXXXXXXXXXXXXXXXXX
Hospital | Light.Ext | 0.018951 |  |  | Primary School | Heat | 1.906% | XXXXXXXXXXXXXXXXXXX
Hospital | Refrig | 0.017611 |  |  | Outpatient Healthcare | Elevator | 1.955% | XXXXXXXXXXXXXXXXXXX
Secondary School | Refrig | 0.017 |  |  | Warehouse | Equip | 1.996% | XXXXXXXXXXXXXXXXXXX
Large Hotel | Refrig | 0.015034 |  |  | Standalone Retail | SHW | 2.055% | XXXXXXXXXXXXXXXXXXX
Warehouse | SHW | 0.014068 |  |  | High-rise Apartment | Elevator | 2.834% | XXXXXXXXXXXXXXXXXXX
Medium Office | SHW | 0.013955 |  |  | Large Office | Elevator | 2.834% | XXXXXXXXXXXXXXXXXXX
Large Hotel | Pumps | 0.012979 |  |  | Large Hotel | Elevator | 2.834% | XXXXXXXXXXXXXXXXXXX
Large Office | Heat | 0.012214 |  |  | Warehouse | SHW | 2.905% | XXXXXXXXXXXXXXXXXXX
High-rise Apartment | Pumps | 0.012059 |  |  | Hospital | Equip | 3.09% | XXXXXXXXXXXXXXXXXXX
Large Office | SHW | 0.010275 |  |  | Mid-rise Apartment | Elevator | 3.565% | XXXXXXXXXXXXXXXXXXX
Primary School | Light.Ext | 0.010236 |  |  | Small Hotel | Elevator | 3.566% | XXXXXXXXXXXXXXXXXXX
Secondary School | Light.Ext | 0.0095301 |  |  | Large Office | SHW | 4.133% | XXXXXXXXXXXXXXXXXXX
Secondary School | Elevator | 0.0092157 |  |  | Primary School | SHW | 4.321% | XXXXXXXXXXXXXXXXXXX
Hospital | Txfmr | 0.0086505 |  |  | Medium Office | Elevator | 5.47% | XXXXXXXXXXXXXXXXXX
Primary School | Txfmr | 0.0068195 |  |  | Large Office | Humidfy | 6.564% | XXXXXXXXXXXXXXXXXX
Medium Office | Txfmr | 0.0064454 |  |  | Medium Office | SHW | 7.057% | XXXXXXXXXXXXXXXXXX
Large Hotel | Txfmr | 0.0052024 |  |  | Small Hotel | SHW | 7.263% | XXXXXXXXXXXXXXXXXX
High-rise Apartment | Txfmr | 0.0050702 |  |  | Hospital | Humidfy | 7.759% | XXXXXXXXXXXXXXXXXX
Secondary School | Txfmr | 0.0041219 |  |  | Strip Mall | SHW | 7.863% | XXXXXXXXXXXXXXXXXX
Secondary School | Pumps | 0.0039571 |  |  | Hospital | SHW | 8.437% | XXXXXXXXXXXXXXXXXX
High-rise Apartment | Ht.Rej | 0.0034834 |  |  | Small Office | Equip | 8.542% | XXXXXXXXXXXXXXXXXX
Large Office | Txfmr | 0.0032422 |  |  | Medium Office | Equip | 8.826% | XXXXXXXXXXXXXXXXXX
Outpatient Healthcare | Pumps | 0.0024475 |  |  | Large Hotel | Equip | 9.05% | XXXXXXXXXXXXXXXXXX
Full-service Restaurant | Pumps | 0.0024157 |  |  | Large Office | Equip | 9.145% | XXXXXXXXXXXXXXXXXX
Large Office | Ht.Rcvy | 0.0020252 |  |  | Medium Office | Heat | 9.518% | XXXXXXXXXXXXXXXXXX
Primary School | Pumps | 0.00079789 |  |  | Secondary School | Equip | 9.58% | XXXXXXXXXXXXXXXXXX
Small Hotel | Pumps | 0.00017776 |  |  | Small Hotel | Equip | 11.15% | XXXXXXXXXXXXXXXXX
Standalone Retail | Ht.Rcvy | 0.00013288 |  |  | Large Office | Heat | 12.21% | XXXXXXXXXXXXXXXXX
Medium Office | Pumps | 8.2614e-05 |  |  | Secondary School | Elevator | 13.14% | XXXXXXXXXXXXXXXXX
Medium Office | Ht.Rcvy | 5.2186e-05 |  |  | Primary School | Equip | 13.6% | XXXXXXXXXXXXXXXXX
Strip Mall | Ht.Rcvy | 3.1875e-06 |  |  | Outpatient Healthcare | SHW | 14.96% | XXXXXXXXXXXXXXXXX
Small Office | Humidfy | 0 |  |  | Large Office | Fans | 21.3% | XXXXXXXXXXXXXXX
Small Office | Ht.Rej | 0 |  |  | Hospital | Light.Int | 21.66% | XXXXXXXXXXXXXXX
Small Office | Ht.Rcvy | 0 |  |  | Secondary School | Heat | 22.1% | XXXXXXXXXXXXXXX
Small Office | Pumps | 0 |  |  | Hospital | Cool | 25.27% | XXXXXXXXXXXXXX
Small Office | Refrig | 0 |  |  | High-rise Apartment | Fans | 29.53% | XXXXXXXXXXXXXX
Small Office | Elevator | 0 |  |  | Small Office | Fans | 30.24% | XXXXXXXXXXXXX
Small Office | Txfmr | 0 |  |  | Large Office | Cool | 30.93% | XXXXXXXXXXXXX
Small Office | Cook | 0 |  |  | Mid-rise Apartment | Fans | 32.99% | XXXXXXXXXXXXX
Small Office | IT | 0 |  |  | Outpatient Healthcare | Cool | 35.58% | XXXXXXXXXXXX
Medium Office | Humidfy | 0 |  |  | Strip Mall | Light.Int | 36.31% | XXXXXXXXXXXX
Medium Office | Ht.Rej | 0 |  |  | Outpatient Healthcare | Light.Int | 37.71% | XXXXXXXXXXXX
Medium Office | Refrig | 0 |  |  | High-rise Apartment | Light.Int | 38.43% | XXXXXXXXXXXX
Medium Office | Cook | 0 |  |  | Secondary School | Ht.Rcvy | 38.64% | XXXXXXXXXXXX
Medium Office | IT | 0 |  |  | Mid-rise Apartment | Light.Int | 40.18% | XXXXXXXXXXX
Large Office | Refrig | 0 |  |  | Large Hotel | Light.Ext | 40.34% | XXXXXXXXXXX
Large Office | Cook | 0 |  |  | Hospital | Light.Ext | 40.77% | XXXXXXXXXXX
Standalone Retail | Humidfy | 0 |  |  | Large Hotel | Refrig | 41.88% | XXXXXXXXXXX
Standalone Retail | Ht.Rej | 0 |  |  | Outpatient Healthcare | Pumps | 42.18% | XXXXXXXXXXX
Standalone Retail | Pumps | 0 |  |  | High-rise Apartment | Cool | 42.22% | XXXXXXXXXXX
Standalone Retail | Refrig | 0 |  |  | Hospital | Fans | 43.56% | XXXXXXXXXXX
Standalone Retail | Elevator | 0 |  |  | Large Office | Ht.Rej | 44.31% | XXXXXXXXXXX
Standalone Retail | Txfmr | 0 |  |  | Large Hotel | Fans | 44.39% | XXXXXXXXXXX
Standalone Retail | Cook | 0 |  |  | High-rise Apartment | Light.Ext | 44.81% | XXXXXXXXXXX
Standalone Retail | IT | 0 |  |  | Medium Office | Fans | 45.03% | XXXXXXXXXX
Strip Mall | Humidfy | 0 |  |  | Secondary School | Fans | 45.14% | XXXXXXXXXX
Strip Mall | Ht.Rej | 0 |  |  | Outpatient Healthcare | Fans | 46.17% | XXXXXXXXXX
Strip Mall | Pumps | 0 |  |  | Secondary School | Refrig | 46.8% | XXXXXXXXXX
Strip Mall | Refrig | 0 |  |  | Hospital | Refrig | 47.15% | XXXXXXXXXX
Strip Mall | Elevator | 0 |  |  | Primary School | Refrig | 47.52% | XXXXXXXXXX
Strip Mall | Txfmr | 0 |  |  | Full-service Restaurant | Refrig | 47.55% | XXXXXXXXXX
Strip Mall | Cook | 0 |  |  | Quick-service Restaurant | Refrig | 47.76% | XXXXXXXXXX
Strip Mall | IT | 0 |  |  | Large Hotel | Heat | 47.93% | XXXXXXXXXX
Primary School | Humidfy | 0 |  |  | Medium Office | Cool | 48.87% | XXXXXXXXXX
Primary School | Ht.Rej | 0 |  |  | Small Hotel | Fans | 48.92% | XXXXXXXXXX
Primary School | Elevator | 0 |  |  | Full-service Restaurant | Cool | 49.19% | XXXXXXXXXX
Primary School | IT | 0 |  |  | Large Office | Light.Int | 49.87% | XXXXXXXXXX
Secondary School | Humidfy | 0 |  |  | Secondary School | Cool | 52.31% | XXXXXXXXX
Secondary School | Ht.Rej | 0 |  |  | Quick-service Restaurant | Cool | 52.34% | XXXXXXXXX
Secondary School | IT | 0 |  |  | Small Hotel | Light.Ext | 53.57% | XXXXXXXXX
Outpatient Healthcare | Ht.Rej | 0 |  |  | Warehouse | Light.Ext | 54.17% | XXXXXXXXX
Outpatient Healthcare | Ht.Rcvy | 0 |  |  | Outpatient Healthcare | Heat | 54.37% | XXXXXXXXX
Outpatient Healthcare | Refrig | 0 |  |  | Large Office | Pumps | 55.09% | XXXXXXXX
Outpatient Healthcare | Txfmr | 0 |  |  | Medium Office | Light.Int | 55.5% | XXXXXXXX
Outpatient Healthcare | Cook | 0 |  |  | Standalone Retail | Light.Int | 55.89% | XXXXXXXX
Outpatient Healthcare | IT | 0 |  |  | Strip Mall | Cool | 56.17% | XXXXXXXX
Hospital | IT | 0 |  |  | Small Office | Cool | 56.34% | XXXXXXXX
Small Hotel | Humidfy | 0 |  |  | Primary School | Fans | 57.31% | XXXXXXXX
Small Hotel | Ht.Rej | 0 |  |  | Standalone Retail | Cool | 58.97% | XXXXXXXX
Small Hotel | Ht.Rcvy | 0 |  |  | Hospital | Txfmr | 59.25% | XXXXXXXX
Small Hotel | Refrig | 0 |  |  | Small Hotel | Cool | 59.81% | XXXXXXXX
Small Hotel | Txfmr | 0 |  |  | High-rise Apartment | Txfmr | 59.98% | XXXXXXXX
Small Hotel | IT | 0 |  |  | Large Office | Txfmr | 61.95% | XXXXXXX
Large Hotel | Humidfy | 0 |  |  | Large Hotel | Txfmr | 62.43% | XXXXXXX
Large Hotel | Ht.Rej | 0 |  |  | Secondary School | Txfmr | 62.93% | XXXXXXX
Large Hotel | IT | 0 |  |  | Small Hotel | Light.Int | 63.1% | XXXXXXX
Quick-service Restaurant | Humidfy | 0 |  |  | Standalone Retail | Fans | 63.35% | XXXXXXX
Quick-service Restaurant | Ht.Rej | 0 |  |  | Large Hotel | Light.Int | 63.74% | XXXXXXX
Quick-service Restaurant | Ht.Rcvy | 0 |  |  | Small Office | Light.Int | 63.82% | XXXXXXX
Quick-service Restaurant | Pumps | 0 |  |  | High-rise Apartment | Pumps | 63.84% | XXXXXXX
Quick-service Restaurant | Elevator | 0 |  |  | Primary School | Txfmr | 64.46% | XXXXXXX
Quick-service Restaurant | Txfmr | 0 |  |  | Mid-rise Apartment | Light.Ext | 64.51% | XXXXXXX
Quick-service Restaurant | IT | 0 |  |  | Strip Mall | Light.Ext | 64.55% | XXXXXXX
Quick-service Restaurant | Equip | 0 |  |  | Hospital | Pumps | 65.27% | XXXXXX
Full-service Restaurant | Humidfy | 0 |  |  | Medium Office | Txfmr | 65.34% | XXXXXX
Full-service Restaurant | Ht.Rej | 0 |  |  | Full-service Restaurant | Fans | 65.51% | XXXXXX
Full-service Restaurant | Ht.Rcvy | 0 |  |  | Large Office | Light.Ext | 65.54% | XXXXXX
Full-service Restaurant | Elevator | 0 |  |  | Quick-service Restaurant | Light.Int | 66.28% | XXXXXX
Full-service Restaurant | Txfmr | 0 |  |  | Standalone Retail | Light.Ext | 66.66% | XXXXXX
Full-service Restaurant | IT | 0 |  |  | Warehouse | Light.Int | 66.74% | XXXXXX
Full-service Restaurant | Equip | 0 |  |  | Quick-service Restaurant | Fans | 67.48% | XXXXXX
Mid-rise Apartment | Humidfy | 0 |  |  | Quick-service Restaurant | Light.Ext | 68.05% | XXXXXX
Mid-rise Apartment | Ht.Rej | 0 |  |  | Full-service Restaurant | Light.Ext | 68.07% | XXXXXX
Mid-rise Apartment | Ht.Rcvy | 0 |  |  | Secondary School | Light.Ext | 68.77% | XXXXXX
Mid-rise Apartment | Pumps | 0 |  |  | Primary School | Light.Ext | 69.43% | XXXXXX
Mid-rise Apartment | Refrig | 0 |  |  | Hospital | Ht.Rej | 70.78% | XXXXX
Mid-rise Apartment | Txfmr | 0 |  |  | Strip Mall | Fans | 71.32% | XXXXX
Mid-rise Apartment | Cook | 0 |  |  | Hospital | Heat | 71.46% | XXXXX
Mid-rise Apartment | IT | 0 |  |  | Warehouse | Heat | 72.48% | XXXXX
High-rise Apartment | Humidfy | 0 |  |  | Full-service Restaurant | Light.Int | 72.95% | XXXXX
High-rise Apartment | Ht.Rcvy | 0 |  |  | Secondary School | Pumps | 73.07% | XXXXX
High-rise Apartment | Refrig | 0 |  |  | Mid-rise Apartment | Cool | 75.37% | XXXX
High-rise Apartment | Cook | 0 |  |  | Secondary School | Light.Int | 76.03% | XXXX
High-rise Apartment | IT | 0 |  |  | Outpatient Healthcare | Light.Ext | 76.24% | XXXX
Warehouse | Humidfy | 0 |  |  | Primary School | Light.Int | 76.75% | XXXX
Warehouse | Ht.Rej | 0 |  |  | Small Office | Light.Ext | 77.4% | XXXX
Warehouse | Ht.Rcvy | 0 |  |  | High-rise Apartment | Ht.Rej | 79.32% | XXXX
Warehouse | Pumps | 0 |  |  | Medium Office | Light.Ext | 79.49% | XXXX
Warehouse | Refrig | 0 |  |  | Primary School | Cool | 81.79% | XXX
Warehouse | Elevator | 0 |  |  | Large Hotel | Pumps | 94.31% | X
Warehouse | Txfmr | 0 |  |  | Large Hotel | Cool | 105.3%
Warehouse | Cook | 0 |  |  | Warehouse | Cool | 109.2%
Warehouse | IT | 0 |  |  | Warehouse | Fans | 133.2%

## National
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | US All Buildings |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [8 empty] | Building Type: | US All Buildings |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [8 empty] | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | US All Buildings |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | US All Buildings | [17 empty] | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.16002 | 0.031662 | 0.10117 | 0.071609 | 0.0095301 | 0.18015 | 0.0039433 | 0.11576 | 0.0067111 | 0.0051795 | 0.0098186 | 0.072276 | 0.0023264 | 0.085529 | 0.021334 | 0.28389 | 1.1609 |  | STD2019 | 5.1362 | 1.0163 | 5.9499 | 6.4423 | 0.30589 | 5.7826 | 0.12657 | 3.7156 | 0.21541 | 0.16625 | 0.31516 | 2.3199 | 0.074674 | 4.8739 | 0.68478 | 9.2143 | 46.3397 |  | STD2019 | 1.5053 | 0.29785 | 0.58829 | 0.1163 | 0.089652 | 1.6948 | 0.037096 | 1.089 | 0.063134 | 0.048725 | 0.092367 | 0.67993 | 0.021886 | 0.5183 | 0.2007 | 2.6569 | 9.7002 |  | STD2019 | 0 | 0 | 0.039426 | 0.060455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.13243 |  | STD2019 | 15.7595 | 3.1182 | 10.4682 | 7.8253 | 0.93857 | 17.7426 | 0.38835 | 11.4005 | 0.66095 | 0.51011 | 0.96699 | 7.1182 | 0.22912 | 8.8203 | 2.1011 | 27.9777 | 116.0256
STD2016 | 0.19055 | 0.031662 | 0.1012 | 0.081003 | 0.0094998 | 0.18863 | 0.0043926 | 0.11819 | 0.0075122 | 0.0059289 | 0.014708 | 0.072276 | 0.0023428 | 0.085529 | 0.021334 | 0.28389 | 1.2186 |  | STD2016 | 6.1161 | 1.0163 | 5.9517 | 7.3329 | 0.30492 | 6.0548 | 0.14099 | 3.7935 | 0.24113 | 0.1903 | 0.47208 | 2.3199 | 0.0752 | 4.8739 | 0.68478 | 9.2143 | 48.7828 |  | STD2016 | 1.7925 | 0.29785 | 0.58847 | 0.12544 | 0.089368 | 1.7745 | 0.041323 | 1.1118 | 0.07067 | 0.055775 | 0.13836 | 0.67993 | 0.02204 | 0.5183 | 0.2007 | 2.6569 | 10.164 |  | STD2016 | 0 | 0 | 0.039438 | 0.069049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.14103 |  | STD2016 | 18.766 | 3.1182 | 10.4713 | 8.8603 | 0.93559 | 18.5778 | 0.43261 | 11.6396 | 0.73984 | 0.58391 | 1.4485 | 7.1182 | 0.23074 | 8.8203 | 2.1011 | 27.9777 | 121.8216
STD2013 | 0.24995 | 0.050575 | 0.10157 | 0.07511 | 0.0087107 | 0.19761 | 0.0050226 | 0.12262 | 0.010392 | 0.0067302 | 0.014706 | 0.072276 | 0.0033346 | 0.085529 | 0.021334 | 0.28389 | 1.3094 |  | STD2013 | 8.0228 | 1.6233 | 5.9898 | 6.6227 | 0.2796 | 6.3428 | 0.16122 | 3.9357 | 0.33355 | 0.21602 | 0.47204 | 2.3199 | 0.10703 | 4.8739 | 0.68478 | 9.2143 | 51.1995 |  | STD2013 | 2.3514 | 0.47578 | 0.5884 | 0.1401 | 0.081945 | 1.859 | 0.04725 | 1.1535 | 0.097757 | 0.063313 | 0.13835 | 0.67993 | 0.03137 | 0.5183 | 0.2007 | 2.6569 | 11.0839 |  | STD2013 | 0 | 0 | 0.039822 | 0.061446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.13381 |  | STD2013 | 24.6164 | 4.9809 | 10.5125 | 8.1828 | 0.85788 | 19.4615 | 0.49466 | 12.0758 | 1.0234 | 0.66282 | 1.4483 | 7.1182 | 0.32841 | 8.8203 | 2.1011 | 27.9777 | 130.6628
STD2010 | 0.28167 | 0.050575 | 0.10167 | 0.10517 | 0.013043 | 0.22779 | 0.0053585 | 0.14989 | 0.0086769 | 0.0082811 | 0.018293 | 0.072453 | 0.003476 | 0.085537 | 0.021334 | 0.29137 | 1.4446 |  | STD2010 | 9.0411 | 1.6233 | 5.9936 | 9.0621 | 0.41865 | 7.3114 | 0.172 | 4.811 | 0.27851 | 0.2658 | 0.58716 | 2.3256 | 0.11157 | 4.8741 | 0.68478 | 9.4544 | 57.0152 |  | STD2010 | 2.6498 | 0.47578 | 0.58926 | 0.22454 | 0.1227 | 2.1429 | 0.050409 | 1.41 | 0.081627 | 0.077903 | 0.17209 | 0.68159 | 0.0327 | 0.51838 | 0.2007 | 2.7272 | 12.1576 |  | STD2010 | 0 | 0 | 0.03983 | 0.08296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.15533 |  | STD2010 | 27.7407 | 4.9809 | 10.5224 | 11.4183 | 1.2845 | 22.4336 | 0.52773 | 14.7617 | 0.85455 | 0.81556 | 1.8016 | 7.1356 | 0.34234 | 8.8211 | 2.1011 | 28.7143 | 144.2559
STD2007 | 0.36261 | 0.085893 | 0.1024 | 0.14899 | 0.012933 | 0.30076 | 0.0088827 | 0.20958 | 0.0071155 | 0.016206 | 0.018237 | 0.074408 | 0.0061645 | 0.085569 | 0.021334 | 0.29682 | 1.7579 |  | STD2007 | 11.6389 | 2.757 | 6.0282 | 12.5273 | 0.41512 | 9.6537 | 0.28511 | 6.7272 | 0.22839 | 0.52017 | 0.58536 | 2.3883 | 0.19787 | 4.8752 | 0.68478 | 9.6296 | 69.1421 |  | STD2007 | 3.4112 | 0.80802 | 0.59457 | 0.35994 | 0.12166 | 2.8293 | 0.083562 | 1.9716 | 0.066938 | 0.15245 | 0.17156 | 0.69998 | 0.057992 | 0.51868 | 0.2007 | 2.7786 | 14.8268 |  | STD2007 | 0 | 0 | 0.039995 | 0.11299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.18553 |  | STD2007 | 35.7116 | 8.4592 | 10.5961 | 16.1182 | 1.2737 | 29.6202 | 0.87481 | 20.6409 | 0.70077 | 1.596 | 1.7961 | 7.3281 | 0.60712 | 8.8243 | 2.1011 | 29.2518 | 175.5
STD2004 | 0.36021 | 0.085893 | 0.1024 | 0.18437 | 0.013714 | 0.32824 | 0.0089066 | 0.23862 | 0.015202 | 0.01691 | 0.018394 | 0.074408 | 0.0061645 | 0.085569 | 0.021334 | 0.29682 | 1.8572 |  | STD2004 | 11.5619 | 2.757 | 6.0276 | 15.5472 | 0.4402 | 10.5359 | 0.28588 | 7.6592 | 0.48795 | 0.54277 | 0.5904 | 2.3883 | 0.19787 | 4.8752 | 0.68478 | 9.6296 | 74.2117 |  | STD2004 | 3.3886 | 0.80802 | 0.59464 | 0.43923 | 0.12902 | 3.0879 | 0.083787 | 2.2448 | 0.14301 | 0.15908 | 0.17304 | 0.69998 | 0.057992 | 0.51868 | 0.2007 | 2.7786 | 15.507 |  | STD2004 | 0 | 0 | 0.039986 | 0.14049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.21302 |  | STD2004 | 35.4753 | 8.4592 | 10.5958 | 19.9534 | 1.3507 | 32.3273 | 0.87717 | 23.5005 | 1.4972 | 1.6654 | 1.8115 | 7.3281 | 0.60712 | 8.8243 | 2.1011 | 29.2518 | 185.6259
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | -0.0023989 | 0 | -1.6231e-06 | 0.035373 | 0.00078157 | 0.027487 | 2.389e-05 | 0.029036 | 0.0080864 | 0.00070406 | 0.00015678 | 0 | 0 | 0 | 0 | 0 | 0.099249 |  | 2004-2007 | -0.077 | 0 | -0.00066059 | 3.0199 | 0.025087 | 0.88227 | 0.00076682 | 0.932 | 0.25956 | 0.022599 | 0.0050322 | 0 | 0 | 0 | 0 | 0 | 5.0696 |  | 2004-2007 | -0.022567 | 0 | 6.6574e-05 | 0.079298 | 0.0073525 | 0.25858 | 0.00022474 | 0.27315 | 0.076072 | 0.0066233 | 0.0014749 | 0 | 0 | 0 | 0 | 0 | 0.68028 |  | 2004-2007 | 0 | 0 | -8.8775e-06 | 0.027494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027485 |  | 2004-2007 | -0.23626 | 0 | -0.00027334 | 3.8352 | 0.076973 | 2.7071 | 0.0023528 | 2.8596 | 0.7964 | 0.06934 | 0.01544 | 0 | 0 | 0 | 0 | 0 | 10.1259
2007-2010 | 0.080935 | 0.035318 | 0.00072641 | 0.043823 | -0.00011014 | 0.072971 | 0.0035242 | 0.059696 | -0.0015614 | 0.0079247 | -5.5815e-05 | 0.0019555 | 0.0026885 | 3.2235e-05 | 0 | 0.0054579 | 0.31333 |  | 2007-2010 | 2.5978 | 1.1336 | 0.034643 | 3.4651 | -0.0035352 | 2.3422 | 0.11312 | 1.9161 | -0.050119 | 0.25437 | -0.0017915 | 0.062767 | 0.086295 | 0.0010347 | 0 | 0.17519 | 12.1269 |  | 2007-2010 | 0.76138 | 0.33225 | 0.0053102 | 0.13539 | -0.0010361 | 0.68647 | 0.033153 | 0.56158 | -0.014689 | 0.074551 | -0.00052507 | 0.018396 | 0.025292 | 0.00030325 | 0 | 0.051344 | 2.6692 |  | 2007-2010 | 0 | 0 | 0.00016524 | 0.030032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030197 |  | 2007-2010 | 7.9709 | 3.4783 | 0.073654 | 4.6999 | -0.010847 | 7.1866 | 0.34708 | 5.8792 | -0.15378 | 0.78047 | -0.005497 | 0.19259 | 0.26478 | 0.0031747 | 0 | 0.53752 | 31.2441
2010-2013 | 0.031723 | 0 | 9.9512e-05 | 0.030059 | 0.0043322 | 0.030179 | 0.00033583 | 0.027272 | -0.0017147 | 0.0015509 | 0.0035865 | 0.00017667 | 0.00014139 | 8.3468e-06 | 0 | 0.0074786 | 0.13523 |  | 2010-2013 | 1.0182 | 0 | 0.0037279 | 2.4395 | 0.13906 | 0.96867 | 0.010779 | 0.87537 | -0.055037 | 0.049781 | 0.11512 | 0.0056707 | 0.0045383 | 0.00026791 | 0 | 0.24005 | 5.8157 |  | 2010-2013 | 0.29843 | 0 | 0.00086435 | 0.084439 | 0.040755 | 0.2839 | 0.0031593 | 0.25656 | -0.01613 | 0.01459 | 0.033739 | 0.001662 | 0.0013301 | 7.8521e-05 | 0 | 0.070354 | 1.0737 |  | 2010-2013 | 0 | 0 | 7.7869e-06 | 0.021514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021522 |  | 2010-2013 | 3.1242 | 0 | 0.0099 | 3.2354 | 0.42666 | 2.9722 | 0.033074 | 2.6859 | -0.16887 | 0.15274 | 0.35322 | 0.017399 | 0.013925 | 0.00082203 | 0 | 0.73653 | 13.5932
2013-2016 | 0.059404 | 0.018914 | 0.00036873 | -0.0058924 | -0.00078908 | 0.0089732 | 0.00063004 | 0.0044291 | 0.0028794 | 0.00080125 | -1.3809e-06 | 0 | 0.00099177 | 0 | 0 | 0 | 0.090708 |  | 2013-2016 | 1.9067 | 0.60708 | 0.038153 | -0.71027 | -0.025328 | 0.28802 | 0.020223 | 0.14216 | 0.092421 | 0.025718 | -4.4323e-05 | 0 | 0.031834 | 0 | 0 | 0 | 2.4167 |  | 2013-2016 | 0.55884 | 0.17793 | -7.085e-05 | 0.014661 | -0.0074231 | 0.084414 | 0.005927 | 0.041666 | 0.027087 | 0.0075376 | -1.299e-05 | 0 | 0.0093299 | 0 | 0 | 0 | 0.91988 |  | 2013-2016 | 0 | 0 | 0.00038394 | -0.0076029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0072189 |  | 2013-2016 | 5.8505 | 1.8627 | 0.041223 | -0.67751 | -0.077713 | 0.88373 | 0.06205 | 0.4362 | 0.28357 | 0.078912 | -0.000136 | 0 | 0.097675 | 0 | 0 | 0 | 8.8412
2016-2019 | 0.030527 | 0 | 3.023e-05 | 0.009394 | -3.0238e-05 | 0.0084802 | 0.00044932 | 0.002428 | 0.00080112 | 0.00074939 | 0.004889 | 0 | 1.6409e-05 | 0 | 0 | 0 | 0.057735 |  | 2016-2019 | 0.97986 | 0 | 0.0017782 | 0.89063 | -0.00097058 | 0.27219 | 0.014422 | 0.077933 | 0.025714 | 0.024054 | 0.15693 | 0 | 0.0005267 | 0 | 0 | 0 | 2.4431 |  | 2016-2019 | 0.28718 | 0 | 0.00017572 | 0.0091375 | -0.00028446 | 0.079776 | 0.0042269 | 0.022841 | 0.0075364 | 0.0070497 | 0.045992 | 0 | 0.00015437 | 0 | 0 | 0 | 0.46378 |  | 2016-2019 | 0 | 0 | 1.1786e-05 | 0.0085946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086063 |  | 2016-2019 | 3.0065 | 0 | 0.0031279 | 1.035 | -0.002978 | 0.83517 | 0.044251 | 0.23912 | 0.078898 | 0.073804 | 0.48149 | 0 | 0.0016161 | 0 | 0 | 0 | 5.796
2004-2019 | 0.20019 | 0.054231 | 0.0012233 | 0.11276 | 0.0041844 | 0.14809 | 0.0049633 | 0.12286 | 0.0084908 | 0.01173 | 0.0085751 | 0.0021322 | 0.0038381 | 4.0582e-05 | 0 | 0.012936 | 0.69625 |  | 2004-2019 | 6.4257 | 1.7407 | 0.077641 | 9.1049 | 0.13431 | 4.7534 | 0.15931 | 3.9436 | 0.27254 | 0.37652 | 0.27524 | 0.068438 | 0.12319 | 0.0013026 | 0 | 0.41523 | 27.872 |  | 2004-2019 | 1.8833 | 0.51017 | 0.006346 | 0.32293 | 0.039364 | 1.3931 | 0.046691 | 1.1558 | 0.079876 | 0.11035 | 0.080668 | 0.020058 | 0.036106 | 0.00038177 | 0 | 0.1217 | 5.8068 |  | 2004-2019 | 0 | 0 | 0.00055988 | 0.080031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080591 |  | 2004-2019 | 19.7159 | 5.341 | 0.12763 | 12.1281 | 0.4121 | 14.5847 | 0.48881 | 12.1001 | 0.83622 | 1.1553 | 0.84452 | 0.20999 | 0.378 | 0.0039967 | 0 | 1.2741 | 69.6003
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | -0.666% | 0% | -0.001585% | 19.19% | 5.699% | 8.374% | 0.2682% | 12.17% | 53.19% | 4.164% | 0.8523% | 0% | 0% | 0% | 0% | 0% | 5.344% |  | 2004-2007 | -0.666% | 0% | -0.01096% | 19.42% | 5.699% | 8.374% | 0.2682% | 12.17% | 53.19% | 4.164% | 0.8523% | 0% | 0% | 0% | 0% | 0% | 6.831% |  | 2004-2007 | -0.666% | 0% | 0.0112% | 18.05% | 5.699% | 8.374% | 0.2682% | 12.17% | 53.19% | 4.164% | 0.8523% | 0% | 0% | 0% | 0% | 0% | 4.387% |  | 2004-2007 |  |  | -0.0222% | 19.57% | [9 empty] | 0% |  | 0% | 12.9% |  | 2004-2007 | -0.666% | 0% | -0.00258% | 19.22% | 5.699% | 8.374% | 0.2682% | 12.17% | 53.19% | 4.164% | 0.8523% | 0% | 0% | 0% | 0% | 0% | 5.455%
2007-2010 | 22.32% | 41.12% | 0.7094% | 29.41% | -0.8516% | 24.26% | 39.68% | 28.48% | -21.94% | 48.9% | -0.3061% | 2.628% | 43.61% | 0.03767% | 0% | 1.839% | 17.82% |  | 2007-2010 | 22.32% | 41.12% | 0.5747% | 27.66% | -0.8516% | 24.26% | 39.68% | 28.48% | -21.94% | 48.9% | -0.3061% | 2.628% | 43.61% | 0.02122% | 0% | 1.819% | 17.54% |  | 2007-2010 | 22.32% | 41.12% | 0.8931% | 37.62% | -0.8516% | 24.26% | 39.68% | 28.48% | -21.94% | 48.9% | -0.3061% | 2.628% | 43.61% | 0.05846% | 0% | 1.848% | 18% |  | 2007-2010 |  |  | 0.4132% | 26.58% | [9 empty] | 0% |  | 0% | 16.28% |  | 2007-2010 | 22.32% | 41.12% | 0.6951% | 29.16% | -0.8516% | 24.26% | 39.68% | 28.48% | -21.94% | 48.9% | -0.3061% | 2.628% | 43.61% | 0.03598% | 0% | 1.838% | 17.8%
2010-2013 | 11.26% | 0% | 0.09788% | 28.58% | 33.22% | 13.25% | 6.267% | 18.2% | -19.76% | 18.73% | 19.61% | 0.2438% | 4.068% | 0.009758% | 0% | 2.567% | 9.361% |  | 2010-2013 | 11.26% | 0% | 0.0622% | 26.92% | 33.22% | 13.25% | 6.267% | 18.2% | -19.76% | 18.73% | 19.61% | 0.2438% | 4.068% | 0.005497% | 0% | 2.539% | 10.2% |  | 2010-2013 | 11.26% | 0% | 0.1467% | 37.61% | 33.22% | 13.25% | 6.267% | 18.2% | -19.76% | 18.73% | 19.61% | 0.2438% | 4.068% | 0.01515% | 0% | 2.58% | 8.832% |  | 2010-2013 |  |  | 0.01955% | 25.93% | [9 empty] | 0% |  | 0% | 13.85% |  | 2010-2013 | 11.26% | 0% | 0.09408% | 28.34% | 33.22% | 13.25% | 6.267% | 18.2% | -19.76% | 18.73% | 19.61% | 0.2438% | 4.068% | 0.009319% | 0% | 2.565% | 9.423%
2013-2016 | 23.77% | 37.4% | 0.363% | -7.845% | -9.059% | 4.541% | 12.54% | 3.612% | 27.71% | 11.91% | -0.00939% | 0% | 29.74% | 0% | 0% | 0% | 6.928% |  | 2013-2016 | 23.77% | 37.4% | 0.637% | -10.72% | -9.059% | 4.541% | 12.54% | 3.612% | 27.71% | 11.91% | -0.00939% | 0% | 29.74% | 0% | 0% | 0% | 4.72% |  | 2013-2016 | 23.77% | 37.4% | -0.01204% | 10.46% | -9.059% | 4.541% | 12.54% | 3.612% | 27.71% | 11.91% | -0.00939% | 0% | 29.74% | 0% | 0% | 0% | 8.299% |  | 2013-2016 |  |  | 0.9641% | -12.37% | [9 empty] | 0% |  | 0% | -5.395% |  | 2013-2016 | 23.77% | 37.4% | 0.3921% | -8.28% | -9.059% | 4.541% | 12.54% | 3.612% | 27.71% | 11.91% | -0.00939% | 0% | 29.74% | 0% | 0% | 0% | 6.766%
2016-2019 | 16.02% | 0% | 0.02987% | 11.6% | -0.3183% | 4.496% | 10.23% | 2.054% | 10.66% | 12.64% | 33.24% | 0% | 0.7004% | 0% | 0% | 0% | 4.738% |  | 2016-2019 | 16.02% | 0% | 0.02988% | 12.15% | -0.3183% | 4.496% | 10.23% | 2.054% | 10.66% | 12.64% | 33.24% | 0% | 0.7004% | 0% | 0% | 0% | 5.008% |  | 2016-2019 | 16.02% | 0% | 0.02986% | 7.284% | -0.3183% | 4.496% | 10.23% | 2.054% | 10.66% | 12.64% | 33.24% | 0% | 0.7004% | 0% | 0% | 0% | 4.563% |  | 2016-2019 |  |  | 0.02988% | 12.45% | [9 empty] | 0% |  | 0% | 6.102% |  | 2016-2019 | 16.02% | 0% | 0.02987% | 11.68% | -0.3183% | 4.496% | 10.23% | 2.054% | 10.66% | 12.64% | 33.24% | 0% | 0.7004% | 0% | 0% | 0% | 4.758%
2004-2019 | 55.58% | 63.14% | 1.195% | 61.16% | 30.51% | 45.12% | 55.73% | 51.49% | 55.85% | 69.37% | 46.62% | 2.865% | 62.26% | 0.04743% | 0% | 4.358% | 37.49% |  | 2004-2019 | 55.58% | 63.14% | 1.288% | 58.56% | 30.51% | 45.12% | 55.73% | 51.49% | 55.85% | 69.37% | 46.62% | 2.865% | 62.26% | 0.02672% | 0% | 4.312% | 37.56% |  | 2004-2019 | 55.58% | 63.14% | 1.067% | 73.52% | 30.51% | 45.12% | 55.73% | 51.49% | 55.85% | 69.37% | 46.62% | 2.865% | 62.26% | 0.0736% | 0% | 4.38% | 37.45% |  | 2004-2019 |  |  | 1.4% | 56.97% | [9 empty] | 0% |  | 0% | 37.83% |  | 2004-2019 | 55.58% | 63.14% | 1.205% | 60.78% | 30.51% | 45.12% | 55.73% | 51.49% | 55.85% | 69.37% | 46.62% | 2.865% | 62.26% | 0.04529% | 0% | 4.355% | 37.49%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | US All Buildings | [23 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.13866 | 0.030618 | 0.096682 | 0.047588 | 0 | 0.11542 | 0 | 0.092015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.78022 | 3.798% | Small Office | 4.4507 | 0.98277 | 3.1033 | 2.1298 | 0 | 3.7048 | 0 | 2.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.6457 | 3.798% | Small Office | 1.3044 | 0.28803 | 0.90952 | 0.36666 | 0 | 1.0858 | 0 | 0.86562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.2588 | 3.798% | Small Office | 0 | 0 | 0 | 0.0087873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0087873 | 3.798% | Small Office | 13.6561 | 3.0154 | 9.5218 | 4.799 | 0 | 11.3675 | 0 | 9.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 76.9527 | 3.798%
Medium Office | 0.13597 | 0.025854 | 0.013955 | 0.05761 | 0 | 0.15767 | 0 | 0.039715 | 5.2186e-05 | 8.2614e-05 | 0 | 0.09109 | 0.0064454 | 0 | 0 | 0.32202 | 0.85045 | 5.009% | Medium Office | 4.3642 | 0.82984 | 1.4239 | 3.2402 | 0 | 5.0607 | 0 | 1.2748 | 0.0016751 | 0.0026517 | 0 | 2.9238 | 0.20688 | 0 | 0 | 10.3361 | 29.6648 | 5.009% | Medium Office | 1.2791 | 0.24321 | 0 | 0.35486 | 0 | 1.4832 | 0 | 0.37362 | 0.00049093 | 0.00077718 | 0 | 0.85692 | 0.060634 | 0 | 0 | 3.0293 | 7.6821 | 5.009% | Medium Office | 0 | 0 | 0.014239 | 0.020294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034533 | 5.009% | Medium Office | 13.3907 | 2.5462 | 1.5564 | 5.9332 | 0 | 15.5278 | 0 | 3.9114 | 0.0051396 | 0.0081363 | 0 | 8.9711 | 0.63478 | 0 | 0 | 31.7141 | 84.1988 | 5.009%
Large Office | 0.15298 | 0.020384 | 0.010275 | 0.012214 | 0.055024 | 0.16797 | 0.056842 | 0.12304 | 0.0020252 | 0.021646 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.6077 | 3.855% | Large Office | 4.9103 | 0.65429 | 1.0485 | 1.2463 | 1.7661 | 5.3915 | 1.8245 | 3.9495 | 0.065004 | 0.6948 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 53.1759 | 3.855% | Large Office | 1.4391 | 0.19176 | 0 | 0 | 0.51763 | 1.5802 | 0.53473 | 1.1575 | 0.019052 | 0.20363 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.9124 | 3.855% | Large Office | 0 | 0 | 0.010485 | 0.012463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022948 | 3.855% | Large Office | 15.0663 | 2.0076 | 1.146 | 1.3623 | 5.4191 | 16.5426 | 5.5981 | 12.1181 | 0.19945 | 2.1318 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 158.626 | 3.855%
Standalone Retail | 0.28499 | 0.046105 | 0.034911 | 0.11616 | 0 | 0.21956 | 0 | 0.17285 | 0.00013288 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1071 | 10.94% | Standalone Retail | 9.1474 | 1.4799 | 3.5623 | 11.8533 | 0 | 7.0474 | 0 | 5.5482 | 0.0042652 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.1029 | 10.94% | Standalone Retail | 2.681 | 0.43372 | 0 | 0 | 0 | 2.0655 | 0 | 1.6261 | 0.0012501 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.9939 | 10.94% | Standalone Retail | 0 | 0 | 0.035623 | 0.11853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15416 | 10.94% | Standalone Retail | 28.067 | 4.5406 | 3.8936 | 12.9557 | 0 | 21.6233 | 0 | 17.0235 | 0.013087 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 111.0066 | 10.94%
Strip Mall | 0.52845 | 0.078047 | 0.081896 | 0.11357 | 0 | 0.22672 | 0 | 0.14392 | 3.1875e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3408 | 3.712% | Strip Mall | 16.962 | 2.5051 | 2.6287 | 11.589 | 0 | 7.2772 | 0 | 4.6195 | 0.00010231 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 50.9813 | 3.712% | Strip Mall | 4.9713 | 0.73422 | 0.77042 | 0 | 0 | 2.1328 | 0 | 1.3539 | 2.9986e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.5452 | 3.712% | Strip Mall | 0 | 0 | 0 | 0.11589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11589 | 3.712% | Strip Mall | 52.0444 | 7.6865 | 8.0656 | 12.6667 | 0 | 22.3284 | 0 | 14.174 | 0.00031393 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 133.5337 | 3.712%
Primary School | 0.11461 | 0.010236 | 0.024644 | 0.037767 | 0 | 0.20435 | 0 | 0.1231 | 0.026866 | 0.00079789 | 0.028908 | 0 | 0.0068195 | 0.10513 | 0 | 0.37841 | 1.0616 | 4.828% | Primary School | 3.6786 | 0.32856 | 1.793 | 3.8538 | 0 | 6.5593 | 0 | 3.9513 | 0.86235 | 0.025611 | 0.92788 | 0 | 0.21889 | 6.5458 | 0 | 12.1461 | 40.8912 | 4.828% | Primary School | 1.0781 | 0.096296 | 0.097071 | 0 | 0 | 1.9224 | 0 | 1.1581 | 0.25274 | 0.007506 | 0.27195 | 0 | 0.064153 | 0.56245 | 0 | 3.5598 | 9.0706 | 4.828% | Primary School | 0 | 0 | 0.014618 | 0.038538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.099423 | 4.828% | Primary School | 11.2871 | 1.0081 | 2.614 | 4.2122 | 0 | 20.1258 | 0 | 12.1238 | 2.6459 | 0.078581 | 2.847 | 0 | 0.67162 | 10.9453 | 0 | 37.2677 | 105.8271 | 4.828%
Secondary School | 0.11484 | 0.0095301 | 0.04253 | 0.029356 | 0 | 0.23127 | 0 | 0.11076 | 0.03057 | 0.0039571 | 0.017 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.94624 | 10.92% | Secondary School | 3.6861 | 0.3059 | 2.8272 | 2.9956 | 0 | 7.4232 | 0 | 3.5552 | 0.98125 | 0.12701 | 0.54567 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 35.5649 | 10.92% | Secondary School | 1.0803 | 0.089653 | 0.20343 | 0 | 0 | 2.1756 | 0 | 1.042 | 0.28759 | 0.037226 | 0.15993 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 8.2032 | 10.92% | Secondary School | 0 | 0 | 0.021331 | 0.029956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.075757 | 10.92% | Secondary School | 11.31 | 0.93858 | 4.4612 | 3.2741 | 0 | 22.7765 | 0 | 10.9085 | 3.0107 | 0.38971 | 1.6743 | 0.90762 | 0.40595 | 7.6313 | 0 | 26.4707 | 94.1593 | 10.92%
Outpatient Healthcare | 0.27495 | 0.039444 | 0.049662 | 0.23478 | 0.094266 | 0.51799 | 0 | 0.24466 | 0 | 0.0024475 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8206 | 3.419% | Outpatient Healthcare | 8.8254 | 1.2661 | 5.0676 | 15.0651 | 3.0257 | 16.6263 | 0 | 7.8529 | 0 | 0.07856 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 104.5255 | 3.419% | Outpatient Healthcare | 2.5866 | 0.37106 | 0 | 1.196 | 0.88679 | 4.8729 | 0 | 2.3016 | 0 | 0.023025 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.6522 | 3.419% | Outpatient Healthcare | 0 | 0 | 0.050676 | 0.10984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20412 | 3.419% | Outpatient Healthcare | 27.0788 | 3.8846 | 5.5389 | 24.527 | 9.2838 | 51.0144 | 0 | 24.095 | 0 | 0.24105 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 280.3943 | 3.419%
Hospital | 0.40087 | 0.018951 | 0.049217 | 0.10909 | 0.092557 | 0.34032 | 0.031314 | 0.35447 | 0.020866 | 0.045344 | 0.017611 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.7423 | 4.523% | Hospital | 12.8669 | 0.60829 | 4.7963 | 10.1423 | 2.9709 | 10.9237 | 1.0051 | 11.3778 | 0.66975 | 1.4554 | 0.56526 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 105.3915 | 4.523% | Hospital | 3.7711 | 0.17828 | 0.030374 | 0.13307 | 0.87072 | 3.2015 | 0.29458 | 3.3347 | 0.19629 | 0.42656 | 0.16567 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 23.4622 | 4.523% | Hospital | 0 | 0 | 0.046927 | 0.096883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.25339 | 4.523% | Hospital | 39.4794 | 1.8664 | 5.4471 | 11.9824 | 9.1155 | 33.517 | 3.084 | 34.9105 | 2.055 | 4.4657 | 1.7344 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 273.3206 | 4.523%
Small Hotel | 0.12596 | 0.030289 | 0.12352 | 0.068337 | 0 | 0.20535 | 0 | 0.11032 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1358 | 1.588% | Small Hotel | 4.043 | 0.9722 | 12.6038 | 2.9114 | 0 | 6.5912 | 0 | 3.5412 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.1535 | 1.588% | Small Hotel | 1.1849 | 0.28493 | 0 | 0.5463 | 0 | 1.9318 | 0 | 1.0379 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.5742 | 1.588% | Small Hotel | 0 | 0 | 0.12604 | 0.010475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22898 | 1.588% | Small Hotel | 12.405 | 2.983 | 13.776 | 6.8641 | 0 | 20.2238 | 0 | 10.8653 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 114.7909 | 1.588%
Large Hotel | 0.12731 | 0.044207 | 0.17838 | 0.023014 | 0 | 0.31212 | 0 | 0.16888 | 0.024576 | 0.012979 | 0.015034 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.673 | 4.219% | Large Hotel | 4.0865 | 1.4189 | 16.6703 | 2.3484 | 0 | 10.0184 | 0 | 5.4208 | 0.78884 | 0.4166 | 0.48256 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 75.7719 | 4.219% | Large Hotel | 1.1977 | 0.41587 | 0.20607 | 0 | 0 | 2.9362 | 0 | 1.5888 | 0.2312 | 0.1221 | 0.14143 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 12.7704 | 4.219% | Large Hotel | 0 | 0 | 0.15967 | 0.023484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32199 | 4.219% | Large Hotel | 12.5384 | 4.3537 | 19.6094 | 2.5668 | 0 | 30.7394 | 0 | 16.6327 | 2.4204 | 1.2783 | 1.4806 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 168.8868 | 4.219%
Quick-service Restaurant | 0.29915 | 0.10383 | 0.65808 | 0.6553 | 0 | 1.0467 | 0 | 0.65509 | 0 | 0 | 0.67217 | 0 | 0 | 4.5293 | 0 | 0 | 8.6195 | 0.3319% | Quick-service Restaurant | 9.6022 | 3.3328 | 67.1511 | 66.8672 | 0 | 33.5954 | 0 | 21.0269 | 0 | 0 | 21.5751 | 0 | 0 | 269.3289 | 0 | 0 | 492.4796 | 0.3319% | Quick-service Restaurant | 2.8142 | 0.97679 | 0 | 0 | 0 | 9.8463 | 0 | 6.1626 | 0 | 0 | 6.3233 | 0 | 0 | 25.937 | 0 | 0 | 52.0602 | 0.3319% | Quick-service Restaurant | 0 | 0 | 0.67151 | 0.66867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1485 | 0.3319% | Quick-service Restaurant | 29.4623 | 10.2261 | 73.3961 | 73.0858 | 0 | 103.0805 | 0 | 64.5165 | 0 | 0 | 66.1988 | 0 | 0 | 469.1836 | 0 | 0 | 889.1496 | 0.3319%
Full-service Restaurant | 0.26975 | 0.10005 | 0.92483 | 0.46682 | 0 | 0.9176 | 0 | 0.56104 | 0 | 0.0024157 | 0.29892 | 0 | 0 | 3.0318 | 0 | 0 | 6.5733 | 0.9718% | Full-service Restaurant | 8.6582 | 3.2114 | 66.0368 | 47.635 | 0 | 29.4529 | 0 | 18.0081 | 0 | 0.077539 | 9.5945 | 0 | 0 | 152.7879 | 0 | 0 | 335.4624 | 0.9718% | Full-service Restaurant | 2.5376 | 0.94119 | 3.8109 | 0 | 0 | 8.6322 | 0 | 5.2779 | 0 | 0.022725 | 2.812 | 0 | 0 | 21.0604 | 0 | 0 | 45.0949 | 0.9718% | Full-service Restaurant | 0 | 0 | 0.53034 | 0.47635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.816 | 0.9718% | Full-service Restaurant | 26.566 | 9.8534 | 97.8623 | 52.0651 | 0 | 90.3701 | 0 | 55.2542 | 0 | 0.23791 | 29.4388 | 0 | 0 | 308.9379 | 0 | 0 | 670.5855 | 0.9718%
Mid-rise Apartment | 0.073032 | 0.022706 | 0.33122 | 0.027212 | 0 | 0.1076 | 0 | 0.069285 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0784 | 13.69% | Mid-rise Apartment | 2.3442 | 0.7288 | 10.6314 | 2.7767 | 0 | 3.4537 | 0 | 2.2239 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 36.5187 | 13.69% | Mid-rise Apartment | 0.68704 | 0.2136 | 3.1159 | 0 | 0 | 1.0122 | 0 | 0.65179 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.8892 | 13.69% | Mid-rise Apartment | 0 | 0 | 0 | 0.027767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027767 | 13.69% | Mid-rise Apartment | 7.1926 | 2.2362 | 32.6201 | 3.0349 | 0 | 10.5969 | 0 | 6.8235 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 106.5651 | 13.69%
High-rise Apartment | 0.0721 | 0.041287 | 0.11595 | 0.066847 | 0 | 0.14132 | 0.0034834 | 0.079609 | 0 | 0.012059 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.93367 | 9.636% | High-rise Apartment | 2.3143 | 1.3252 | 11.8315 | 4.582 | 0 | 4.5362 | 0.11181 | 2.5553 | 0 | 0.38706 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 40.5149 | 9.636% | High-rise Apartment | 0.67827 | 0.3884 | 0 | 0.30116 | 0 | 1.3295 | 0.03277 | 0.74891 | 0 | 0.11344 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.3649 | 9.636% | High-rise Apartment | 0 | 0 | 0.11832 | 0.035545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15386 | 9.636% | High-rise Apartment | 7.1008 | 4.0661 | 12.9318 | 7.0379 | 0 | 13.9184 | 0.34306 | 7.8403 | 0 | 1.1876 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 93.9197 | 9.636%
Warehouse | 0.095425 | 0.032254 | 0.014068 | 0.067865 | 0 | 0.019223 | 0 | 0.027909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.33421 | 18.56% | Warehouse | 3.0629 | 1.0353 | 0.45156 | 6.925 | 0 | 0.617 | 0 | 0.89582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.4741 | 18.56% | Warehouse | 0.89769 | 0.30343 | 0.13234 | 0 | 0 | 0.18083 | 0 | 0.26255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5056 | 18.56% | Warehouse | 0 | 0 | 0 | 0.06925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06925 | 18.56% | Warehouse | 9.3979 | 3.1766 | 1.3855 | 7.569 | 0 | 1.8931 | 0 | 2.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 33.8 | 18.56%
US Weighted | 0.16002 | 0.031662 | 0.10117 | 0.071609 | 0.0095301 | 0.18015 | 0.0039433 | 0.11576 | 0.0067111 | 0.0051795 | 0.0098186 | 0.072276 | 0.0023264 | 0.085529 | 0.021334 | 0.28389 | 1.1609 | 100% | US Weighted | 5.1362 | 1.0163 | 5.9499 | 6.4423 | 0.30589 | 5.7826 | 0.12657 | 3.7156 | 0.21541 | 0.16625 | 0.31516 | 2.3199 | 0.074674 | 4.8739 | 0.68478 | 9.2143 | 46.3397 | 100% | US Weighted | 1.5053 | 0.29785 | 0.58829 | 0.1163 | 0.089652 | 1.6948 | 0.037096 | 1.089 | 0.063134 | 0.048725 | 0.092367 | 0.67993 | 0.021886 | 0.5183 | 0.2007 | 2.6569 | 9.7002 | 100% | US Weighted | 0 | 0 | 0.039426 | 0.060455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.13243 | 100% | US Weighted | 15.7595 | 3.1182 | 10.4682 | 7.8253 | 0.93857 | 17.7426 | 0.38835 | 11.4005 | 0.66095 | 0.51011 | 0.96699 | 7.1182 | 0.22912 | 8.8203 | 2.1011 | 27.9777 | 116.0256 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | US All Buildings | [23 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.17233 | 0.030618 | 0.096682 | 0.046613 | 0 | 0.12121 | 0 | 0.10019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.82687 | 3.798% | Small Office | 5.5314 | 0.98277 | 3.1033 | 2.0696 | 0 | 3.8905 | 0 | 3.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.1143 | 3.798% | Small Office | 1.6212 | 0.28803 | 0.90952 | 0.36138 | 0 | 1.1402 | 0 | 0.94252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.7015 | 3.798% | Small Office | 0 | 0 | 0 | 0.0083658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083658 | 3.798% | Small Office | 16.9719 | 3.0154 | 9.5218 | 4.6977 | 0 | 11.9371 | 0 | 9.8673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 81.5419 | 3.798%
Medium Office | 0.16727 | 0.025854 | 0.013956 | 0.06332 | 0 | 0.16034 | 0 | 0.042075 | 0.0013565 | 8.2614e-05 | 0 | 0.09109 | 0.0064807 | 0 | 0 | 0.32202 | 0.89385 | 5.009% | Medium Office | 5.3691 | 0.82984 | 1.424 | 3.1458 | 0 | 5.1466 | 0 | 1.3505 | 0.04354 | 0.0026517 | 0 | 2.9238 | 0.20802 | 0 | 0 | 10.3361 | 30.7801 | 5.009% | Medium Office | 1.5736 | 0.24321 | 0 | 0.44592 | 0 | 1.5084 | 0 | 0.39582 | 0.012761 | 0.00077718 | 0 | 0.85692 | 0.060966 | 0 | 0 | 3.0293 | 8.1277 | 5.009% | Medium Office | 0 | 0 | 0.01424 | 0.016243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030483 | 5.009% | Medium Office | 16.4741 | 2.5462 | 1.5565 | 6.4437 | 0 | 15.7914 | 0 | 4.1438 | 0.13359 | 0.0081363 | 0 | 8.9711 | 0.63826 | 0 | 0 | 31.7141 | 88.4208 | 5.009%
Large Office | 0.18798 | 0.020384 | 0.010276 | 0.014679 | 0.050754 | 0.18466 | 0.064517 | 0.12745 | 0.0022936 | 0.022668 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6709 | 3.855% | Large Office | 6.0336 | 0.65429 | 1.0485 | 1.4978 | 1.6291 | 5.9273 | 2.0708 | 4.0907 | 0.07362 | 0.72758 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 55.379 | 3.855% | Large Office | 1.7684 | 0.19176 | 0 | 0 | 0.47746 | 1.7372 | 0.60693 | 1.1989 | 0.021577 | 0.21324 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 15.4844 | 3.855% | Large Office | 0 | 0 | 0.010485 | 0.014978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025463 | 3.855% | Large Office | 18.5129 | 2.0076 | 1.146 | 1.6371 | 4.9986 | 18.1868 | 6.3539 | 12.5515 | 0.22589 | 2.2324 | 0 | 11.0904 | 0.32083 | 0 | 54.5001 | 31.125 | 164.889 | 3.855%
Standalone Retail | 0.35968 | 0.046105 | 0.034907 | 0.10848 | 0 | 0.2336 | 0 | 0.18061 | 0.00012978 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1959 | 10.94% | Standalone Retail | 11.5448 | 1.4799 | 3.562 | 11.0693 | 0 | 7.498 | 0 | 5.7973 | 0.0041657 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 48.4156 | 10.94% | Standalone Retail | 3.3836 | 0.43372 | 0 | 0 | 0 | 2.1975 | 0 | 1.6991 | 0.0012209 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.9016 | 10.94% | Standalone Retail | 0 | 0 | 0.03562 | 0.11069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14631 | 10.94% | Standalone Retail | 35.4229 | 4.5406 | 3.8932 | 12.0987 | 0 | 23.0059 | 0 | 17.7879 | 0.012781 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 119.6519 | 10.94%
Strip Mall | 0.59189 | 0.078047 | 0.081874 | 0.10995 | 0 | 0.23785 | 0 | 0.14217 | 3.1124e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.41 | 3.712% | Strip Mall | 18.9984 | 2.5051 | 2.628 | 11.2196 | 0 | 7.6345 | 0 | 4.5634 | 9.9902e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.9488 | 3.712% | Strip Mall | 5.5681 | 0.73422 | 0.77022 | 0 | 0 | 2.2375 | 0 | 1.3374 | 2.928e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.2301 | 3.712% | Strip Mall | 0 | 0 | 0 | 0.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1122 | 3.712% | Strip Mall | 58.2927 | 7.6865 | 8.0634 | 12.2631 | 0 | 23.4248 | 0 | 14.0017 | 0.00030653 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 140.3002 | 3.712%
Primary School | 0.14164 | 0.010236 | 0.024676 | 0.043249 | 0 | 0.22228 | 0 | 0.14016 | 0.026486 | 0.00081245 | 0.044061 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.1441 | 4.828% | Primary School | 4.5463 | 0.32856 | 1.7962 | 4.4132 | 0 | 7.1347 | 0 | 4.499 | 0.85014 | 0.026078 | 1.4143 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 43.9226 | 4.828% | Primary School | 1.3324 | 0.096296 | 0.097071 | 0 | 0 | 2.0911 | 0 | 1.3186 | 0.24916 | 0.007643 | 0.4145 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 9.7942 | 4.828% | Primary School | 0 | 0 | 0.01465 | 0.044132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10505 | 4.828% | Primary School | 13.9494 | 1.0081 | 2.6175 | 4.8236 | 0 | 21.8915 | 0 | 13.8041 | 2.6085 | 0.080014 | 4.3394 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 114.017 | 4.828%
Secondary School | 0.1336 | 0.0095301 | 0.042548 | 0.032553 | 0 | 0.2415 | 0 | 0.12447 | 0.027737 | 0.0040832 | 0.025229 | 0.0092157 | 0.0041591 | 0.07431 | 0 | 0.26878 | 0.99771 | 10.92% | Secondary School | 4.2881 | 0.3059 | 2.8291 | 3.3218 | 0 | 7.7516 | 0 | 3.9952 | 0.8903 | 0.13106 | 0.8098 | 0.29581 | 0.1335 | 4.0625 | 0 | 8.6272 | 37.4418 | 10.92% | Secondary School | 1.2568 | 0.089653 | 0.20343 | 0 | 0 | 2.2719 | 0 | 1.1709 | 0.26093 | 0.038412 | 0.23734 | 0.086696 | 0.039126 | 0.47347 | 0 | 2.5285 | 8.6571 | 10.92% | Secondary School | 0 | 0 | 0.02135 | 0.033218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.079038 | 10.92% | Secondary School | 13.1573 | 0.93858 | 4.4633 | 3.6307 | 0 | 23.7841 | 0 | 12.2584 | 2.7317 | 0.40214 | 2.4847 | 0.90762 | 0.40961 | 7.6313 | 0 | 26.4707 | 99.27 | 10.92%
Outpatient Healthcare | 0.33387 | 0.039444 | 0.049663 | 0.25333 | 0.094302 | 0.5277 | 0 | 0.25163 | 0 | 0.0025319 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9148 | 3.419% | Outpatient Healthcare | 10.7164 | 1.2661 | 5.0676 | 15.931 | 3.0269 | 16.9379 | 0 | 8.0769 | 0 | 0.081267 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.8218 | 3.419% | Outpatient Healthcare | 3.1408 | 0.37106 | 0 | 1.3342 | 0.88713 | 4.9642 | 0 | 2.3672 | 0 | 0.023818 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 25.5026 | 3.419% | Outpatient Healthcare | 0 | 0 | 0.050676 | 0.11379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20807 | 3.419% | Outpatient Healthcare | 32.8809 | 3.8846 | 5.5389 | 26.4044 | 9.2874 | 51.9704 | 0 | 24.7823 | 0 | 0.24935 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 289.7289 | 3.419%
Hospital | 0.41562 | 0.018951 | 0.049212 | 0.25392 | 0.095501 | 0.29975 | 0.034393 | 0.35574 | 0.022002 | 0.058956 | 0.026377 | 0.30666 | 0.008691 | 0.27812 | 0 | 0.66831 | 2.8922 | 4.523% | Hospital | 13.3404 | 0.60829 | 4.7958 | 24.91 | 3.0654 | 9.6213 | 1.104 | 11.4184 | 0.70621 | 1.8924 | 0.84664 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 120.3198 | 4.523% | Hospital | 3.9098 | 0.17828 | 0.030374 | 0.13458 | 0.89841 | 2.8199 | 0.32355 | 3.3465 | 0.20698 | 0.55462 | 0.24814 | 2.8848 | 0.08176 | 1.6061 | 0 | 6.287 | 23.5109 | 4.523% | Hospital | 0 | 0 | 0.046922 | 0.24451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40101 | 4.523% | Hospital | 40.9322 | 1.8664 | 5.4466 | 28.1337 | 9.4054 | 29.5211 | 3.3872 | 35.0349 | 2.1668 | 5.8063 | 2.5977 | 30.2012 | 0.85594 | 28.7914 | 0 | 65.8187 | 289.9656 | 4.523%
Small Hotel | 0.19632 | 0.030289 | 0.12351 | 0.061636 | 0 | 0.21858 | 0 | 0.11605 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2184 | 1.588% | Small Hotel | 6.3015 | 0.9722 | 12.6026 | 2.704 | 0 | 7.0159 | 0 | 3.7248 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 54.8118 | 1.588% | Small Hotel | 1.8469 | 0.28493 | 0 | 0.48223 | 0 | 2.0563 | 0 | 1.0917 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.3503 | 1.588% | Small Hotel | 0 | 0 | 0.12603 | 0.010586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22908 | 1.588% | Small Hotel | 19.3348 | 2.983 | 13.7747 | 6.2055 | 0 | 21.5269 | 0 | 11.4289 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 122.9276 | 1.588%
Large Hotel | 0.20008 | 0.044207 | 0.17866 | 0.05726 | 0 | 0.38126 | 0 | 0.12269 | 0.048333 | 0.014006 | 0.020573 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.8337 | 4.219% | Large Hotel | 6.4223 | 1.4189 | 16.6949 | 5.8429 | 0 | 12.2375 | 0 | 3.9379 | 1.5514 | 0.44956 | 0.66034 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 83.3386 | 4.219% | Large Hotel | 1.8823 | 0.41587 | 0.20649 | 0 | 0 | 3.5866 | 0 | 1.1541 | 0.45468 | 0.13176 | 0.19353 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 13.9571 | 4.219% | Large Hotel | 0 | 0 | 0.1599 | 0.058429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35717 | 4.219% | Large Hotel | 19.7054 | 4.3537 | 19.6392 | 6.3863 | 0 | 37.5483 | 0 | 12.0827 | 4.7601 | 1.3794 | 2.0261 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 185.1553 | 4.219%
Quick-service Restaurant | 0.32126 | 0.10383 | 0.65797 | 0.66889 | 0 | 1.1161 | 0 | 0.67554 | 0 | 0 | 1.013 | 0 | 0 | 4.5293 | 0 | 0 | 9.0859 | 0.3319% | Quick-service Restaurant | 10.3118 | 3.3328 | 67.1396 | 68.2538 | 0 | 35.825 | 0 | 21.6833 | 0 | 0 | 32.5152 | 0 | 0 | 269.3289 | 0 | 0 | 508.3904 | 0.3319% | Quick-service Restaurant | 3.0222 | 0.97679 | 0 | 0 | 0 | 10.4997 | 0 | 6.355 | 0 | 0 | 9.5297 | 0 | 0 | 25.937 | 0 | 0 | 56.3204 | 0.3319% | Quick-service Restaurant | 0 | 0 | 0.6714 | 0.68254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1623 | 0.3319% | Quick-service Restaurant | 31.6396 | 10.2261 | 73.3835 | 74.6014 | 0 | 109.9216 | 0 | 66.5306 | 0 | 0 | 99.766 | 0 | 0 | 469.1836 | 0 | 0 | 935.2523 | 0.3319%
Full-service Restaurant | 0.2939 | 0.10005 | 0.92474 | 0.46438 | 0 | 0.95587 | 0 | 0.57144 | 0 | 0.0024157 | 0.45301 | 0 | 0 | 3.0318 | 0 | 0 | 6.7976 | 0.9718% | Full-service Restaurant | 9.4336 | 3.2114 | 66.0296 | 47.386 | 0 | 30.6812 | 0 | 18.3419 | 0 | 0.077539 | 14.5405 | 0 | 0 | 152.7879 | 0 | 0 | 342.4895 | 0.9718% | Full-service Restaurant | 2.7648 | 0.94119 | 3.8106 | 0 | 0 | 8.9921 | 0 | 5.3757 | 0 | 0.022725 | 4.2616 | 0 | 0 | 21.0604 | 0 | 0 | 47.2292 | 0.9718% | Full-service Restaurant | 0 | 0 | 0.53028 | 0.47386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8134 | 0.9718% | Full-service Restaurant | 28.945 | 9.8534 | 97.8523 | 51.7928 | 0 | 94.1388 | 0 | 56.2782 | 0 | 0.23791 | 44.6144 | 0 | 0 | 308.9379 | 0 | 0 | 692.6507 | 0.9718%
Mid-rise Apartment | 0.089384 | 0.022706 | 0.33135 | 0.032266 | 0 | 0.11434 | 0 | 0.071086 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1085 | 13.69% | Mid-rise Apartment | 2.869 | 0.7288 | 10.6356 | 3.2925 | 0 | 3.6702 | 0 | 2.2817 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 37.8379 | 13.69% | Mid-rise Apartment | 0.84087 | 0.2136 | 3.1171 | 0 | 0 | 1.0757 | 0 | 0.66873 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.1247 | 13.69% | Mid-rise Apartment | 0 | 0 | 0 | 0.032925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032925 | 13.69% | Mid-rise Apartment | 8.803 | 2.2362 | 32.6331 | 3.5987 | 0 | 11.2612 | 0 | 7.001 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 109.5939 | 13.69%
High-rise Apartment | 0.088732 | 0.041287 | 0.11595 | 0.069226 | 0 | 0.14387 | 0.0036305 | 0.078486 | 0 | 0.012409 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.95459 | 9.636% | High-rise Apartment | 2.8481 | 1.3252 | 11.8316 | 4.7473 | 0 | 4.6178 | 0.11653 | 2.5192 | 0 | 0.39829 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.2756 | 9.636% | High-rise Apartment | 0.83474 | 0.3884 | 0 | 0.31157 | 0 | 1.3534 | 0.034154 | 0.73834 | 0 | 0.11673 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.5498 | 9.636% | High-rise Apartment | 0 | 0 | 0.11832 | 0.036843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15516 | 9.636% | High-rise Apartment | 8.7389 | 4.0661 | 12.9319 | 7.2888 | 0 | 14.1686 | 0.35755 | 7.7297 | 0 | 1.2221 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 95.9972 | 9.636%
Warehouse | 0.10314 | 0.032254 | 0.014068 | 0.067574 | 0 | 0.020065 | 0 | 0.027801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.34237 | 18.56% | Warehouse | 3.3105 | 1.0353 | 0.45156 | 6.8953 | 0 | 0.64404 | 0 | 0.89236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.7155 | 18.56% | Warehouse | 0.97026 | 0.30343 | 0.13234 | 0 | 0 | 0.18876 | 0 | 0.26154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5851 | 18.56% | Warehouse | 0 | 0 | 0 | 0.068953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068953 | 18.56% | Warehouse | 10.1576 | 3.1766 | 1.3855 | 7.5365 | 0 | 1.9761 | 0 | 2.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 34.5996 | 18.56%
US Weighted | 0.19055 | 0.031662 | 0.1012 | 0.081003 | 0.0094998 | 0.18863 | 0.0043926 | 0.11819 | 0.0075122 | 0.0059289 | 0.014708 | 0.072276 | 0.0023428 | 0.085529 | 0.021334 | 0.28389 | 1.2186 | 100% | US Weighted | 6.1161 | 1.0163 | 5.9517 | 7.3329 | 0.30492 | 6.0548 | 0.14099 | 3.7935 | 0.24113 | 0.1903 | 0.47208 | 2.3199 | 0.0752 | 4.8739 | 0.68478 | 9.2143 | 48.7828 | 100% | US Weighted | 1.7925 | 0.29785 | 0.58847 | 0.12544 | 0.089368 | 1.7745 | 0.041323 | 1.1118 | 0.07067 | 0.055775 | 0.13836 | 0.67993 | 0.02204 | 0.5183 | 0.2007 | 2.6569 | 10.164 | 100% | US Weighted | 0 | 0 | 0.039438 | 0.069049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.14103 | 100% | US Weighted | 18.766 | 3.1182 | 10.4713 | 8.8603 | 0.93559 | 18.5778 | 0.43261 | 11.6396 | 0.73984 | 0.58391 | 1.4485 | 7.1182 | 0.23074 | 8.8203 | 2.1011 | 27.9777 | 121.8216 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | US All Buildings | [23 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.23769 | 0.063937 | 0.096682 | 0.043604 | 0 | 0.12919 | 0 | 0.10239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.93272 | 3.798% | Small Office | 7.6292 | 2.0522 | 3.1033 | 1.9407 | 0 | 4.1467 | 0 | 3.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.4793 | 3.798% | Small Office | 2.236 | 0.60148 | 0.90952 | 0.33742 | 0 | 1.2153 | 0 | 0.96319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.7016 | 3.798% | Small Office | 0 | 0 | 0 | 0.0078944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078944 | 3.798% | Small Office | 23.4085 | 6.2969 | 9.5218 | 4.3953 | 0 | 12.7232 | 0 | 10.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 91.9601 | 3.798%
Medium Office | 0.18078 | 0.056746 | 0.014262 | 0.066723 | 0 | 0.16376 | 0 | 0.043044 | 0.001276 | 8.2614e-05 | 0 | 0.09109 | 0.0093959 | 0 | 0 | 0.32202 | 0.94918 | 5.009% | Medium Office | 5.8026 | 1.8214 | 1.4553 | 3.2507 | 0 | 5.2565 | 0 | 1.3816 | 0.040957 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 32.5732 | 5.009% | Medium Office | 1.7006 | 0.53383 | 0 | 0.47852 | 0 | 1.5406 | 0 | 0.40493 | 0.012004 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.6459 | 5.009% | Medium Office | 0 | 0 | 0.014553 | 0.01618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030733 | 5.009% | Medium Office | 17.8041 | 5.5887 | 1.5907 | 6.7781 | 0 | 16.1283 | 0 | 4.2392 | 0.12567 | 0.0081363 | 0 | 8.9711 | 0.92536 | 0 | 0 | 31.7141 | 93.8734 | 5.009%
Large Office | 0.20214 | 0.040368 | 0.010554 | 0.017787 | 0.030376 | 0.21094 | 0.071731 | 0.12856 | 0.0026257 | 0.024938 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.7268 | 3.855% | Large Office | 6.4882 | 1.2957 | 1.0769 | 1.815 | 0.97499 | 6.7709 | 2.3024 | 4.1263 | 0.084279 | 0.80045 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 57.4079 | 3.855% | Large Office | 1.9016 | 0.37975 | 0 | 0 | 0.28575 | 1.9844 | 0.67479 | 1.2094 | 0.024701 | 0.2346 | 0 | 1.0594 | 0.0445 | 0 | 5.2059 | 2.9731 | 15.9777 | 3.855% | Large Office | 0 | 0 | 0.010769 | 0.01815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028919 | 3.855% | Large Office | 19.9075 | 3.9756 | 1.177 | 1.9838 | 2.9916 | 20.7749 | 7.0644 | 12.6608 | 0.25859 | 2.456 | 0 | 11.0904 | 0.46587 | 0 | 54.5001 | 31.125 | 170.4316 | 3.855%
Standalone Retail | 0.44263 | 0.072171 | 0.034902 | 0.054628 | 0 | 0.23783 | 0 | 0.18045 | 0.018255 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2733 | 10.94% | Standalone Retail | 14.2076 | 2.3165 | 3.5615 | 5.5743 | 0 | 7.6339 | 0 | 5.792 | 0.58596 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.1319 | 10.94% | Standalone Retail | 4.164 | 0.67894 | 0 | 0 | 0 | 2.2374 | 0 | 1.6975 | 0.17174 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 11.136 | 10.94% | Standalone Retail | 0 | 0 | 0.035615 | 0.055743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091358 | 10.94% | Standalone Retail | 43.5929 | 7.1078 | 3.8927 | 6.0927 | 0 | 23.4231 | 0 | 17.7714 | 1.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 126.5684 | 10.94%
Strip Mall | 0.72311 | 0.12064 | 0.08182 | 0.099421 | 0 | 0.2584 | 0 | 0.14059 | 2.9948e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5922 | 3.712% | Strip Mall | 23.2103 | 3.8724 | 2.6262 | 10.145 | 0 | 8.294 | 0 | 4.5128 | 9.6128e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.0605 | 3.712% | Strip Mall | 6.8025 | 1.1349 | 0.7697 | 0 | 0 | 2.4308 | 0 | 1.3226 | 2.8174e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.0432 | 3.712% | Strip Mall | 0 | 0 | 0 | 0.10145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10145 | 3.712% | Strip Mall | 71.2159 | 11.8817 | 8.058 | 11.0885 | 0 | 25.4485 | 0 | 13.8465 | 0.00029495 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 158.1071 | 3.712%
Primary School | 0.27555 | 0.01772 | 0.024715 | 0.035459 | 0 | 0.24093 | 0 | 0.14919 | 0.024277 | 0.00064175 | 0.044047 | 0 | 0.0096614 | 0.10513 | 0 | 0.37841 | 1.3057 | 4.828% | Primary School | 8.8446 | 0.56877 | 1.8002 | 3.6183 | 0 | 7.7333 | 0 | 4.7886 | 0.77925 | 0.020599 | 1.4138 | 0 | 0.31011 | 6.5458 | 0 | 12.1461 | 48.5694 | 4.828% | Primary School | 2.5922 | 0.1667 | 0.097071 | 0 | 0 | 2.2665 | 0 | 1.4035 | 0.22838 | 0.0060372 | 0.41437 | 0 | 0.090888 | 0.56245 | 0 | 3.5598 | 11.3879 | 4.828% | Primary School | 0 | 0 | 0.01469 | 0.036183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.09714 | 4.828% | Primary School | 27.1379 | 1.7451 | 2.6218 | 3.9548 | 0 | 23.7279 | 0 | 14.6928 | 2.3909 | 0.063203 | 4.338 | 0 | 0.9515 | 10.9453 | 0 | 37.2677 | 129.837 | 4.828%
Secondary School | 0.25157 | 0.016495 | 0.042548 | 0.025893 | 0 | 0.25848 | 0 | 0.12981 | 0.028214 | 0.0053003 | 0.025224 | 0.0092157 | 0.0057249 | 0.07431 | 0 | 0.26878 | 1.1416 | 10.92% | Secondary School | 8.0747 | 0.52947 | 2.8291 | 2.6421 | 0 | 8.2965 | 0 | 4.1667 | 0.9056 | 0.17013 | 0.80965 | 0.29581 | 0.18376 | 4.0625 | 0 | 8.6272 | 41.5932 | 10.92% | Secondary School | 2.3666 | 0.15518 | 0.20343 | 0 | 0 | 2.4316 | 0 | 1.2212 | 0.26542 | 0.049862 | 0.23729 | 0.086696 | 0.053856 | 0.47347 | 0 | 2.5285 | 10.073 | 10.92% | Secondary School | 0 | 0 | 0.02135 | 0.026421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.072242 | 10.92% | Secondary School | 24.7756 | 1.6246 | 4.4633 | 2.8878 | 0 | 25.456 | 0 | 12.7845 | 2.7786 | 0.522 | 2.4842 | 0.90762 | 0.56381 | 7.6313 | 0 | 26.4707 | 113.3502 | 10.92%
Outpatient Healthcare | 0.3627 | 0.080985 | 0.055544 | 0.28838 | 0.093399 | 0.54363 | 0 | 0.27289 | 0.012435 | 0.0028758 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.0752 | 3.419% | Outpatient Healthcare | 11.642 | 2.5994 | 5.6678 | 17.5885 | 2.9979 | 17.4494 | 0 | 8.7593 | 0.39914 | 0.092308 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 113.9136 | 3.419% | Outpatient Healthcare | 3.4121 | 0.76185 | 0 | 1.5922 | 0.87864 | 5.1141 | 0 | 2.5672 | 0.11698 | 0.027054 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.8844 | 3.419% | Outpatient Healthcare | 0 | 0 | 0.056678 | 0.12156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22184 | 3.419% | Outpatient Healthcare | 35.721 | 7.9759 | 6.1949 | 29.9549 | 9.1985 | 53.5397 | 0 | 26.8761 | 1.2247 | 0.28323 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 305.6996 | 3.419%
Hospital | 0.42419 | 0.025952 | 0.050961 | 0.25448 | 0.096107 | 0.30176 | 0.034464 | 0.35742 | 0.027714 | 0.066849 | 0.026374 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.932 | 4.523% | Hospital | 13.6155 | 0.83301 | 4.9742 | 24.9616 | 3.0848 | 9.686 | 1.1062 | 11.4725 | 0.88956 | 2.1457 | 0.84654 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 121.7524 | 4.523% | Hospital | 3.9905 | 0.24414 | 0.030374 | 0.1353 | 0.90411 | 2.8388 | 0.32422 | 3.3624 | 0.26072 | 0.62887 | 0.24811 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.8641 | 4.523% | Hospital | 0 | 0 | 0.048706 | 0.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40328 | 4.523% | Hospital | 41.7761 | 2.5559 | 5.6416 | 28.1949 | 9.4652 | 29.7193 | 3.3942 | 35.2008 | 2.7294 | 6.5836 | 2.5974 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 293.9117 | 4.523%
Small Hotel | 0.21944 | 0.044985 | 0.12527 | 0.097726 | 0 | 0.23853 | 0 | 0.18084 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3788 | 1.588% | Small Hotel | 7.0435 | 1.4439 | 12.7823 | 3.8845 | 0 | 7.6562 | 0 | 5.8045 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 60.1055 | 1.588% | Small Hotel | 2.0643 | 0.42319 | 0 | 0.81877 | 0 | 2.2439 | 0 | 1.7012 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.8397 | 1.588% | Small Hotel | 0 | 0 | 0.12782 | 0.010908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2312 | 1.588% | Small Hotel | 21.6114 | 4.4304 | 13.9711 | 9.764 | 0 | 23.4913 | 0 | 17.8099 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 138.7518 | 1.588%
Large Hotel | 0.22056 | 0.059534 | 0.17874 | 0.057686 | 0 | 0.39392 | 0 | 0.13464 | 0.054454 | 0.017764 | 0.020569 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.9067 | 4.219% | Large Hotel | 7.0794 | 1.9109 | 16.7035 | 5.8863 | 0 | 12.644 | 0 | 4.3216 | 1.7479 | 0.57018 | 0.66022 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 85.7192 | 4.219% | Large Hotel | 2.0749 | 0.56005 | 0.20649 | 0 | 0 | 3.7057 | 0 | 1.2666 | 0.51227 | 0.16711 | 0.1935 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 14.6395 | 4.219% | Large Hotel | 0 | 0 | 0.15999 | 0.058863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35769 | 4.219% | Large Hotel | 21.7218 | 5.8632 | 19.6486 | 6.4337 | 0 | 38.7953 | 0 | 13.2598 | 5.3629 | 1.7495 | 2.0257 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 192.3568 | 4.219%
Quick-service Restaurant | 0.37798 | 0.18137 | 0.65797 | 0.67401 | 0 | 1.1271 | 0 | 0.68035 | 0 | 0 | 1.013 | 0 | 0 | 4.5293 | 0 | 0 | 9.241 | 0.3319% | Quick-service Restaurant | 12.1325 | 5.8216 | 67.1395 | 68.7766 | 0 | 36.1769 | 0 | 21.8378 | 0 | 0 | 32.5159 | 0 | 0 | 269.3289 | 0 | 0 | 513.7297 | 0.3319% | Quick-service Restaurant | 3.5558 | 1.7062 | 0 | 0 | 0 | 10.6028 | 0 | 6.4003 | 0 | 0 | 9.5299 | 0 | 0 | 25.937 | 0 | 0 | 57.732 | 0.3319% | Quick-service Restaurant | 0 | 0 | 0.6714 | 0.68777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1675 | 0.3319% | Quick-service Restaurant | 37.2259 | 17.8624 | 73.3835 | 75.1728 | 0 | 111.0012 | 0 | 67.0048 | 0 | 0 | 99.7682 | 0 | 0 | 469.1836 | 0 | 0 | 950.6023 | 0.3319%
Full-service Restaurant | 0.37519 | 0.17725 | 0.92504 | 0.4593 | 0 | 0.97433 | 0 | 0.5769 | 0 | 0.0024157 | 0.45301 | 0 | 0 | 3.0318 | 0 | 0 | 6.9753 | 0.9718% | Full-service Restaurant | 12.0429 | 5.6892 | 66.0606 | 46.8673 | 0 | 31.2739 | 0 | 18.5171 | 0 | 0.077539 | 14.5405 | 0 | 0 | 152.7879 | 0 | 0 | 347.857 | 0.9718% | Full-service Restaurant | 3.5296 | 1.6674 | 3.8106 | 0 | 0 | 9.1659 | 0 | 5.4271 | 0 | 0.022725 | 4.2616 | 0 | 0 | 21.0604 | 0 | 0 | 48.9452 | 0.9718% | Full-service Restaurant | 0 | 0 | 0.53059 | 0.46867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8086 | 0.9718% | Full-service Restaurant | 36.9512 | 17.4561 | 97.8861 | 51.2259 | 0 | 95.9575 | 0 | 56.8159 | 0 | 0.23791 | 44.6145 | 0 | 0 | 308.9379 | 0 | 0 | 710.083 | 0.9718%
Mid-rise Apartment | 0.1139 | 0.034495 | 0.33132 | 0.031332 | 0 | 0.11881 | 0 | 0.073144 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1504 | 13.69% | Mid-rise Apartment | 3.656 | 1.1072 | 10.6345 | 3.1972 | 0 | 3.8136 | 0 | 2.3478 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 39.1163 | 13.69% | Mid-rise Apartment | 1.0715 | 0.32451 | 3.1168 | 0 | 0 | 1.1177 | 0 | 0.68809 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.5273 | 13.69% | Mid-rise Apartment | 0 | 0 | 0 | 0.031972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031972 | 13.69% | Mid-rise Apartment | 11.2178 | 3.3973 | 32.6297 | 3.4945 | 0 | 11.7012 | 0 | 7.2036 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 113.7049 | 13.69%
High-rise Apartment | 0.11277 | 0.058979 | 0.1163 | 0.068507 | 0 | 0.15007 | 0.0072494 | 0.080327 | 0 | 0.01305 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.0105 | 9.636% | High-rise Apartment | 3.6196 | 1.8931 | 11.8678 | 4.694 | 0 | 4.8171 | 0.23269 | 2.5783 | 0 | 0.41888 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 43.0641 | 9.636% | High-rise Apartment | 1.0608 | 0.55484 | 0 | 0.30888 | 0 | 1.4118 | 0.068197 | 0.75566 | 0 | 0.12277 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 8.0763 | 9.636% | High-rise Apartment | 0 | 0 | 0.11868 | 0.036401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15508 | 9.636% | High-rise Apartment | 11.1059 | 5.8086 | 12.9715 | 7.2123 | 0 | 14.7801 | 0.71396 | 7.911 | 0 | 1.2852 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 101.5005 | 9.636%
Warehouse | 0.17399 | 0.047513 | 0.014064 | 0.066139 | 0 | 0.023259 | 0 | 0.030214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.43265 | 18.56% | Warehouse | 5.5848 | 1.5251 | 0.45141 | 6.7489 | 0 | 0.74656 | 0 | 0.96981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 18.513 | 18.56% | Warehouse | 1.6368 | 0.44697 | 0.1323 | 0 | 0 | 0.2188 | 0 | 0.28423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.4479 | 18.56% | Warehouse | 0 | 0 | 0 | 0.067489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067489 | 18.56% | Warehouse | 17.1359 | 4.6793 | 1.3851 | 7.3766 | 0 | 2.2907 | 0 | 2.9756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 43.4723 | 18.56%
US Weighted | 0.24995 | 0.050575 | 0.10157 | 0.07511 | 0.0087107 | 0.19761 | 0.0050226 | 0.12262 | 0.010392 | 0.0067302 | 0.014706 | 0.072276 | 0.0033346 | 0.085529 | 0.021334 | 0.28389 | 1.3094 | 100% | US Weighted | 8.0228 | 1.6233 | 5.9898 | 6.6227 | 0.2796 | 6.3428 | 0.16122 | 3.9357 | 0.33355 | 0.21602 | 0.47204 | 2.3199 | 0.10703 | 4.8739 | 0.68478 | 9.2143 | 51.1995 | 100% | US Weighted | 2.3514 | 0.47578 | 0.5884 | 0.1401 | 0.081945 | 1.859 | 0.04725 | 1.1535 | 0.097757 | 0.063313 | 0.13835 | 0.67993 | 0.03137 | 0.5183 | 0.2007 | 2.6569 | 11.0839 | 100% | US Weighted | 0 | 0 | 0.039822 | 0.061446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.13381 | 100% | US Weighted | 24.6164 | 4.9809 | 10.5125 | 8.1828 | 0.85788 | 19.4615 | 0.49466 | 12.0758 | 1.0234 | 0.66282 | 1.4483 | 7.1182 | 0.32841 | 8.8203 | 2.1011 | 27.9777 | 130.6628 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | US All Buildings | [23 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.27955 | 0.063937 | 0.096682 | 0.053116 | 0 | 0.16095 | 0 | 0.12166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.04 | 3.798% | Small Office | 8.9731 | 2.0522 | 3.1033 | 2.3554 | 0 | 5.1663 | 0 | 3.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 34.0311 | 3.798% | Small Office | 2.6299 | 0.60148 | 0.90952 | 0.41219 | 0 | 1.5141 | 0 | 1.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.6958 | 3.798% | Small Office | 0 | 0 | 0 | 0.0094898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0094898 | 3.798% | Small Office | 27.532 | 6.2969 | 9.5218 | 5.3525 | 0 | 15.8516 | 0 | 11.9816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 102.5428 | 3.798%
Medium Office | 0.20518 | 0.056746 | 0.014267 | 0.087912 | 0 | 0.18463 | 0 | 0.044822 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.009576 | 0 | 0 | 0.32596 | 1.0205 | 5.009% | Medium Office | 6.5859 | 1.8214 | 1.4558 | 4.0011 | 0 | 5.9262 | 0 | 1.4387 | 0 | 0.0026517 | 0 | 2.9318 | 0.30737 | 0 | 0 | 10.4627 | 34.9336 | 5.009% | Medium Office | 1.9302 | 0.53383 | 0 | 0.6684 | 0 | 1.7369 | 0 | 0.42165 | 0 | 0.00077718 | 0 | 0.85925 | 0.090085 | 0 | 0 | 3.0664 | 9.3075 | 5.009% | Medium Office | 0 | 0 | 0.014558 | 0.017205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031763 | 5.009% | Medium Office | 20.2073 | 5.5887 | 1.5912 | 8.878 | 0 | 18.1834 | 0 | 4.4143 | 0 | 0.0081363 | 0 | 8.9955 | 0.94309 | 0 | 0 | 32.1025 | 100.912 | 5.009%
Large Office | 0.22363 | 0.040368 | 0.010554 | 0.032647 | 0.031008 | 0.21323 | 0.073473 | 0.1343 | 0 | 0.03299 | 0 | 0.11285 | 0.0047592 | 0 | 0.55338 | 0.31716 | 1.7803 | 3.855% | Large Office | 7.1781 | 1.2957 | 1.0769 | 3.3313 | 0.9953 | 6.8441 | 2.3583 | 4.3106 | 0 | 1.0589 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 60.1668 | 3.855% | Large Office | 2.1038 | 0.37975 | 0 | 0 | 0.2917 | 2.0059 | 0.69119 | 1.2634 | 0 | 0.31035 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 16.3419 | 3.855% | Large Office | 0 | 0 | 0.010769 | 0.033313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044083 | 3.855% | Large Office | 22.0245 | 3.9756 | 1.1771 | 3.6411 | 3.0539 | 20.9996 | 7.236 | 13.2262 | 0 | 3.2491 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 175.9016 | 3.855%
Standalone Retail | 0.50606 | 0.072171 | 0.03491 | 0.12007 | 0 | 0.26481 | 0 | 0.24163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.4725 | 10.94% | Standalone Retail | 16.2434 | 2.3165 | 3.5622 | 12.2517 | 0 | 8.4999 | 0 | 7.7559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 58.1025 | 10.94% | Standalone Retail | 4.7607 | 0.67894 | 0 | 0 | 0 | 2.4912 | 0 | 2.2731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 12.3941 | 10.94% | Standalone Retail | 0 | 0 | 0.035622 | 0.12252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15814 | 10.94% | Standalone Retail | 49.8394 | 7.1078 | 3.8935 | 13.3911 | 0 | 26.0803 | 0 | 23.7972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 147.0381 | 10.94%
Strip Mall | 0.80123 | 0.12064 | 0.081921 | 0.098982 | 0 | 0.28657 | 0 | 0.26815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.8257 | 3.712% | Strip Mall | 25.7178 | 3.8724 | 2.6295 | 10.1002 | 0 | 9.1982 | 0 | 8.6071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 65.5249 | 3.712% | Strip Mall | 7.5374 | 1.1349 | 0.77066 | 0 | 0 | 2.6958 | 0 | 2.5226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 16.244 | 3.712% | Strip Mall | 0 | 0 | 0 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.101 | 3.712% | Strip Mall | 78.9096 | 11.8817 | 8.068 | 11.0396 | 0 | 28.2227 | 0 | 26.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 181.0984 | 3.712%
Primary School | 0.3124 | 0.01772 | 0.02471 | 0.053437 | 0 | 0.29549 | 0 | 0.19713 | 0.032522 | 0.00092123 | 0.054609 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.5381 | 4.828% | Primary School | 10.0273 | 0.56877 | 1.7997 | 5.4528 | 0 | 9.4846 | 0 | 6.3273 | 1.0439 | 0.029569 | 1.7528 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 57.2856 | 4.828% | Primary School | 2.9388 | 0.1667 | 0.097071 | 0 | 0 | 2.7798 | 0 | 1.8544 | 0.30595 | 0.0086663 | 0.51372 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 13.4049 | 4.828% | Primary School | 0 | 0 | 0.014685 | 0.054528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11548 | 4.828% | Primary School | 30.7666 | 1.7451 | 2.6213 | 5.9599 | 0 | 29.1014 | 0 | 19.414 | 3.203 | 0.090728 | 5.3782 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 152.958 | 4.828%
Secondary School | 0.28949 | 0.016495 | 0.042602 | 0.034586 | 0 | 0.33387 | 0 | 0.16342 | 0.03461 | 0.007758 | 0.029703 | 0.0092395 | 0.0062098 | 0.07431 | 0 | 0.29592 | 1.3382 | 10.92% | Secondary School | 9.2919 | 0.52947 | 2.8334 | 3.5292 | 0 | 10.7163 | 0 | 5.2453 | 1.1109 | 0.24901 | 0.95339 | 0.29657 | 0.19932 | 4.0625 | 0 | 9.4984 | 48.5158 | 10.92% | Secondary School | 2.7233 | 0.15518 | 0.2036 | 0 | 0 | 3.1408 | 0 | 1.5373 | 0.32558 | 0.072982 | 0.27942 | 0.08692 | 0.058418 | 0.47347 | 0 | 2.7838 | 11.8408 | 10.92% | Secondary School | 0 | 0 | 0.021387 | 0.035292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.081149 | 10.92% | Secondary School | 28.5104 | 1.6246 | 4.4691 | 3.8574 | 0 | 32.8809 | 0 | 16.0942 | 3.4085 | 0.76405 | 2.9253 | 0.90996 | 0.61158 | 7.6313 | 0 | 29.1439 | 132.8311 | 10.92%
Outpatient Healthcare | 0.39034 | 0.080985 | 0.055545 | 0.35466 | 0.12578 | 0.56159 | 0 | 0.29077 | 0.012491 | 0.0027878 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.2404 | 3.419% | Outpatient Healthcare | 12.5289 | 2.5994 | 5.6678 | 19.6761 | 4.0373 | 18.0257 | 0 | 9.3332 | 0.40094 | 0.089482 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 119.1772 | 3.419% | Outpatient Healthcare | 3.672 | 0.76185 | 0 | 2.2211 | 1.1833 | 5.283 | 0 | 2.7354 | 0.11751 | 0.026226 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 28.4441 | 3.419% | Outpatient Healthcare | 0 | 0 | 0.056678 | 0.12098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22126 | 3.419% | Outpatient Healthcare | 38.4423 | 7.9759 | 6.1949 | 36.4754 | 12.3875 | 55.3081 | 0 | 28.637 | 1.2302 | 0.27456 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 321.9648 | 3.419%
Hospital | 0.43859 | 0.025952 | 0.050961 | 0.32757 | 0.16688 | 0.31666 | 0.037045 | 0.36452 | 0.022874 | 0.07887 | 0.03342 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.132 | 4.523% | Hospital | 14.0778 | 0.83301 | 4.9743 | 28.322 | 5.3565 | 10.164 | 1.1891 | 11.7002 | 0.7342 | 2.5316 | 1.0727 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 129.1862 | 4.523% | Hospital | 4.126 | 0.24414 | 0.030374 | 0.68644 | 1.5699 | 2.9789 | 0.34849 | 3.4291 | 0.21518 | 0.74196 | 0.3144 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 25.609 | 4.523% | Hospital | 0 | 0 | 0.048707 | 0.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41808 | 4.523% | Hospital | 43.1947 | 2.5559 | 5.6416 | 35.5823 | 16.4353 | 31.1861 | 3.6484 | 35.8997 | 2.2527 | 7.7676 | 3.2914 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 313.7972 | 4.523%
Small Hotel | 0.28297 | 0.044985 | 0.1253 | 0.099568 | 0 | 0.26635 | 0 | 0.20837 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.5224 | 1.588% | Small Hotel | 9.0828 | 1.4439 | 12.7856 | 3.8403 | 0 | 8.5493 | 0 | 6.6881 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 64.6126 | 1.588% | Small Hotel | 2.662 | 0.42319 | 0 | 0.85001 | 0 | 2.5057 | 0 | 1.9602 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 12.2039 | 1.588% | Small Hotel | 0 | 0 | 0.12786 | 0.0094004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22973 | 1.588% | Small Hotel | 27.8686 | 4.4304 | 13.9747 | 9.9262 | 0 | 26.2318 | 0 | 20.5211 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 152.872 | 1.588%
Large Hotel | 0.3065 | 0.059534 | 0.17873 | 0.092812 | 0 | 0.45697 | 0 | 0.16215 | 0.044232 | 0.019733 | 0.025465 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.1355 | 4.219% | Large Hotel | 9.838 | 1.9109 | 16.703 | 9.4706 | 0 | 14.6676 | 0 | 5.2048 | 1.4198 | 0.63338 | 0.81736 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 95.5177 | 4.219% | Large Hotel | 2.8834 | 0.56005 | 0.20649 | 0 | 0 | 4.2988 | 0 | 1.5254 | 0.41611 | 0.18563 | 0.23956 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 16.461 | 4.219% | Large Hotel | 0 | 0 | 0.15998 | 0.094706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39353 | 4.219% | Large Hotel | 30.1859 | 5.8632 | 19.648 | 10.3513 | 0 | 45.0045 | 0 | 15.9697 | 4.3562 | 1.9434 | 2.5079 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 215.3424 | 4.219%
Quick-service Restaurant | 0.40349 | 0.18137 | 0.65835 | 0.78952 | 0 | 1.1505 | 0 | 1.1054 | 0 | 0 | 1.2784 | 0 | 0 | 4.5293 | 0 | 0 | 10.0962 | 0.3319% | Quick-service Restaurant | 12.951 | 5.8216 | 67.1786 | 80.5632 | 0 | 36.9277 | 0 | 35.4812 | 0 | 0 | 41.0331 | 0 | 0 | 269.3289 | 0 | 0 | 549.2854 | 0.3319% | Quick-service Restaurant | 3.7957 | 1.7062 | 0 | 0 | 0 | 10.8229 | 0 | 10.399 | 0 | 0 | 12.0261 | 0 | 0 | 25.937 | 0 | 0 | 64.6869 | 0.3319% | Quick-service Restaurant | 0 | 0 | 0.67179 | 0.80563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2857 | 0.3319% | Quick-service Restaurant | 39.7375 | 17.8624 | 73.4262 | 88.0556 | 0 | 113.3048 | 0 | 108.8666 | 0 | 0 | 125.9015 | 0 | 0 | 469.1836 | 0 | 0 | 1036.3382 | 0.3319%
Full-service Restaurant | 0.40254 | 0.17725 | 0.92521 | 0.46384 | 0 | 1.0153 | 0 | 0.77941 | 0 | 0.0024157 | 0.57459 | 0 | 0 | 3.0327 | 0 | 0 | 7.3732 | 0.9718% | Full-service Restaurant | 12.9206 | 5.6892 | 66.0753 | 47.3311 | 0 | 32.5887 | 0 | 25.0172 | 0 | 0.077539 | 18.4432 | 0 | 0 | 152.8155 | 0 | 0 | 360.9584 | 0.9718% | Full-service Restaurant | 3.7868 | 1.6674 | 3.8109 | 0 | 0 | 9.5512 | 0 | 7.3321 | 0 | 0.022725 | 5.4054 | 0 | 0 | 21.0685 | 0 | 0 | 52.6451 | 0.9718% | Full-service Restaurant | 0 | 0 | 0.53072 | 0.47331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8133 | 0.9718% | Full-service Restaurant | 39.6442 | 17.4561 | 97.9049 | 51.7329 | 0 | 99.9914 | 0 | 76.7601 | 0 | 0.23791 | 56.5892 | 0 | 0 | 309.0225 | 0 | 0 | 749.3391 | 0.9718%
Mid-rise Apartment | 0.13482 | 0.034495 | 0.33193 | 0.067148 | 0 | 0.1446 | 0 | 0.081396 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.2421 | 13.69% | Mid-rise Apartment | 4.3276 | 1.1072 | 10.6543 | 6.8518 | 0 | 4.6414 | 0 | 2.6126 | 0 | 0 | 0 | 3.5203 | 0 | 0 | 0 | 10.849 | 44.5643 | 13.69% | Mid-rise Apartment | 1.2683 | 0.32451 | 3.1226 | 0 | 0 | 1.3603 | 0 | 0.76572 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 11.0529 | 13.69% | Mid-rise Apartment | 0 | 0 | 0 | 0.068518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068518 | 13.69% | Mid-rise Apartment | 13.2783 | 3.3973 | 32.6904 | 7.489 | 0 | 14.2411 | 0 | 8.0164 | 0 | 0 | 0 | 10.8014 | 0 | 0 | 0 | 33.2879 | 123.2017 | 13.69%
High-rise Apartment | 0.13548 | 0.058979 | 0.1163 | 0.12543 | 0 | 0.19239 | 0.0088263 | 0.088979 | 0 | 0.016525 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.1463 | 9.636% | High-rise Apartment | 4.3485 | 1.8931 | 11.8678 | 8.5608 | 0 | 6.1752 | 0.28331 | 2.856 | 0 | 0.53042 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 49.4617 | 9.636% | High-rise Apartment | 1.2745 | 0.55484 | 0 | 0.57003 | 0 | 1.8098 | 0.083032 | 0.83706 | 0 | 0.15546 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 9.0792 | 9.636% | High-rise Apartment | 0 | 0 | 0.11868 | 0.066159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18484 | 9.636% | High-rise Apartment | 13.3426 | 5.8086 | 12.9715 | 13.1988 | 0 | 18.9473 | 0.86926 | 8.7632 | 0 | 1.6275 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 115.2523 | 9.636%
Warehouse | 0.1777 | 0.047513 | 0.014071 | 0.072624 | 0 | 0.025962 | 0 | 0.035294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.45095 | 18.56% | Warehouse | 5.7038 | 1.5251 | 0.45164 | 7.4106 | 0 | 0.83334 | 0 | 1.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 19.554 | 18.56% | Warehouse | 1.6717 | 0.44697 | 0.13237 | 0 | 0 | 0.24424 | 0 | 0.33203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.559 | 18.56% | Warehouse | 0 | 0 | 0 | 0.074106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074106 | 18.56% | Warehouse | 17.501 | 4.6793 | 1.3858 | 8.0998 | 0 | 2.5569 | 0 | 3.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 45.3592 | 18.56%
US Weighted | 0.28167 | 0.050575 | 0.10167 | 0.10517 | 0.013043 | 0.22779 | 0.0053585 | 0.14989 | 0.0086769 | 0.0082811 | 0.018293 | 0.072453 | 0.003476 | 0.085537 | 0.021334 | 0.29137 | 1.4446 | 100% | US Weighted | 9.0411 | 1.6233 | 5.9936 | 9.0621 | 0.41865 | 7.3114 | 0.172 | 4.811 | 0.27851 | 0.2658 | 0.58716 | 2.3256 | 0.11157 | 4.8741 | 0.68478 | 9.4544 | 57.0152 | 100% | US Weighted | 2.6498 | 0.47578 | 0.58926 | 0.22454 | 0.1227 | 2.1429 | 0.050409 | 1.41 | 0.081627 | 0.077903 | 0.17209 | 0.68159 | 0.0327 | 0.51838 | 0.2007 | 2.7272 | 12.1576 | 100% | US Weighted | 0 | 0 | 0.03983 | 0.08296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.15533 | 100% | US Weighted | 27.7407 | 4.9809 | 10.5224 | 11.4183 | 1.2845 | 22.4336 | 0.52773 | 14.7617 | 0.85455 | 0.81556 | 1.8016 | 7.1356 | 0.34234 | 8.8211 | 2.1011 | 28.7143 | 144.2559 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | US All Buildings | [23 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.38093 | 0.1335 | 0.096844 | 0.057276 | 0 | 0.18142 | 0 | 0.13528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2687 | 3.798% | Small Office | 12.2271 | 4.2851 | 3.1085 | 2.6555 | 0 | 5.8232 | 0 | 4.3424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.5396 | 3.798% | Small Office | 3.5836 | 1.2559 | 0.91104 | 0.42891 | 0 | 1.7067 | 0 | 1.2727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.8252 | 3.798% | Small Office | 0 | 0 | 0 | 0.011921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011921 | 3.798% | Small Office | 37.5162 | 13.1478 | 9.5377 | 5.7932 | 0 | 17.8671 | 0 | 13.3236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 125.1008 | 3.798%
Medium Office | 0.30444 | 0.12408 | 0.014607 | 0.14204 | 0 | 0.25174 | 0 | 0.053007 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3581 | 5.009% | Medium Office | 9.772 | 3.9826 | 1.4905 | 6.0967 | 0 | 8.0804 | 0 | 1.7014 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 46.1526 | 5.009% | Medium Office | 2.864 | 1.1672 | 0 | 1.1295 | 0 | 2.3682 | 0 | 0.49865 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.4324 | 5.009% | Medium Office | 0 | 0 | 0.014905 | 0.022429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037334 | 5.009% | Medium Office | 29.9833 | 12.2196 | 1.6291 | 14.276 | 0 | 24.793 | 0 | 5.2204 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 134.2351 | 5.009%
Large Office | 0.30444 | 0.058431 | 0.010631 | 0.059194 | 0.0074914 | 0.28998 | 0.1029 | 0.14364 | 0 | 0.06472 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0671 | 3.855% | Large Office | 9.772 | 1.8755 | 1.0848 | 6.0402 | 0.24046 | 9.3077 | 3.3029 | 4.6104 | 0 | 2.0774 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 71.2322 | 3.855% | Large Office | 2.864 | 0.54968 | 0 | 0 | 0.070474 | 2.7279 | 0.96804 | 1.3512 | 0 | 0.60884 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.7888 | 3.855% | Large Office | 0 | 0 | 0.010848 | 0.060402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071249 | 3.855% | Large Office | 29.9834 | 5.7546 | 1.1856 | 6.6019 | 0.73779 | 28.5587 | 10.1344 | 14.146 | 0 | 6.374 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 204.4872 | 3.855%
Standalone Retail | 0.58858 | 0.1376 | 0.035652 | 0.1062 | 0 | 0.40476 | 0 | 0.47676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.983 | 10.94% | Standalone Retail | 18.8922 | 4.4167 | 3.638 | 10.8372 | 0 | 12.9919 | 0 | 15.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 73.5721 | 10.94% | Standalone Retail | 5.537 | 1.2945 | 0 | 0 | 0 | 3.8077 | 0 | 4.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 17.3203 | 10.94% | Standalone Retail | 0 | 0 | 0.03638 | 0.10837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14475 | 10.94% | Standalone Retail | 57.9668 | 13.5518 | 3.9763 | 11.845 | 0 | 39.8629 | 0 | 46.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 197.148 | 10.94%
Strip Mall | 0.89433 | 0.21919 | 0.089124 | 0.10056 | 0 | 0.43486 | 0 | 0.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2613 | 3.712% | Strip Mall | 28.706 | 7.0354 | 2.8607 | 10.2616 | 0 | 13.958 | 0 | 11.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 79.6176 | 3.712% | Strip Mall | 8.4133 | 2.062 | 0.83842 | 0 | 0 | 4.0908 | 0 | 3.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.3271 | 3.712% | Strip Mall | 0 | 0 | 0 | 0.10262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10262 | 3.712% | Strip Mall | 88.0783 | 21.5866 | 8.7774 | 11.2159 | 0 | 42.827 | 0 | 34.8934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 224.0201 | 3.712%
Primary School | 0.48336 | 0.033243 | 0.02567 | 0.098193 | 0 | 0.41951 | 0 | 0.21848 | 0.044844 | 0.0013744 | 0.054371 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9413 | 4.828% | Primary School | 15.5148 | 1.067 | 1.8379 | 10.0197 | 0 | 13.4655 | 0 | 7.0128 | 1.4394 | 0.044114 | 1.7452 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 73.3654 | 4.828% | Primary School | 4.5471 | 0.31273 | 0.10511 | 0 | 0 | 3.9465 | 0 | 2.0553 | 0.42187 | 0.012929 | 0.51149 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 16.776 | 4.828% | Primary School | 0 | 0 | 0.014792 | 0.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16126 | 4.828% | Primary School | 47.6039 | 3.274 | 2.7172 | 10.9515 | 0 | 41.316 | 0 | 21.5172 | 4.4165 | 0.13536 | 5.3548 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 193.2535 | 4.828%
Secondary School | 0.46148 | 0.030358 | 0.04263 | 0.059824 | 0 | 0.44228 | 0 | 0.21885 | 0.045335 | 0.022048 | 0.02955 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.7456 | 10.92% | Secondary School | 14.8126 | 0.97441 | 2.8362 | 6.1045 | 0 | 14.1961 | 0 | 7.0246 | 1.4551 | 0.7077 | 0.94848 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 63.3609 | 10.92% | Secondary School | 4.3413 | 0.28558 | 0.20361 | 0 | 0 | 4.1606 | 0 | 2.0588 | 0.42648 | 0.20742 | 0.27798 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 15.4361 | 10.92% | Secondary School | 0 | 0 | 0.021415 | 0.061045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10693 | 10.92% | Secondary School | 45.4494 | 2.9898 | 4.4722 | 6.6723 | 0 | 43.5578 | 0 | 21.5536 | 4.4648 | 2.1714 | 2.9102 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 173.2877 | 10.92%
Outpatient Healthcare | 0.44094 | 0.16367 | 0.056291 | 0.6029 | 0.098189 | 0.754 | 0 | 0.37155 | 0 | 0.0030606 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.8704 | 3.419% | Outpatient Healthcare | 14.1533 | 5.2533 | 5.7439 | 29.0975 | 3.1517 | 24.2017 | 0 | 11.926 | 0 | 0.098238 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 140.9041 | 3.419% | Outpatient Healthcare | 4.1481 | 1.5397 | 0 | 4.3609 | 0.9237 | 7.0931 | 0 | 3.4953 | 0 | 0.028792 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.1681 | 3.419% | Outpatient Healthcare | 0 | 0 | 0.057439 | 0.14218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24323 | 3.419% | Outpatient Healthcare | 43.4265 | 16.1186 | 6.2781 | 61.1944 | 9.6702 | 74.2579 | 0 | 36.5925 | 0 | 0.30142 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 384.2903 | 3.419%
Hospital | 0.51158 | 0.031966 | 0.05144 | 0.58097 | 0.20535 | 0.49352 | 0.089247 | 0.52758 | 0 | 0.15279 | 0.033431 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9775 | 4.523% | Hospital | 16.4205 | 1.026 | 5.0042 | 51.688 | 6.5912 | 15.8408 | 2.8646 | 16.9342 | 0 | 4.9041 | 1.0731 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 171.5735 | 4.523% | Hospital | 4.8126 | 0.30071 | 0.032918 | 1.0214 | 1.9318 | 4.6427 | 0.83958 | 4.9631 | 0 | 1.4373 | 0.3145 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.5126 | 4.523% | Hospital | 0 | 0 | 0.048919 | 0.48203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64052 | 4.523% | Hospital | 50.3828 | 3.1481 | 5.6915 | 63.379 | 20.2238 | 48.6041 | 8.7895 | 51.9591 | 0 | 15.0471 | 3.2925 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 399.915 | 4.523%
Small Hotel | 0.3405 | 0.065124 | 0.12563 | 0.10951 | 0 | 0.31798 | 0 | 0.21696 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.678 | 1.588% | Small Hotel | 10.9295 | 2.0903 | 12.8193 | 4.1075 | 0 | 10.2065 | 0 | 6.964 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 69.5794 | 1.588% | Small Hotel | 3.2032 | 0.61265 | 0 | 0.95051 | 0 | 2.9913 | 0 | 2.041 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.6719 | 1.588% | Small Hotel | 0 | 0 | 0.12819 | 0.0086435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22931 | 1.588% | Small Hotel | 33.5348 | 6.4138 | 14.0115 | 10.8957 | 0 | 31.3164 | 0 | 21.3674 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 168.1948 | 1.588%
Large Hotel | 0.35129 | 0.074022 | 0.17928 | 0.2204 | 0 | 0.54241 | 0 | 0.15978 | 0 | 0.048013 | 0.025377 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.4035 | 4.219% | Large Hotel | 11.2757 | 2.3759 | 16.7211 | 22.4896 | 0 | 17.4102 | 0 | 5.1285 | 0 | 1.5411 | 0.81453 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 113.0441 | 4.219% | Large Hotel | 3.3047 | 0.69635 | 0.21152 | 0 | 0 | 5.1026 | 0 | 1.5031 | 0 | 0.45168 | 0.23873 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 17.7817 | 4.219% | Large Hotel | 0 | 0 | 0.15999 | 0.2249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.52373 | 4.219% | Large Hotel | 34.5972 | 7.2901 | 19.7017 | 24.5812 | 0 | 53.4195 | 0 | 15.7356 | 0 | 4.7286 | 2.4992 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 243.4003 | 4.219%
Quick-service Restaurant | 0.88668 | 0.32337 | 0.65841 | 0.74246 | 0 | 1.6254 | 0 | 1.6392 | 0 | 0 | 1.2772 | 0 | 0 | 4.5327 | 0 | 0 | 11.6854 | 0.3319% | Quick-service Restaurant | 28.4604 | 10.3794 | 67.1851 | 75.7613 | 0 | 52.1728 | 0 | 52.6137 | 0 | 0 | 40.9958 | 0 | 0 | 269.4388 | 0 | 0 | 597.0073 | 0.3319% | Quick-service Restaurant | 8.3413 | 3.042 | 0 | 0 | 0 | 15.291 | 0 | 15.4202 | 0 | 0 | 12.0152 | 0 | 0 | 25.9692 | 0 | 0 | 80.0789 | 0.3319% | Quick-service Restaurant | 0 | 0 | 0.67185 | 0.75761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2378 | 0.3319% | Quick-service Restaurant | 87.3246 | 31.8469 | 73.4333 | 82.8071 | 0 | 160.0813 | 0 | 161.4341 | 0 | 0 | 125.7869 | 0 | 0 | 469.5209 | 0 | 0 | 1192.2351 | 0.3319%
Full-service Restaurant | 0.99662 | 0.31167 | 0.93757 | 0.43682 | 0 | 1.4895 | 0 | 1.659 | 0 | 0.0024157 | 0.57248 | 0 | 0 | 3.0348 | 0 | 0 | 9.4409 | 0.9718% | Full-service Restaurant | 31.9893 | 10.0041 | 66.5135 | 44.5733 | 0 | 47.8105 | 0 | 53.2497 | 0 | 0.077539 | 18.3753 | 0 | 0 | 152.8844 | 0 | 0 | 425.4776 | 0.9718% | Full-service Restaurant | 9.3755 | 2.932 | 3.9216 | 0 | 0 | 14.0125 | 0 | 15.6066 | 0 | 0.022725 | 5.3855 | 0 | 0 | 21.0887 | 0 | 0 | 72.3452 | 0.9718% | Full-service Restaurant | 0 | 0 | 0.53133 | 0.44573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7864 | 0.9718% | Full-service Restaurant | 98.1523 | 30.6954 | 99.1297 | 48.7186 | 0 | 146.6964 | 0 | 163.3856 | 0 | 0.23791 | 56.3808 | 0 | 0 | 309.234 | 0 | 0 | 952.6307 | 0.9718%
Mid-rise Apartment | 0.12208 | 0.06384 | 0.33206 | 0.089143 | 0 | 0.14384 | 0 | 0.084313 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2884 | 13.69% | Mid-rise Apartment | 3.9185 | 2.0491 | 10.6583 | 9.0962 | 0 | 4.6168 | 0 | 2.7063 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9035 | 47.5896 | 13.69% | Mid-rise Apartment | 1.1484 | 0.60057 | 3.1238 | 0 | 0 | 1.3531 | 0 | 0.79316 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1956 | 11.2818 | 13.69% | Mid-rise Apartment | 0 | 0 | 0 | 0.090962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090962 | 13.69% | Mid-rise Apartment | 12.023 | 6.2873 | 32.7028 | 9.9421 | 0 | 14.1658 | 0 | 8.3036 | 0 | 0 | 0 | 11.1712 | 0 | 0 | 0 | 33.4551 | 128.0511 | 13.69%
High-rise Apartment | 0.1171 | 0.074714 | 0.11637 | 0.18017 | 0 | 0.19362 | 0.0091241 | 0.094789 | 0 | 0.02248 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2193 | 9.636% | High-rise Apartment | 3.7586 | 2.3982 | 11.8742 | 12.4668 | 0 | 6.2147 | 0.29287 | 3.0425 | 0 | 0.72156 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 53.9587 | 9.636% | High-rise Apartment | 1.1016 | 0.70286 | 0 | 0.7959 | 0 | 1.8214 | 0.085834 | 0.89171 | 0 | 0.21148 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.4763 | 9.636% | High-rise Apartment | 0 | 0 | 0.11874 | 0.097512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21625 | 9.636% | High-rise Apartment | 11.5325 | 7.3583 | 12.9785 | 18.9904 | 0 | 19.0684 | 0.89859 | 9.3353 | 0 | 2.214 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 122.8444 | 9.636%
Warehouse | 0.27352 | 0.070064 | 0.01452 | 0.089428 | 0 | 0.036896 | 0 | 0.040392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.60386 | 18.56% | Warehouse | 8.7793 | 2.2489 | 0.46605 | 9.1253 | 0 | 1.1843 | 0 | 1.2965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.6375 | 18.56% | Warehouse | 2.5731 | 0.65912 | 0.13659 | 0 | 0 | 0.34709 | 0 | 0.37999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.8394 | 18.56% | Warehouse | 0 | 0 | 0 | 0.091253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091253 | 18.56% | Warehouse | 26.9375 | 6.9003 | 1.43 | 9.9739 | 0 | 3.6337 | 0 | 3.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 60.6381 | 18.56%
US Weighted | 0.36261 | 0.085893 | 0.1024 | 0.14899 | 0.012933 | 0.30076 | 0.0088827 | 0.20958 | 0.0071155 | 0.016206 | 0.018237 | 0.074408 | 0.0061645 | 0.085569 | 0.021334 | 0.29682 | 1.7579 | 100% | US Weighted | 11.6389 | 2.757 | 6.0282 | 12.5273 | 0.41512 | 9.6537 | 0.28511 | 6.7272 | 0.22839 | 0.52017 | 0.58536 | 2.3883 | 0.19787 | 4.8752 | 0.68478 | 9.6296 | 69.1421 | 100% | US Weighted | 3.4112 | 0.80802 | 0.59457 | 0.35994 | 0.12166 | 2.8293 | 0.083562 | 1.9716 | 0.066938 | 0.15245 | 0.17156 | 0.69998 | 0.057992 | 0.51868 | 0.2007 | 2.7786 | 14.8268 | 100% | US Weighted | 0 | 0 | 0.039995 | 0.11299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.18553 | 100% | US Weighted | 35.7116 | 8.4592 | 10.5961 | 16.1182 | 1.2737 | 29.6202 | 0.87481 | 20.6409 | 0.70077 | 1.596 | 1.7961 | 7.3281 | 0.60712 | 8.8243 | 2.1011 | 29.2518 | 175.5 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [7 empty] | Building Type: | US All Buildings |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [7 empty] | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | US All Buildings | [23 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.38093 | 0.1335 | 0.096844 | 0.082117 | 0 | 0.22824 | 0 | 0.14092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.346 | 3.798% | Small Office | 12.2271 | 4.2851 | 3.1085 | 3.8082 | 0 | 7.3261 | 0 | 4.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.3761 | 3.798% | Small Office | 3.5836 | 1.2559 | 0.91104 | 0.61482 | 0 | 2.1472 | 0 | 1.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.5046 | 3.798% | Small Office | 0 | 0 | 0 | 0.017104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017104 | 3.798% | Small Office | 37.5162 | 13.1478 | 9.5377 | 8.306 | 0 | 22.4787 | 0 | 13.8786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 132.7801 | 3.798%
Medium Office | 0.30444 | 0.12408 | 0.014609 | 0.19525 | 0 | 0.26654 | 0 | 0.062225 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.4354 | 5.009% | Medium Office | 9.772 | 3.9826 | 1.4908 | 8.5074 | 0 | 8.5552 | 0 | 1.9973 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 49.3343 | 5.009% | Medium Office | 2.864 | 1.1672 | 0 | 1.5355 | 0 | 2.5074 | 0 | 0.58537 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.0643 | 5.009% | Medium Office | 0 | 0 | 0.014908 | 0.032682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04759 | 5.009% | Medium Office | 29.9833 | 12.2196 | 1.6294 | 19.6474 | 0 | 26.2499 | 0 | 6.1283 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 141.9715 | 5.009%
Large Office | 0.30444 | 0.058431 | 0.010631 | 0.079344 | 0.0077692 | 0.2978 | 0.10497 | 0.14836 | 0 | 0.064471 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.1019 | 3.855% | Large Office | 9.772 | 1.8755 | 1.0848 | 8.0963 | 0.24937 | 9.5588 | 3.3693 | 4.762 | 0 | 2.0694 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 73.7584 | 3.855% | Large Office | 2.864 | 0.54968 | 0 | 0 | 0.073087 | 2.8015 | 0.9875 | 1.3957 | 0 | 0.6065 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.9265 | 3.855% | Large Office | 0 | 0 | 0.010848 | 0.080963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091811 | 3.855% | Large Office | 29.9834 | 5.7546 | 1.1857 | 8.8493 | 0.76515 | 29.3291 | 10.3381 | 14.6112 | 0 | 6.3494 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 208.1767 | 3.855%
Standalone Retail | 0.58858 | 0.1376 | 0.03567 | 0.16932 | 0 | 0.44671 | 0 | 0.54528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.1566 | 10.94% | Standalone Retail | 18.8922 | 4.4167 | 3.6398 | 17.2778 | 0 | 14.3384 | 0 | 17.5023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 83.5604 | 10.94% | Standalone Retail | 5.537 | 1.2945 | 0 | 0 | 0 | 4.2023 | 0 | 5.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 18.3596 | 10.94% | Standalone Retail | 0 | 0 | 0.036398 | 0.17278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20918 | 10.94% | Standalone Retail | 57.9668 | 13.5518 | 3.9783 | 18.8846 | 0 | 43.9944 | 0 | 53.7021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 215.0691 | 10.94%
Strip Mall | 0.8297 | 0.21919 | 0.089296 | 0.18115 | 0 | 0.45174 | 0 | 0.37824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.3183 | 3.712% | Strip Mall | 26.6317 | 7.0354 | 2.8662 | 18.4843 | 0 | 14.4999 | 0 | 12.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 87.0818 | 3.712% | Strip Mall | 7.8053 | 2.062 | 0.84004 | 0 | 0 | 4.2497 | 0 | 3.5582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.1048 | 3.712% | Strip Mall | 0 | 0 | 0 | 0.18484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18484 | 3.712% | Strip Mall | 81.7137 | 21.5866 | 8.7944 | 20.2033 | 0 | 44.4899 | 0 | 37.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 230.6802 | 3.712%
Primary School | 0.48336 | 0.033243 | 0.025689 | 0.12787 | 0 | 0.44626 | 0 | 0.24699 | 0.058845 | 0.0017805 | 0.054373 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.0407 | 4.828% | Primary School | 15.5148 | 1.067 | 1.8396 | 13.0476 | 0 | 14.3241 | 0 | 7.9278 | 1.8888 | 0.05715 | 1.7453 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 78.6312 | 4.828% | Primary School | 4.5471 | 0.31273 | 0.10514 | 0 | 0 | 4.1981 | 0 | 2.3235 | 0.55357 | 0.01675 | 0.51151 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 17.4314 | 4.828% | Primary School | 0 | 0 | 0.014809 | 0.13048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19155 | 4.828% | Primary School | 47.6039 | 3.274 | 2.7193 | 14.2611 | 0 | 43.9504 | 0 | 24.3247 | 5.7953 | 0.17535 | 5.355 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 203.4261 | 4.828%
Secondary School | 0.46148 | 0.030358 | 0.042637 | 0.09296 | 0 | 0.48162 | 0 | 0.29191 | 0.074845 | 0.024008 | 0.029549 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.9227 | 10.92% | Secondary School | 14.8126 | 0.97441 | 2.837 | 9.4857 | 0 | 15.4591 | 0 | 9.3698 | 2.4024 | 0.7706 | 0.94846 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 71.361 | 10.92% | Secondary School | 4.3413 | 0.28558 | 0.20361 | 0 | 0 | 4.5308 | 0 | 2.7461 | 0.70409 | 0.22585 | 0.27798 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 16.7896 | 10.92% | Secondary School | 0 | 0 | 0.021422 | 0.094857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.14075 | 10.92% | Secondary School | 45.4494 | 2.9898 | 4.473 | 10.3679 | 0 | 47.4329 | 0 | 28.7491 | 7.3712 | 2.3644 | 2.9102 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 191.1539 | 10.92%
Outpatient Healthcare | 0.44094 | 0.16367 | 0.05629 | 0.73425 | 0.12064 | 0.79807 | 0 | 0.41124 | 0 | 0.0034673 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1084 | 3.419% | Outpatient Healthcare | 14.1533 | 5.2533 | 5.7439 | 35.1462 | 3.8724 | 25.6162 | 0 | 13.1999 | 0 | 0.11129 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 150.3748 | 3.419% | Outpatient Healthcare | 4.1481 | 1.5397 | 0 | 5.35 | 1.1349 | 7.5077 | 0 | 3.8687 | 0 | 0.032618 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.1602 | 3.419% | Outpatient Healthcare | 0 | 0 | 0.057439 | 0.16892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26996 | 3.419% | Outpatient Healthcare | 43.4265 | 16.1186 | 6.278 | 74.472 | 11.8816 | 78.5979 | 0 | 40.5011 | 0 | 0.34148 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 408.0678 | 3.419%
Hospital | 0.51158 | 0.031966 | 0.051436 | 0.55488 | 0.20542 | 0.49096 | 0.08713 | 0.54439 | 0 | 0.1493 | 0.033431 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9602 | 4.523% | Hospital | 16.4205 | 1.026 | 5.0038 | 49.0222 | 6.5935 | 15.7588 | 2.7967 | 17.4738 | 0 | 4.7924 | 1.0731 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 169.1875 | 4.523% | Hospital | 4.8126 | 0.30071 | 0.032918 | 1.022 | 1.9324 | 4.6186 | 0.81966 | 5.1213 | 0 | 1.4046 | 0.3145 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.5953 | 4.523% | Hospital | 0 | 0 | 0.048915 | 0.45535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.61384 | 4.523% | Hospital | 50.3828 | 3.1481 | 5.6911 | 60.4693 | 20.2308 | 48.3525 | 8.581 | 53.6148 | 0 | 14.7043 | 3.2925 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 397.8647 | 4.523%
Small Hotel | 0.3405 | 0.065124 | 0.12573 | 0.19438 | 0 | 0.33409 | 0 | 0.218 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.7802 | 1.588% | Small Hotel | 10.9295 | 2.0903 | 12.8298 | 8.185 | 0 | 10.7235 | 0 | 6.9972 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 74.2176 | 1.588% | Small Hotel | 3.2032 | 0.61265 | 0 | 1.5669 | 0 | 3.1429 | 0 | 2.0508 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.4495 | 1.588% | Small Hotel | 0 | 0 | 0.1283 | 0.028389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24916 | 1.588% | Small Hotel | 33.5348 | 6.4138 | 14.023 | 19.5063 | 0 | 32.9027 | 0 | 21.4694 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 178.5051 | 1.588%
Large Hotel | 0.35129 | 0.074022 | 0.17936 | 0.22982 | 0 | 0.61287 | 0 | 0.30235 | 0.099276 | 0.059459 | 0.025033 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.7364 | 4.219% | Large Hotel | 11.2757 | 2.3759 | 16.7279 | 23.4507 | 0 | 19.672 | 0 | 9.7049 | 3.1865 | 1.9085 | 0.8035 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 124.393 | 4.219% | Large Hotel | 3.3047 | 0.69635 | 0.21168 | 0 | 0 | 5.7655 | 0 | 2.8444 | 0.93392 | 0.55935 | 0.23549 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 20.8244 | 4.219% | Large Hotel | 0 | 0 | 0.16006 | 0.23451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.5334 | 4.219% | Large Hotel | 34.5972 | 7.2901 | 19.7102 | 25.6316 | 0 | 60.3592 | 0 | 29.7775 | 9.7772 | 5.8559 | 2.4654 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 276.3114 | 4.219%
Quick-service Restaurant | 0.88668 | 0.32337 | 0.65768 | 0.94706 | 0 | 1.7413 | 0 | 1.6713 | 0 | 0 | 1.2866 | 0 | 0 | 4.5327 | 0 | 0 | 12.0466 | 0.3319% | Quick-service Restaurant | 28.4604 | 10.3794 | 67.11 | 96.6386 | 0 | 55.8912 | 0 | 53.6441 | 0 | 0 | 41.298 | 0 | 0 | 269.4388 | 0 | 0 | 622.8604 | 0.3319% | Quick-service Restaurant | 8.3413 | 3.042 | 0 | 0 | 0 | 16.3808 | 0 | 15.7222 | 0 | 0 | 12.1037 | 0 | 0 | 25.9692 | 0 | 0 | 81.5592 | 0.3319% | Quick-service Restaurant | 0 | 0 | 0.6711 | 0.96639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.4458 | 0.3319% | Quick-service Restaurant | 87.3246 | 31.8469 | 73.3512 | 105.626 | 0 | 171.4904 | 0 | 164.5955 | 0 | 0 | 126.7142 | 0 | 0 | 469.5209 | 0 | 0 | 1230.4696 | 0.3319%
Full-service Restaurant | 0.99662 | 0.31167 | 0.93528 | 0.72345 | 0 | 1.7986 | 0 | 1.7809 | 0 | 0.0024157 | 0.58688 | 0 | 0 | 3.0348 | 0 | 0 | 10.1707 | 0.9718% | Full-service Restaurant | 31.9893 | 10.0041 | 66.3398 | 73.8219 | 0 | 57.7319 | 0 | 57.1645 | 0 | 0.077539 | 18.8377 | 0 | 0 | 152.8844 | 0 | 0 | 468.851 | 0.9718% | Full-service Restaurant | 9.3755 | 2.932 | 3.9135 | 0 | 0 | 16.9202 | 0 | 16.754 | 0 | 0.022725 | 5.521 | 0 | 0 | 21.0887 | 0 | 0 | 76.5277 | 0.9718% | Full-service Restaurant | 0 | 0 | 0.52987 | 0.73822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0774 | 0.9718% | Full-service Restaurant | 98.1523 | 30.6954 | 98.8851 | 80.6874 | 0 | 177.138 | 0 | 175.3973 | 0 | 0.23791 | 57.7994 | 0 | 0 | 309.234 | 0 | 0 | 1028.2267 | 0.9718%
Mid-rise Apartment | 0.12208 | 0.06384 | 0.33212 | 0.10226 | 0 | 0.18221 | 0 | 0.08798 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3436 | 13.69% | Mid-rise Apartment | 3.9185 | 2.0491 | 10.6602 | 10.4345 | 0 | 5.8486 | 0 | 2.824 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9035 | 50.2793 | 13.69% | Mid-rise Apartment | 1.1484 | 0.60057 | 3.1243 | 0 | 0 | 1.7141 | 0 | 0.82766 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1956 | 11.6778 | 13.69% | Mid-rise Apartment | 0 | 0 | 0 | 0.10435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10435 | 13.69% | Mid-rise Apartment | 12.023 | 6.2873 | 32.7087 | 11.4049 | 0 | 17.9452 | 0 | 8.6648 | 0 | 0 | 0 | 11.1712 | 0 | 0 | 0 | 33.4551 | 133.6603 | 13.69%
High-rise Apartment | 0.1171 | 0.074714 | 0.11637 | 0.19952 | 0 | 0.19939 | 0.0095382 | 0.098893 | 0 | 0.023941 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2504 | 9.636% | High-rise Apartment | 3.7586 | 2.3982 | 11.8742 | 13.8033 | 0 | 6.4001 | 0.30616 | 3.1742 | 0 | 0.76845 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 55.6725 | 9.636% | High-rise Apartment | 1.1016 | 0.70286 | 0 | 0.88171 | 0 | 1.8758 | 0.089729 | 0.93032 | 0 | 0.22522 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.6727 | 9.636% | High-rise Apartment | 0 | 0 | 0.11874 | 0.10795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22669 | 9.636% | High-rise Apartment | 11.5325 | 7.3583 | 12.9785 | 21.0294 | 0 | 19.6374 | 0.93938 | 9.7395 | 0 | 2.3578 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 126.0412 | 9.636%
Warehouse | 0.27352 | 0.070064 | 0.01452 | 0.11022 | 0 | 0.037126 | 0 | 0.040931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.62542 | 18.56% | Warehouse | 8.7793 | 2.2489 | 0.46606 | 11.2466 | 0 | 1.1916 | 0 | 1.3138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 27.7835 | 18.56% | Warehouse | 2.5731 | 0.65912 | 0.13659 | 0 | 0 | 0.34925 | 0 | 0.38505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.8467 | 18.56% | Warehouse | 0 | 0 | 0 | 0.11247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11247 | 18.56% | Warehouse | 26.9375 | 6.9003 | 1.43 | 12.2926 | 0 | 3.6563 | 0 | 4.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 63.0325 | 18.56%
US Weighted | 0.36021 | 0.085893 | 0.1024 | 0.18437 | 0.013714 | 0.32824 | 0.0089066 | 0.23862 | 0.015202 | 0.01691 | 0.018394 | 0.074408 | 0.0061645 | 0.085569 | 0.021334 | 0.29682 | 1.8572 | 100% | US Weighted | 11.5619 | 2.757 | 6.0276 | 15.5472 | 0.4402 | 10.5359 | 0.28588 | 7.6592 | 0.48795 | 0.54277 | 0.5904 | 2.3883 | 0.19787 | 4.8752 | 0.68478 | 9.6296 | 74.2117 | 100% | US Weighted | 3.3886 | 0.80802 | 0.59464 | 0.43923 | 0.12902 | 3.0879 | 0.083787 | 2.2448 | 0.14301 | 0.15908 | 0.17304 | 0.69998 | 0.057992 | 0.51868 | 0.2007 | 2.7786 | 15.507 | 100% | US Weighted | 0 | 0 | 0.039986 | 0.14049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031054 | 0 | 0.0014907 | 0.21302 | 100% | US Weighted | 35.4753 | 8.4592 | 10.5958 | 19.9534 | 1.3507 | 32.3273 | 0.87717 | 23.5005 | 1.4972 | 1.6654 | 1.8115 | 7.3281 | 0.60712 | 8.8243 | 2.1011 | 29.2518 | 185.6259 | 100%
Building Type: | US All Buildings |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | US All Buildings |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [14 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [23 empty] | Building Type: | US All Buildings | [23 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 0.24227 | 0.10288 | 0.00016157 | 0.034529 | 0 | 0.11282 | 0 | 0.048905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.56578 | 3.798% | Small Office | 7.7764 | 3.3023 | 0.0051861 | 1.6784 | 0 | 3.6213 | 0 | 1.5698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 18.7304 | 3.798% | Small Office | 2.2791 | 0.96784 | 0.0015199 | 0.24816 | 0 | 1.0613 | 0 | 0.46007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 5.2458 | 3.798% | Small Office | 0 | 0 | 0 | 0.0083167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083167 | 3.798% | Small Office | 23.8601 | 10.1324 | 0.015912 | 3.507 | 0 | 11.1112 | 0 | 4.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 55.8274 | 3.798%
Medium Office | 0.16848 | 0.098222 | 0.0006547 | 0.13764 | 0 | 0.10887 | 0 | 0.02251 | -5.2186e-05 | 0 | 0 | 0.0052708 | 0.012148 | 0 | 0 | 0.031173 | 0.58492 | 5.009% | Medium Office | 5.4078 | 3.1527 | 0.066806 | 5.2672 | 0 | 3.4945 | 0 | 0.72251 | -0.0016751 | 0 | 0 | 0.16918 | 0.38993 | 0 | 0 | 1.0006 | 19.6695 | 5.009% | Medium Office | 1.5849 | 0.92401 | 0 | 1.1807 | 0 | 1.0242 | 0 | 0.21176 | -0.00049093 | 0 | 0 | 0.049584 | 0.11428 | 0 | 0 | 0.29326 | 5.3821 | 5.009% | Medium Office | 0 | 0 | 0.00066806 | 0.012388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013056 | 5.009% | Medium Office | 16.5926 | 9.6734 | 0.073019 | 13.7143 | 0 | 10.7221 | 0 | 2.2169 | -0.0051396 | 0 | 0 | 0.51909 | 1.1964 | 0 | 0 | 3.0701 | 57.7727 | 5.009%
Large Office | 0.15146 | 0.038046 | 0.00035546 | 0.06713 | -0.047255 | 0.12983 | 0.048129 | 0.025314 | -0.0020252 | 0.042824 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.49419 | 3.855% | Large Office | 4.8617 | 1.2212 | 0.036271 | 6.85 | -1.5168 | 4.1673 | 1.5448 | 0.81254 | -0.065004 | 1.3746 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 20.5825 | 3.855% | Large Office | 1.4249 | 0.35791 | 0 | 0 | -0.44454 | 1.2214 | 0.45276 | 0.23814 | -0.019052 | 0.40286 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 4.0141 | 3.855% | Large Office | 0 | 0 | 0.00036271 | 0.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068863 | 3.855% | Large Office | 14.9171 | 3.747 | 0.039644 | 7.4871 | -4.6539 | 12.7865 | 4.74 | 2.4931 | -0.19945 | 4.2176 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 49.5507 | 3.855%
Standalone Retail | 0.3036 | 0.091497 | 0.00075956 | 0.05316 | 0 | 0.22715 | 0 | 0.37243 | -0.00013288 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.0495 | 10.94% | Standalone Retail | 9.7448 | 2.9369 | 0.077506 | 5.4245 | 0 | 7.2911 | 0 | 11.9541 | -0.0042652 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 37.4575 | 10.94% | Standalone Retail | 2.856 | 0.86074 | 0 | 0 | 0 | 2.1369 | 0 | 3.5035 | -0.0012501 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 9.3656 | 10.94% | Standalone Retail | 0 | 0 | 0.00077506 | 0.054245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05502 | 10.94% | Standalone Retail | 29.8998 | 9.0111 | 0.084714 | 5.9289 | 0 | 22.3711 | 0 | 36.6786 | -0.013087 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 104.0625 | 10.94%
Strip Mall | 0.30126 | 0.14114 | 0.0074003 | 0.067574 | 0 | 0.22502 | 0 | 0.23432 | -3.1875e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.97745 | 3.712% | Strip Mall | 9.6697 | 4.5302 | 0.23753 | 6.8953 | 0 | 7.2227 | 0 | 7.5211 | -0.00010231 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 36.1005 | 3.712% | Strip Mall | 2.834 | 1.3277 | 0.069617 | 0 | 0 | 2.1169 | 0 | 2.2043 | -2.9986e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 8.5596 | 3.712% | Strip Mall | 0 | 0 | 0 | 0.068953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068953 | 3.712% | Strip Mall | 29.6693 | 13.9001 | 0.72882 | 7.5366 | 0 | 22.1614 | 0 | 23.0769 | -0.00031393 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 97.1465 | 3.712%
Primary School | 0.36875 | 0.023007 | 0.0010445 | 0.0901 | 0 | 0.24191 | 0 | 0.12389 | 0.031979 | 0.0009826 | 0.025466 | 0 | 0.012362 | 0 | 0 | 0.059552 | 0.97904 | 4.828% | Primary School | 11.8362 | 0.73847 | 0.046614 | 9.1938 | 0 | 7.7648 | 0 | 3.9764 | 1.0264 | 0.031539 | 0.81739 | 0 | 0.39678 | 0 | 0 | 1.9115 | 37.74 | 4.828% | Primary School | 3.469 | 0.21643 | 0.0080658 | 0 | 0 | 2.2757 | 0 | 1.1654 | 0.30083 | 0.0092436 | 0.23956 | 0 | 0.11629 | 0 | 0 | 0.56023 | 8.3608 | 4.828% | Primary School | 0 | 0 | 0.00019094 | 0.091938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092129 | 4.828% | Primary School | 36.3168 | 2.2658 | 0.10531 | 10.0489 | 0 | 23.8246 | 0 | 12.2009 | 3.1494 | 0.096772 | 2.508 | 0 | 1.2175 | 0 | 0 | 5.865 | 97.599 | 4.828%
Secondary School | 0.34664 | 0.020827 | 0.00010795 | 0.063604 | 0 | 0.25036 | 0 | 0.18115 | 0.044275 | 0.020051 | 0.012549 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.97643 | 10.92% | Secondary School | 11.1265 | 0.66851 | 0.0097306 | 6.4902 | 0 | 8.0359 | 0 | 5.8145 | 1.4211 | 0.64359 | 0.40279 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 35.7961 | 10.92% | Secondary School | 3.261 | 0.19593 | 0.00017275 | 0 | 0 | 2.3552 | 0 | 1.7041 | 0.41651 | 0.18862 | 0.11805 | 0.01311 | 0.065785 | 0 | 0 | 0.2679 | 8.5864 | 10.92% | Secondary School | 0 | 0 | 9.1411e-05 | 0.064902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064993 | 10.92% | Secondary School | 34.1393 | 2.0512 | 0.0118 | 7.0938 | 0 | 24.6564 | 0 | 17.8406 | 4.3604 | 1.9747 | 1.2359 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 96.9946 | 10.92%
Outpatient Healthcare | 0.16599 | 0.12422 | 0.0066274 | 0.49946 | 0.026377 | 0.28008 | 0 | 0.16658 | 0 | 0.0010198 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2878 | 3.419% | Outpatient Healthcare | 5.3279 | 3.9872 | 0.67626 | 20.0811 | 0.84665 | 8.9899 | 0 | 5.347 | 0 | 0.032734 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 45.8493 | 3.419% | Outpatient Healthcare | 1.5615 | 1.1686 | 0 | 4.154 | 0.24814 | 2.6348 | 0 | 1.5671 | 0 | 0.0095938 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.508 | 3.419% | Outpatient Healthcare | 0 | 0 | 0.0067626 | 0.059078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065841 | 3.419% | Outpatient Healthcare | 16.3477 | 12.234 | 0.73916 | 49.945 | 2.5978 | 27.5835 | 0 | 16.4061 | 0 | 0.10044 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 127.6735 | 3.419%
Hospital | 0.11071 | 0.013014 | 0.0022191 | 0.44579 | 0.11286 | 0.15064 | 0.055816 | 0.18992 | -0.020866 | 0.10396 | 0.015821 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2178 | 4.523% | Hospital | 3.5536 | 0.41773 | 0.20753 | 38.8799 | 3.6226 | 4.8351 | 1.7916 | 6.096 | -0.66975 | 3.3369 | 0.50781 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 63.796 | 4.523% | Hospital | 1.0415 | 0.12243 | 0.0025435 | 0.88895 | 1.0617 | 1.4171 | 0.52508 | 1.7866 | -0.19629 | 0.978 | 0.14883 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.1332 | 4.523% | Hospital | 0 | 0 | 0.0019885 | 0.35847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36046 | 4.523% | Hospital | 10.9034 | 1.2817 | 0.24397 | 48.4869 | 11.1153 | 14.8355 | 5.4971 | 18.7043 | -2.055 | 10.2386 | 1.5581 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 124.5441 | 4.523%
Small Hotel | 0.21455 | 0.034836 | 0.0022145 | 0.12604 | 0 | 0.12874 | 0 | 0.10767 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.64432 | 1.588% | Small Hotel | 6.8865 | 1.1182 | 0.22597 | 5.2736 | 0 | 4.1322 | 0 | 3.456 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 22.0642 | 1.588% | Small Hotel | 2.0183 | 0.32771 | 0 | 1.0206 | 0 | 1.2111 | 0 | 1.0129 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.8754 | 1.588% | Small Hotel | 0 | 0 | 0.0022597 | 0.017914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020174 | 1.588% | Small Hotel | 21.1297 | 3.4308 | 0.24699 | 12.6422 | 0 | 12.6789 | 0 | 10.6041 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 63.7142 | 1.588%
Large Hotel | 0.22398 | 0.029815 | 0.0009733 | 0.2068 | 0 | 0.30075 | 0 | 0.13347 | 0.0747 | 0.04648 | 0.0099989 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0633 | 4.219% | Large Hotel | 7.1893 | 0.957 | 0.057607 | 21.1023 | 0 | 9.6535 | 0 | 4.2841 | 2.3977 | 1.4919 | 0.32094 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 48.6211 | 4.219% | Large Hotel | 2.1071 | 0.28048 | 0.0056098 | 0 | 0 | 2.8293 | 0 | 1.2556 | 0.70272 | 0.43725 | 0.094063 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 8.054 | 4.219% | Large Hotel | 0 | 0 | 0.00038467 | 0.21102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21141 | 4.219% | Large Hotel | 22.0587 | 2.9363 | 0.10077 | 23.0648 | 0 | 29.6198 | 0 | 13.1448 | 7.3568 | 4.5776 | 0.98475 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 107.4246 | 4.219%
Quick-service Restaurant | 0.58752 | 0.21953 | -0.00040268 | 0.29176 | 0 | 0.69462 | 0 | 1.0162 | 0 | 0 | 0.61446 | 0 | 0 | 0.0034248 | 0 | 0 | 3.4271 | 0.3319% | Quick-service Restaurant | 18.8582 | 7.0465 | -0.04109 | 29.7714 | 0 | 22.2958 | 0 | 32.6172 | 0 | 0 | 19.7228 | 0 | 0 | 0.10993 | 0 | 0 | 130.3808 | 0.3319% | Quick-service Restaurant | 5.527 | 2.0652 | 0 | 0 | 0 | 6.5345 | 0 | 9.5596 | 0 | 0 | 5.7804 | 0 | 0 | 0.032218 | 0 | 0 | 29.499 | 0.3319% | Quick-service Restaurant | 0 | 0 | -0.0004109 | 0.29771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2973 | 0.3319% | Quick-service Restaurant | 57.8623 | 21.6208 | -0.044911 | 32.5401 | 0 | 68.4099 | 0 | 100.079 | 0 | 0 | 60.5154 | 0 | 0 | 0.3373 | 0 | 0 | 341.3199 | 0.3319%
Full-service Restaurant | 0.72687 | 0.21163 | 0.010446 | 0.25663 | 0 | 0.88102 | 0 | 1.2199 | 0 | 0 | 0.28797 | 0 | 0 | 0.0030062 | 0 | 0 | 3.5975 | 0.9718% | Full-service Restaurant | 23.331 | 6.7927 | 0.30299 | 26.1869 | 0 | 28.2789 | 0 | 39.1564 | 0 | 0 | 9.2431 | 0 | 0 | 0.096493 | 0 | 0 | 133.3886 | 0.9718% | Full-service Restaurant | 6.8379 | 1.9908 | 0.10262 | 0 | 0 | 8.2881 | 0 | 11.4761 | 0 | 0 | 2.709 | 0 | 0 | 0.028281 | 0 | 0 | 31.4328 | 0.9718% | Full-service Restaurant | 0 | 0 | -0.00047148 | 0.26187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2614 | 0.9718% | Full-service Restaurant | 71.5863 | 20.8421 | 1.0228 | 28.6223 | 0 | 86.7679 | 0 | 120.1431 | 0 | 0 | 28.3606 | 0 | 0 | 0.29607 | 0 | 0 | 357.6411 | 0.9718%
Mid-rise Apartment | 0.049047 | 0.041135 | 0.00089931 | 0.075047 | 0 | 0.074613 | 0 | 0.018696 | 0 | 0 | 0 | 0.0040442 | 0 | 0 | 0 | 0.0016982 | 0.26518 | 13.69% | Mid-rise Apartment | 1.5743 | 1.3203 | 0.028866 | 7.6578 | 0 | 2.3949 | 0 | 0.60009 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 13.7606 | 13.69% | Mid-rise Apartment | 0.4614 | 0.38697 | 0.0084601 | 0 | 0 | 0.70191 | 0 | 0.17588 | 0 | 0 | 0 | 0.038045 | 0 | 0 | 0 | 0.015976 | 1.7886 | 13.69% | Mid-rise Apartment | 0 | 0 | 0 | 0.076578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076578 | 13.69% | Mid-rise Apartment | 4.8304 | 4.0512 | 0.088568 | 8.37 | 0 | 7.3483 | 0 | 1.8412 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 27.0952 | 13.69%
High-rise Apartment | 0.044998 | 0.033428 | 0.00041821 | 0.13267 | 0 | 0.058069 | 0.0060548 | 0.019284 | 0 | 0.011882 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.3167 | 9.636% | High-rise Apartment | 1.4443 | 1.073 | 0.042675 | 9.2213 | 0 | 1.8639 | 0.19435 | 0.61896 | 0 | 0.38139 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 15.1576 | 9.636% | High-rise Apartment | 0.42331 | 0.31446 | 0 | 0.58054 | 0 | 0.54628 | 0.05696 | 0.18141 | 0 | 0.11178 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.3079 | 9.636% | High-rise Apartment | 0 | 0 | 0.00042675 | 0.072405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072831 | 9.636% | High-rise Apartment | 4.4317 | 3.2921 | 0.046644 | 13.9915 | 0 | 5.719 | 0.59631 | 1.8991 | 0 | 1.1702 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 32.1215 | 9.636%
Warehouse | 0.17809 | 0.03781 | 0.00045175 | 0.042352 | 0 | 0.017903 | 0 | 0.013022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.29121 | 18.56% | Warehouse | 5.7164 | 1.2136 | 0.0145 | 4.3217 | 0 | 0.57465 | 0 | 0.41798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 12.3095 | 18.56% | Warehouse | 1.6754 | 0.35569 | 0.0042498 | 0 | 0 | 0.16842 | 0 | 0.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.3411 | 18.56% | Warehouse | 0 | 0 | 0 | 0.043217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043217 | 18.56% | Warehouse | 17.5396 | 3.7237 | 0.044491 | 4.7236 | 0 | 1.7632 | 0 | 1.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 29.2324 | 18.56%
US Weighted | 0.20019 | 0.054231 | 0.0012233 | 0.11276 | 0.0041844 | 0.14809 | 0.0049633 | 0.12286 | 0.0084908 | 0.01173 | 0.0085751 | 0.0021322 | 0.0038381 | 4.0582e-05 | 0 | 0.012936 | 0.69625 | 100% | US Weighted | 6.4257 | 1.7407 | 0.077641 | 9.1049 | 0.13431 | 4.7534 | 0.15931 | 3.9436 | 0.27254 | 0.37652 | 0.27524 | 0.068438 | 0.12319 | 0.0013026 | 0 | 0.41523 | 27.872 | 100% | US Weighted | 1.8833 | 0.51017 | 0.006346 | 0.32293 | 0.039364 | 1.3931 | 0.046691 | 1.1558 | 0.079876 | 0.11035 | 0.080668 | 0.020058 | 0.036106 | 0.00038177 | 0 | 0.1217 | 5.8068 | 100% | US Weighted | 0 | 0 | 0.00055988 | 0.080031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080591 | 100% | US Weighted | 19.7159 | 5.341 | 0.12763 | 12.1281 | 0.4121 | 14.5847 | 0.48881 | 12.1001 | 0.83622 | 1.1553 | 0.84452 | 0.20999 | 0.378 | 0.0039967 | 0 | 1.2741 | 69.6003 | 100%
Building Type: | US All Buildings |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | US All Buildings |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | US All Buildings |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | US All Buildings |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [14 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [23 empty] | Building Type: | US All Buildings | [23 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
Small Office | 63.6% | 77.07% | 0.1668% | 42.05% |  | 49.43% |  | 34.7% | [7 empty] | 8.542% | 42.03% | 3.798% | Small Office | 63.6% | 77.07% | 0.1668% | 44.07% |  | 49.43% |  | 34.7% | [7 empty] | 8.542% | 42.21% | 3.798% | Small Office | 63.6% | 77.07% | 0.1668% | 40.36% |  | 49.43% |  | 34.7% | [7 empty] | 8.542% | 41.95% | 3.798% | Small Office |  |  |  | 48.62% | [12 empty] | 48.62% | 3.798% | Small Office | 63.6% | 77.07% | 0.1668% | 42.22% |  | 49.43% |  | 34.7% | [7 empty] | 8.542% | 42.05% | 3.798%
Medium Office | 55.34% | 79.16% | 4.481% | 70.49% |  | 40.85% |  | 36.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 40.75% | 5.009% | Medium Office | 55.34% | 79.16% | 4.481% | 61.91% |  | 40.85% |  | 36.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.87% | 5.009% | Medium Office | 55.34% | 79.16% |  | 76.89% |  | 40.85% |  | 36.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 41.2% | 5.009% | Medium Office |  |  | 4.481% | 37.91% | [12 empty] | 27.44% | 5.009% | Medium Office | 55.34% | 79.16% | 4.481% | 69.8% |  | 40.85% |  | 36.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 40.69% | 5.009%
Large Office | 49.75% | 65.11% | 3.344% | 84.61% | -608.2% | 43.6% | 45.85% | 17.06% |  | 66.42% |  | 2.834% | 61.95% |  | 0% | 9.145% | 23.51% | 3.855% | Large Office | 49.75% | 65.11% | 3.344% | 84.61% | -608.2% | 43.6% | 45.85% | 17.06% |  | 66.42% |  | 2.834% | 61.95% |  | 0% | 9.145% | 27.91% | 3.855% | Large Office | 49.75% | 65.11% |  |  | -608.2% | 43.6% | 45.85% | 17.06% |  | 66.42% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.21% | 3.855% | Large Office |  |  | 3.344% | 84.61% | [12 empty] | 75% | 3.855% | Large Office | 49.75% | 65.11% | 3.344% | 84.61% | -608.2% | 43.6% | 45.85% | 17.06% |  | 66.42% |  | 2.834% | 61.95% |  | 0% | 9.145% | 23.8% | 3.855%
Standalone Retail | 51.58% | 66.49% | 2.129% | 31.4% |  | 50.85% |  | 68.3% | [7 empty] | 0.4407% | 48.66% | 10.94% | Standalone Retail | 51.58% | 66.49% | 2.129% | 31.4% |  | 50.85% |  | 68.3% | [7 empty] | 0.4407% | 44.83% | 10.94% | Standalone Retail | 51.58% | 66.49% |  |  |  | 50.85% |  | 68.3% | [7 empty] | 0.4407% | 51.01% | 10.94% | Standalone Retail |  |  | 2.129% | 31.4% | [12 empty] | 26.3% | 10.94% | Standalone Retail | 51.58% | 66.49% | 2.129% | 31.4% |  | 50.85% |  | 68.3% | [7 empty] | 0.4407% | 48.39% | 10.94%
Strip Mall | 36.31% | 64.39% | 8.287% | 37.3% |  | 49.81% |  | 61.95% | [7 empty] | 0.4428% | 42.16% | 3.712% | Strip Mall | 36.31% | 64.39% | 8.287% | 37.3% |  | 49.81% |  | 61.95% | [7 empty] | 0.4428% | 41.46% | 3.712% | Strip Mall | 36.31% | 64.39% | 8.287% |  |  | 49.81% |  | 61.95% | [7 empty] | 0.4428% | 42.57% | 3.712% | Strip Mall |  |  |  | 37.3% | [12 empty] | 37.3% | 3.712% | Strip Mall | 36.31% | 64.39% | 8.287% | 37.3% |  | 49.81% |  | 61.95% | [7 empty] | 0.4428% | 42.11% | 3.712%
Primary School | 76.29% | 69.21% | 4.066% | 70.46% |  | 54.21% |  | 50.16% | 54.34% | 55.19% | 46.83% |  | 64.45% | 0% |  | 13.6% | 47.98% | 4.828% | Primary School | 76.29% | 69.21% | 2.534% | 70.46% |  | 54.21% |  | 50.16% | 54.34% | 55.19% | 46.83% |  | 64.45% | 0% |  | 13.6% | 48% | 4.828% | Primary School | 76.29% | 69.21% | 7.672% |  |  | 54.21% |  | 50.16% | 54.34% | 55.19% | 46.83% |  | 64.45% | 0% |  | 13.6% | 47.96% | 4.828% | Primary School |  |  | 1.289% | 70.46% | [9 empty] | 0% |  |  | 48.1% | 4.828% | Primary School | 76.29% | 69.21% | 3.873% | 70.46% |  | 54.21% |  | 50.16% | 54.34% | 55.19% | 46.83% |  | 64.45% | 0% |  | 13.6% | 47.98% | 4.828%
Secondary School | 75.12% | 68.61% | 0.2532% | 68.42% |  | 51.98% |  | 62.06% | 59.16% | 83.52% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 50.79% | 10.92% | Secondary School | 75.12% | 68.61% | 0.343% | 68.42% |  | 51.98% |  | 62.06% | 59.16% | 83.52% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 50.16% | 10.92% | Secondary School | 75.12% | 68.61% | 0.08484% |  |  | 51.98% |  | 62.06% | 59.16% | 83.52% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 51.14% | 10.92% | Secondary School |  |  | 0.4267% | 68.42% | [9 empty] | 0% |  |  | 46.18% | 10.92% | Secondary School | 75.12% | 68.61% | 0.2638% | 68.42% |  | 51.98% |  | 62.06% | 59.16% | 83.52% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 50.74% | 10.92%
Outpatient Healthcare | 37.64% | 75.9% | 11.77% | 68.02% | 21.86% | 35.09% |  | 40.51% |  | 29.41% |  | 1.955% |  |  |  | 0.9089% | 31.35% | 3.419% | Outpatient Healthcare | 37.64% | 75.9% | 11.77% | 57.14% | 21.86% | 35.09% |  | 40.51% |  | 29.41% |  | 1.955% |  |  |  | 0.8245% | 30.49% | 3.419% | Outpatient Healthcare | 37.64% | 75.9% |  | 77.64% | 21.86% | 35.09% |  | 40.51% |  | 29.41% |  | 1.955% |  |  |  | 0.9537% | 31.83% | 3.419% | Outpatient Healthcare |  |  | 11.77% | 34.97% | [11 empty] | 0% | 24.39% | 3.419% | Outpatient Healthcare | 37.64% | 75.9% | 11.77% | 67.07% | 21.86% | 35.09% |  | 40.51% |  | 29.41% |  | 1.955% |  |  |  | 0.9033% | 31.29% | 3.419%
Hospital | 21.64% | 40.71% | 4.314% | 80.34% | 54.94% | 30.68% | 64.06% | 34.89% |  | 69.63% | 47.32% | 1.297% | 59.25% | 0% |  | 3.09% | 30.75% | 4.523% | Hospital | 21.64% | 40.71% | 4.147% | 79.31% | 54.94% | 30.68% | 64.06% | 34.89% |  | 69.63% | 47.32% | 1.297% | 59.25% | 0% |  | 3.09% | 37.71% | 4.523% | Hospital | 21.64% | 40.71% | 7.727% | 86.98% | 54.94% | 30.68% | 64.06% | 34.89% |  | 69.63% | 47.32% | 1.297% | 59.25% | 0% |  | 3.09% | 25.74% | 4.523% | Hospital |  |  | 4.065% | 78.72% | [9 empty] | 0% |  |  | 58.72% | 4.523% | Hospital | 21.64% | 40.71% | 4.287% | 80.18% | 54.94% | 30.68% | 64.06% | 34.89% |  | 69.63% | 47.32% | 1.297% | 59.25% | 0% |  | 3.09% | 31.3% | 4.523%
Small Hotel | 63.01% | 53.49% | 1.761% | 64.84% |  | 38.53% |  | 49.39% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 36.19% | 1.588% | Small Hotel | 63.01% | 53.49% | 1.761% | 64.43% |  | 38.53% |  | 49.39% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 29.73% | 1.588% | Small Hotel | 63.01% | 53.49% |  | 65.13% |  | 38.53% |  | 49.39% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 40.66% | 1.588% | Small Hotel |  |  | 1.761% | 63.1% | [9 empty] | 0% |  |  | 8.097% | 1.588% | Small Hotel | 63.01% | 53.49% | 1.761% | 64.81% |  | 38.53% |  | 49.39% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.69% | 1.588%
Large Hotel | 63.76% | 40.28% | 0.5427% | 89.99% |  | 49.07% |  | 44.14% | 75.24% | 78.17% | 39.94% | 2.834% | 62.43% | 0% |  | 9.05% | 38.86% | 4.219% | Large Hotel | 63.76% | 40.28% | 0.3444% | 89.99% |  | 49.07% |  | 44.14% | 75.24% | 78.17% | 39.94% | 2.834% | 62.43% | 0% |  | 9.05% | 39.09% | 4.219% | Large Hotel | 63.76% | 40.28% | 2.65% |  |  | 49.07% |  | 44.14% | 75.24% | 78.17% | 39.94% | 2.834% | 62.43% | 0% |  | 9.05% | 38.68% | 4.219% | Large Hotel |  |  | 0.2403% | 89.99% | [9 empty] | 0% |  |  | 39.63% | 4.219% | Large Hotel | 63.76% | 40.28% | 0.5113% | 89.99% |  | 49.07% |  | 44.14% | 75.24% | 78.17% | 39.94% | 2.834% | 62.43% | 0% |  | 9.05% | 38.88% | 4.219%
Quick-service Restaurant | 66.26% | 67.89% | -0.06123% | 30.81% |  | 39.89% |  | 60.8% |  |  | 47.76% |  |  | 0.07556% |  |  | 28.45% | 0.3319% | Quick-service Restaurant | 66.26% | 67.89% | -0.06123% | 30.81% |  | 39.89% |  | 60.8% |  |  | 47.76% |  |  | 0.0408% |  |  | 20.93% | 0.3319% | Quick-service Restaurant | 66.26% | 67.89% |  |  |  | 39.89% |  | 60.8% |  |  | 47.76% |  |  | 0.1241% |  |  | 36.17% | 0.3319% | Quick-service Restaurant |  |  | -0.06123% | 30.81% | [9 empty] | 0% |  |  | 8.628% | 0.3319% | Quick-service Restaurant | 66.26% | 67.89% | -0.06123% | 30.81% |  | 39.89% |  | 60.8% |  |  | 47.76% |  |  | 0.07184% |  |  | 27.74% | 0.3319%
Full-service Restaurant | 72.93% | 67.9% | 1.117% | 35.47% |  | 48.98% |  | 68.5% |  | 0% | 49.07% |  |  | 0.09906% |  |  | 35.37% | 0.9718% | Full-service Restaurant | 72.93% | 67.9% | 0.4567% | 35.47% |  | 48.98% |  | 68.5% |  | 0% | 49.07% |  |  | 0.06312% |  |  | 28.45% | 0.9718% | Full-service Restaurant | 72.93% | 67.9% | 2.622% |  |  | 48.98% |  | 68.5% |  | 0% | 49.07% |  |  | 0.1341% |  |  | 41.07% | 0.9718% | Full-service Restaurant |  |  | -0.08898% | 35.47% | [9 empty] | 0% |  |  | 12.58% | 0.9718% | Full-service Restaurant | 72.93% | 67.9% | 1.034% | 35.47% |  | 48.98% |  | 68.5% |  | 0% | 49.07% |  |  | 0.09574% |  |  | 34.78% | 0.9718%
Mid-rise Apartment | 40.18% | 64.43% | 0.2708% | 73.39% |  | 40.95% |  | 21.25% |  |  |  | 3.565% |  |  |  | 0.4999% | 19.74% | 13.69% | Mid-rise Apartment | 40.18% | 64.43% | 0.2708% | 73.39% |  | 40.95% |  | 21.25% |  |  |  | 3.565% |  |  |  | 0.4999% | 27.37% | 13.69% | Mid-rise Apartment | 40.18% | 64.43% | 0.2708% |  |  | 40.95% |  | 21.25% |  |  |  | 3.565% |  |  |  | 0.4999% | 15.32% | 13.69% | Mid-rise Apartment |  |  |  | 73.39% | [12 empty] | 73.39% | 13.69% | Mid-rise Apartment | 40.18% | 64.43% | 0.2708% | 73.39% |  | 40.95% |  | 21.25% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.27% | 13.69%
High-rise Apartment | 38.43% | 44.74% | 0.3594% | 66.5% |  | 29.12% | 63.48% | 19.5% |  | 49.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.33% | 9.636% | High-rise Apartment | 38.43% | 44.74% | 0.3594% | 66.8% |  | 29.12% | 63.48% | 19.5% |  | 49.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 27.23% | 9.636% | High-rise Apartment | 38.43% | 44.74% |  | 65.84% |  | 29.12% | 63.48% | 19.5% |  | 49.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.86% | 9.636% | High-rise Apartment |  |  | 0.3594% | 67.07% | [12 empty] | 32.13% | 9.636% | High-rise Apartment | 38.43% | 44.74% | 0.3594% | 66.53% |  | 29.12% | 63.48% | 19.5% |  | 49.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.48% | 9.636%
Warehouse | 65.11% | 53.96% | 3.111% | 38.43% |  | 48.22% |  | 31.81% | [7 empty] | 1.996% | 46.56% | 18.56% | Warehouse | 65.11% | 53.96% | 3.111% | 38.43% |  | 48.22% |  | 31.81% | [7 empty] | 1.996% | 44.3% | 18.56% | Warehouse | 65.11% | 53.96% | 3.111% |  |  | 48.22% |  | 31.81% | [7 empty] | 1.996% | 48.3% | 18.56% | Warehouse |  |  |  | 38.43% | [12 empty] | 38.43% | 18.56% | Warehouse | 65.11% | 53.96% | 3.111% | 38.43% |  | 48.22% |  | 31.81% | [7 empty] | 1.996% | 46.38% | 18.56%
US Weighted | 54.15% | 60.92% | 2.432% | 58.9% | -20.22% | 44.55% | 10.78% | 39.93% | 12.26% | 26.58% | 11.36% | 2.88% | 26.74% | 0.001213% | 0% | 4.074% | 38.19% | 100% | US Weighted | 54.15% | 60.92% | 2.346% | 58.15% | -20.22% | 44.55% | 10.78% | 39.93% | 12.26% | 26.58% | 11.36% | 2.88% | 26.74% | 0.0007488% | 0% | 4.071% | 38.72% | 100% | US Weighted | 54.15% | 60.92% | 1.795% | 19.35% | -20.22% | 44.55% | 10.78% | 39.93% | 12.26% | 26.58% | 11.36% | 2.88% | 26.74% | 0.001715% | 0% | 4.076% | 37.95% | 100% | US Weighted | 0% | 0% | 1.353% | 56.34% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.46% | 100% | US Weighted | 54.15% | 60.92% | 2.421% | 58.84% | -20.22% | 44.55% | 10.78% | 39.93% | 12.26% | 26.58% | 11.36% | 2.88% | 26.74% | 0.001169% | 0% | 4.074% | 38.23% | 100%

## OffS
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Small Office |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 5502 |  | Building Type: | Small Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Building Type: | Small Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Small Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Small Office | [14 empty] | Prototype Floor Area: | 5502 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.13866 | 0.030618 | 0.096682 | 0.047588 | 0 | 0.11542 | 0 | 0.092015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.78022 |  | STD2019 | 4.4507 | 0.98277 | 3.1033 | 2.1298 | 0 | 3.7048 | 0 | 2.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.6457 |  | STD2019 | 1.3044 | 0.28803 | 0.90952 | 0.36666 | 0 | 1.0858 | 0 | 0.86562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.2588 |  | STD2019 | 0 | 0 | 0 | 0.0087873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0087873 |  | STD2019 | 13.6561 | 3.0154 | 9.5218 | 4.799 | 0 | 11.3675 | 0 | 9.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 76.9527
STD2016 | 0.17233 | 0.030618 | 0.096682 | 0.046613 | 0 | 0.12121 | 0 | 0.10019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.82687 |  | STD2016 | 5.5314 | 0.98277 | 3.1033 | 2.0696 | 0 | 3.8905 | 0 | 3.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.1143 |  | STD2016 | 1.6212 | 0.28803 | 0.90952 | 0.36138 | 0 | 1.1402 | 0 | 0.94252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.7015 |  | STD2016 | 0 | 0 | 0 | 0.0083658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083658 |  | STD2016 | 16.9719 | 3.0154 | 9.5218 | 4.6977 | 0 | 11.9371 | 0 | 9.8673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 81.5419
STD2013 | 0.23769 | 0.063937 | 0.096682 | 0.043604 | 0 | 0.12919 | 0 | 0.10239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.93272 |  | STD2013 | 7.6292 | 2.0522 | 3.1033 | 1.9407 | 0 | 4.1467 | 0 | 3.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.4793 |  | STD2013 | 2.236 | 0.60148 | 0.90952 | 0.33742 | 0 | 1.2153 | 0 | 0.96319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.7016 |  | STD2013 | 0 | 0 | 0 | 0.0078944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078944 |  | STD2013 | 23.4085 | 6.2969 | 9.5218 | 4.3953 | 0 | 12.7232 | 0 | 10.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 91.9601
STD2010 | 0.27955 | 0.063937 | 0.096682 | 0.053116 | 0 | 0.16095 | 0 | 0.12166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.04 |  | STD2010 | 8.9731 | 2.0522 | 3.1033 | 2.3554 | 0 | 5.1663 | 0 | 3.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 34.0311 |  | STD2010 | 2.6299 | 0.60148 | 0.90952 | 0.41219 | 0 | 1.5141 | 0 | 1.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.6958 |  | STD2010 | 0 | 0 | 0 | 0.0094898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0094898 |  | STD2010 | 27.532 | 6.2969 | 9.5218 | 5.3525 | 0 | 15.8516 | 0 | 11.9816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 102.5428
STD2007 | 0.38093 | 0.1335 | 0.096844 | 0.057276 | 0 | 0.18142 | 0 | 0.13528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2687 |  | STD2007 | 12.2271 | 4.2851 | 3.1085 | 2.6555 | 0 | 5.8232 | 0 | 4.3424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.5396 |  | STD2007 | 3.5836 | 1.2559 | 0.91104 | 0.42891 | 0 | 1.7067 | 0 | 1.2727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.8252 |  | STD2007 | 0 | 0 | 0 | 0.011921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011921 |  | STD2007 | 37.5162 | 13.1478 | 9.5377 | 5.7932 | 0 | 17.8671 | 0 | 13.3236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 125.1008
STD2004 | 0.38093 | 0.1335 | 0.096844 | 0.082117 | 0 | 0.22824 | 0 | 0.14092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.346 |  | STD2004 | 12.2271 | 4.2851 | 3.1085 | 3.8082 | 0 | 7.3261 | 0 | 4.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.3761 |  | STD2004 | 3.5836 | 1.2559 | 0.91104 | 0.61482 | 0 | 2.1472 | 0 | 1.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.5046 |  | STD2004 | 0 | 0 | 0 | 0.017104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017104 |  | STD2004 | 37.5162 | 13.1478 | 9.5377 | 8.306 | 0 | 22.4787 | 0 | 13.8786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 132.7801
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 0 | 0.024841 | 0 | 0.046825 | 0 | 0.0056356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077301 |  | 2004-2007 | 0 | 0 | 0 | 1.1526 | 0 | 1.503 | 0 | 0.18089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8365 |  | 2004-2007 | 0 | 0 | 0 | 0.18591 | 0 | 0.44049 | 0 | 0.053016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67942 |  | 2004-2007 | 0 | 0 | 0 | 0.0051831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0051831 |  | 2004-2007 | 0 | 0 | 0 | 2.5128 | 0 | 4.6115 | 0 | 0.55502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6793
2007-2010 | 0.10138 | 0.069563 | 0.00016157 | 0.00416 | 0 | 0.020465 | 0 | 0.013627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019379 | 0.22873 |  | 2007-2010 | 3.254 | 2.2328 | 0.0051861 | 0.30016 | 0 | 0.6569 | 0 | 0.43738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62204 | 7.5085 |  | 2007-2010 | 0.95369 | 0.6544 | 0.0015199 | 0.016722 | 0 | 0.19253 | 0 | 0.12819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18231 | 2.1294 |  | 2007-2010 | 0 | 0 | 0 | 0.002431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002431 |  | 2007-2010 | 9.9842 | 6.8509 | 0.015912 | 0.44078 | 0 | 2.0155 | 0 | 1.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9086 | 22.558
2010-2013 | 0.041869 | 0 | 0 | 0.0095117 | 0 | 0.031765 | 0 | 0.019271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048314 | 0.10725 |  | 2010-2013 | 1.3439 | 0 | 0 | 0.41467 | 0 | 1.0196 | 0 | 0.61856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15508 | 3.5518 |  | 2010-2013 | 0.39388 | 0 | 0 | 0.074771 | 0 | 0.29882 | 0 | 0.18129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045451 | 0.99421 |  | 2010-2013 | 0 | 0 | 0 | 0.0015955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015955 |  | 2010-2013 | 4.1235 | 0 | 0 | 0.95716 | 0 | 3.1284 | 0 | 1.8979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47583 | 10.5828
2013-2016 | 0.065356 | 0.033319 | 0 | -0.0030091 | 0 | 0.0079825 | 0 | 0.002197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10584 |  | 2013-2016 | 2.0978 | 1.0695 | 0 | -0.1289 | 0 | 0.25622 | 0 | 0.070519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3651 |  | 2013-2016 | 0.61482 | 0.31344 | 0 | -0.023961 | 0 | 0.075094 | 0 | 0.020668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0001 |  | 2013-2016 | 0 | 0 | 0 | -0.00047147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00047147 |  | 2013-2016 | 6.4366 | 3.2814 | 0 | -0.30238 | 0 | 0.78616 | 0 | 0.21637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4182
2016-2019 | 0.033669 | 0 | 0 | -0.0009744 | 0 | 0.0057836 | 0 | 0.0081749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046653 |  | 2016-2019 | 1.0807 | 0 | 0 | -0.060163 | 0 | 0.18564 | 0 | 0.2624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4686 |  | 2016-2019 | 0.31673 | 0 | 0 | -0.0052812 | 0 | 0.054408 | 0 | 0.076904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44276 |  | 2016-2019 | 0 | 0 | 0 | -0.00042144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00042144 |  | 2016-2019 | 3.3159 | 0 | 0 | -0.10135 | 0 | 0.5696 | 0 | 0.80511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5892
2004-2019 | 0.24227 | 0.10288 | 0.00016157 | 0.034529 | 0 | 0.11282 | 0 | 0.048905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.56578 |  | 2004-2019 | 7.7764 | 3.3023 | 0.0051861 | 1.6784 | 0 | 3.6213 | 0 | 1.5698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 18.7304 |  | 2004-2019 | 2.2791 | 0.96784 | 0.0015199 | 0.24816 | 0 | 1.0613 | 0 | 0.46007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 5.2458 |  | 2004-2019 | 0 | 0 | 0 | 0.0083167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083167 |  | 2004-2019 | 23.8601 | 10.1324 | 0.015912 | 3.507 | 0 | 11.1112 | 0 | 4.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 55.8274
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0% | 30.25% |  | 20.52% |  | 3.999% | [7 empty] | 0% | 5.743% |  | 2004-2007 | 0% | 0% | 0% | 30.27% |  | 20.52% |  | 3.999% | [7 empty] | 0% | 6.392% |  | 2004-2007 | 0% | 0% | 0% | 30.24% |  | 20.52% |  | 3.999% | [7 empty] | 0% | 5.433% |  | 2004-2007 |  |  |  | 30.3% | [12 empty] | 30.3% |  | 2004-2007 | 0% | 0% | 0% | 30.25% |  | 20.52% |  | 3.999% | [7 empty] | 0% | 5.783%
2007-2010 | 26.61% | 52.11% | 0.1668% | 7.263% |  | 11.28% |  | 10.07% | [7 empty] | 6.837% | 18.03% |  | 2007-2010 | 26.61% | 52.11% | 0.1668% | 11.3% |  | 11.28% |  | 10.07% | [7 empty] | 6.837% | 18.08% |  | 2007-2010 | 26.61% | 52.11% | 0.1668% | 3.899% |  | 11.28% |  | 10.07% | [7 empty] | 6.837% | 18.01% |  | 2007-2010 |  |  |  | 20.39% | [12 empty] | 20.39% |  | 2007-2010 | 26.61% | 52.11% | 0.1668% | 7.608% |  | 11.28% |  | 10.07% | [7 empty] | 6.837% | 18.03%
2010-2013 | 14.98% | 0% | 0% | 17.91% |  | 19.74% |  | 15.84% | [7 empty] | 1.83% | 10.31% |  | 2010-2013 | 14.98% | 0% | 0% | 17.61% |  | 19.74% |  | 15.84% | [7 empty] | 1.83% | 10.44% |  | 2010-2013 | 14.98% | 0% | 0% | 18.14% |  | 19.74% |  | 15.84% | [7 empty] | 1.83% | 10.25% |  | 2010-2013 |  |  |  | 16.81% | [12 empty] | 16.81% |  | 2010-2013 | 14.98% | 0% | 0% | 17.88% |  | 19.74% |  | 15.84% | [7 empty] | 1.83% | 10.32%
2013-2016 | 27.5% | 52.11% | 0% | -6.901% |  | 6.179% |  | 2.146% | [7 empty] | 0% | 11.35% |  | 2013-2016 | 27.5% | 52.11% | 0% | -6.642% |  | 6.179% |  | 2.146% | [7 empty] | 0% | 11.04% |  | 2013-2016 | 27.5% | 52.11% | 0% | -7.101% |  | 6.179% |  | 2.146% | [7 empty] | 0% | 11.49% |  | 2013-2016 |  |  |  | -5.972% | [12 empty] | -5.972% |  | 2013-2016 | 27.5% | 52.11% | 0% | -6.88% |  | 6.179% |  | 2.146% | [7 empty] | 0% | 11.33%
2016-2019 | 19.54% | 0% | 0% | -2.09% |  | 4.772% |  | 8.159% | [7 empty] | 0% | 5.642% |  | 2016-2019 | 19.54% | 0% | 0% | -2.907% |  | 4.772% |  | 8.159% | [7 empty] | 0% | 5.416% |  | 2016-2019 | 19.54% | 0% | 0% | -1.461% |  | 4.772% |  | 8.159% | [7 empty] | 0% | 5.749% |  | 2016-2019 |  |  |  | -5.038% | [12 empty] | -5.038% |  | 2016-2019 | 19.54% | 0% | 0% | -2.157% |  | 4.772% |  | 8.159% | [7 empty] | 0% | 5.628%
2004-2019 | 63.6% | 77.07% | 0.1668% | 42.05% |  | 49.43% |  | 34.7% | [7 empty] | 8.542% | 42.03% |  | 2004-2019 | 63.6% | 77.07% | 0.1668% | 44.07% |  | 49.43% |  | 34.7% | [7 empty] | 8.542% | 42.21% |  | 2004-2019 | 63.6% | 77.07% | 0.1668% | 40.36% |  | 49.43% |  | 34.7% | [7 empty] | 8.542% | 41.95% |  | 2004-2019 |  |  |  | 48.62% | [12 empty] | 48.62% |  | 2004-2019 | 63.6% | 77.07% | 0.1668% | 42.22% |  | 49.43% |  | 34.7% | [7 empty] | 8.542% | 42.05%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.13716 | 0.029848 | 0.096682 | 0 | 0 | 0.35092 | 0 | 0.096897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.97074 | 0% | CZ 0A | 4.4025 | 0.95804 | 3.1033 | 0 | 0 | 11.2639 | 0 | 3.1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 31.1587 | 0% | CZ 0A | 1.2903 | 0.28079 | 0.90952 | 0 | 0 | 3.3013 | 0 | 0.91154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 9.1321 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 13.5082 | 2.9395 | 9.5218 | 0 | 0 | 34.5608 | 0 | 9.5429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 95.604 | 0%
CZ 0B | 0.1378 | 0.030384 | 0.096682 | 0 | 0 | 0.32902 | 0 | 0.1144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.96752 | 0% | CZ 0B | 4.4232 | 0.97527 | 3.1033 | 0 | 0 | 10.5609 | 0 | 3.6719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 31.0553 | 0% | CZ 0B | 1.2964 | 0.28584 | 0.90952 | 0 | 0 | 3.0952 | 0 | 1.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 9.1018 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 13.5716 | 2.9924 | 9.5218 | 0 | 0 | 32.4037 | 0 | 11.2665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 95.2868 | 0%
CZ 1A | 0.13963 | 0.030545 | 0.096682 | 0 | 0 | 0.25129 | 0 | 0.092495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.86987 | 2.924% | CZ 1A | 4.4818 | 0.98044 | 3.1033 | 0 | 0 | 8.0658 | 0 | 2.9689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.921 | 2.924% | CZ 1A | 1.3135 | 0.28735 | 0.90952 | 0 | 0 | 2.364 | 0 | 0.87013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.1832 | 2.924% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.924% | CZ 1A | 13.7514 | 3.0083 | 9.5218 | 0 | 0 | 24.7482 | 0 | 9.1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 85.6698 | 2.924%
CZ 1B | 0.13925 | 0.030438 | 0.096682 | 0.00021473 | 0 | 0.26015 | 0 | 0.10629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.89226 | 0% | CZ 1B | 4.4697 | 0.97699 | 3.1033 | 0.0068924 | 0 | 8.3501 | 0 | 3.4117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.6396 | 0% | CZ 1B | 1.31 | 0.28634 | 0.90952 | 0.00202 | 0 | 2.4473 | 0 | 0.99992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.3938 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 13.7144 | 2.9977 | 9.5218 | 0.021148 | 0 | 25.6206 | 0 | 10.4682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 87.8744 | 0%
CZ 2A | 0.13882 | 0.030545 | 0.096682 | 0.0012884 | 0 | 0.20802 | 0 | 0.095662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.83026 | 20.19% | CZ 2A | 4.4559 | 0.98044 | 3.1033 | 0.041354 | 0 | 6.677 | 0 | 3.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.6494 | 20.19% | CZ 2A | 1.306 | 0.28735 | 0.90952 | 0.01212 | 0 | 1.9569 | 0 | 0.89993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.8105 | 20.19% | CZ 2A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.19% | CZ 2A | 13.6721 | 3.0083 | 9.5218 | 0.12689 | 0 | 20.4869 | 0 | 9.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 81.768 | 20.19%
CZ 2B | 0.14017 | 0.030545 | 0.096682 | 0.0016642 | 0 | 0.18096 | 0 | 0.11241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.82167 | 4.066% | CZ 2B | 4.499 | 0.98044 | 3.1033 | 0.053416 | 0 | 5.8086 | 0 | 3.6082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.3737 | 4.066% | CZ 2B | 1.3186 | 0.28735 | 0.90952 | 0.015655 | 0 | 1.7024 | 0 | 1.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.7297 | 4.066% | CZ 2B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.066% | CZ 2B | 13.8042 | 3.0083 | 9.5218 | 0.1639 | 0 | 17.8223 | 0 | 11.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 80.9221 | 4.066%
CZ 3A | 0.13947 | 0.03076 | 0.096682 | 0.030628 | 0 | 0.11187 | 0 | 0.091153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.7598 | 18.35% | CZ 3A | 4.4766 | 0.98733 | 3.1033 | 1.1579 | 0 | 3.5909 | 0 | 2.9258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 24.5627 | 18.35% | CZ 3A | 1.312 | 0.28937 | 0.90952 | 0.26463 | 0 | 1.0524 | 0 | 0.85751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.1242 | 18.35% | CZ 3A | 0 | 0 | 0 | 0.0025496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025496 | 18.35% | CZ 3A | 13.7355 | 3.0294 | 9.5218 | 3.049 | 0 | 11.018 | 0 | 8.9772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 74.8617 | 18.35%
CZ 3B | 0.13974 | 0.030277 | 0.096682 | 0.011131 | 0 | 0.12428 | 0 | 0.1071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.76843 | 7.24% | CZ 3B | 4.4852 | 0.97183 | 3.1033 | 0.37735 | 0 | 3.989 | 0 | 3.4376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 24.6851 | 7.24% | CZ 3B | 1.3145 | 0.28483 | 0.90952 | 0.10201 | 0 | 1.1691 | 0 | 1.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.2262 | 7.24% | CZ 3B | 0 | 0 | 0 | 0.00029286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00029286 | 7.24% | CZ 3B | 13.7619 | 2.9818 | 9.5218 | 1.1 | 0 | 12.2393 | 0 | 10.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 75.683 | 7.24%
CZ 3C | 0.13952 | 0.030223 | 0.096682 | 0.0015031 | 0 | 0.078162 | 0 | 0.083369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.68869 | 1.232% | CZ 3C | 4.4783 | 0.9701 | 3.1033 | 0.048247 | 0 | 2.5088 | 0 | 2.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 22.1056 | 1.232% | CZ 3C | 1.3125 | 0.28432 | 0.90952 | 0.01414 | 0 | 0.73529 | 0 | 0.78428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.4788 | 1.232% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.232% | CZ 3C | 13.7408 | 2.9766 | 9.5218 | 0.14803 | 0 | 7.6978 | 0 | 8.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 67.8263 | 1.232%
CZ 4A | 0.13791 | 0.030545 | 0.096682 | 0.060117 | 0 | 0.080739 | 0 | 0.083584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.74881 | 15.19% | CZ 4A | 4.4266 | 0.98044 | 3.1033 | 2.2933 | 0 | 2.5915 | 0 | 2.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 24.3989 | 15.19% | CZ 4A | 1.2974 | 0.28735 | 0.90952 | 0.51663 | 0 | 0.75954 | 0 | 0.7863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.9954 | 15.19% | CZ 4A | 0 | 0 | 0 | 0.0053058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0053058 | 15.19% | CZ 4A | 13.5822 | 3.0083 | 9.5218 | 5.9885 | 0 | 7.9516 | 0 | 8.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 73.8148 | 15.19%
CZ 4B | 0.1377 | 0.030331 | 0.096682 | 0.022722 | 0 | 0.092871 | 0 | 0.10468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.74422 | 0.8143% | CZ 4B | 4.4197 | 0.97355 | 3.1033 | 0.77538 | 0 | 2.981 | 0 | 3.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 23.9338 | 0.8143% | CZ 4B | 1.2954 | 0.28533 | 0.90952 | 0.20756 | 0 | 0.87367 | 0 | 0.98477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.9949 | 0.8143% | CZ 4B | 0 | 0 | 0 | 0.00067184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00067184 | 0.8143% | CZ 4B | 13.561 | 2.9871 | 9.5218 | 2.2464 | 0 | 9.1464 | 0 | 10.3096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 73.303 | 0.8143%
CZ 4C | 0.13941 | 0.030975 | 0.096682 | 0.033525 | 0 | 0.038115 | 0 | 0.086805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.68475 | 2.441% | CZ 4C | 4.4749 | 0.99423 | 3.1033 | 1.1493 | 0 | 1.2234 | 0 | 2.7862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 22.0521 | 2.441% | CZ 4C | 1.3115 | 0.29139 | 0.90952 | 0.30553 | 0 | 0.35856 | 0 | 0.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.4318 | 2.441% | CZ 4C | 0 | 0 | 0 | 0.0010681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010681 | 2.441% | CZ 4C | 13.7302 | 3.0506 | 9.5218 | 3.3153 | 0 | 3.7537 | 0 | 8.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 67.4514 | 2.441%
CZ 5A | 0.13775 | 0.03076 | 0.096682 | 0.11337 | 0 | 0.04869 | 0 | 0.083154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.76964 | 17.64% | CZ 5A | 4.4215 | 0.98733 | 3.1033 | 5.1774 | 0 | 1.5628 | 0 | 2.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.2422 | 17.64% | CZ 5A | 1.2959 | 0.28937 | 0.90952 | 0.85953 | 0 | 0.45804 | 0 | 0.78226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.0333 | 17.64% | CZ 5A | 0 | 0 | 0 | 0.022446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022446 | 17.64% | CZ 5A | 13.5663 | 3.0294 | 9.5218 | 11.4518 | 0 | 4.7953 | 0 | 8.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 76.0848 | 17.64%
CZ 5B | 0.13753 | 0.030492 | 0.096682 | 0.061603 | 0 | 0.0656 | 0 | 0.10028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.75142 | 5.428% | CZ 5B | 4.4146 | 0.97872 | 3.1033 | 2.674 | 0 | 2.1056 | 0 | 3.2187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 24.8158 | 5.428% | CZ 5B | 1.2938 | 0.28685 | 0.90952 | 0.48582 | 0 | 0.61712 | 0 | 0.94336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.9752 | 5.428% | CZ 5B | 0 | 0 | 0 | 0.010164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010164 | 5.428% | CZ 5B | 13.5452 | 3.003 | 9.5218 | 6.197 | 0 | 6.4607 | 0 | 9.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 74.1343 | 5.428%
CZ 5C | 0.1385 | 0.031029 | 0.096682 | 0.041337 | 0 | 0.027754 | 0 | 0.082081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.67662 | 0.0594% | CZ 5C | 4.4456 | 0.99595 | 3.1033 | 1.4508 | 0 | 0.89084 | 0 | 2.6346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 21.8419 | 0.0594% | CZ 5C | 1.3029 | 0.2919 | 0.90952 | 0.37219 | 0 | 0.26109 | 0 | 0.77216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.3485 | 0.0594% | CZ 5C | 0 | 0 | 0 | 0.0018088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018088 | 0.0594% | CZ 5C | 13.6403 | 3.0559 | 9.5218 | 4.0942 | 0 | 2.7334 | 0 | 8.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 66.66 | 0.0594%
CZ 6A | 0.13786 | 0.03076 | 0.096682 | 0.1708 | 0 | 0.050193 | 0 | 0.091636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.83716 | 3.429% | CZ 6A | 4.4249 | 0.98733 | 3.1033 | 10.0354 | 0 | 1.6111 | 0 | 2.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 31.4242 | 3.429% | CZ 6A | 1.2969 | 0.28937 | 0.90952 | 0.99437 | 0 | 0.47218 | 0 | 0.86205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.2631 | 3.429% | CZ 6A | 0 | 0 | 0 | 0.066426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066426 | 3.429% | CZ 6A | 13.5769 | 3.0294 | 9.5218 | 17.6704 | 0 | 4.9433 | 0 | 9.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 83.2974 | 3.429%
CZ 6B | 0.13807 | 0.031029 | 0.096682 | 0.10883 | 0 | 0.041228 | 0 | 0.098508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.77358 | 0.5733% | CZ 6B | 4.4318 | 0.99595 | 3.1033 | 6.1264 | 0 | 1.3233 | 0 | 3.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.4635 | 0.5733% | CZ 6B | 1.2989 | 0.2919 | 0.90952 | 0.66964 | 0 | 0.38785 | 0 | 0.92669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.9232 | 0.5733% | CZ 6B | 0 | 0 | 0 | 0.038416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038416 | 0.5733% | CZ 6B | 13.598 | 3.0559 | 9.5218 | 11.2093 | 0 | 4.0604 | 0 | 9.7016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 76.6777 | 0.5733%
CZ 7 | 0.13796 | 0.031029 | 0.096682 | 0.19083 | 0 | 0.038705 | 0 | 0.090079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.84452 | 0.4129% | CZ 7 | 4.4284 | 0.99595 | 3.1033 | 13.0293 | 0 | 1.2424 | 0 | 2.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 34.0115 | 0.4129% | CZ 7 | 1.2979 | 0.2919 | 0.90952 | 0.8666 | 0 | 0.36411 | 0 | 0.84741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.0161 | 0.4129% | CZ 7 | 0 | 0 | 0 | 0.10072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10072 | 0.4129% | CZ 7 | 13.5875 | 3.0559 | 9.5218 | 20.0816 | 0 | 3.8119 | 0 | 8.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 84.4609 | 0.4129%
CZ 8 | 0.14145 | 0.03323 | 0.096682 | 0.24476 | 0 | 0.026466 | 0 | 0.099259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.90109 | 0.02101% | CZ 8 | 4.5404 | 1.0666 | 3.1033 | 19.3136 | 0 | 0.84949 | 0 | 3.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 40.3801 | 0.02101% | CZ 8 | 1.3307 | 0.3126 | 0.90952 | 0.76156 | 0 | 0.24897 | 0 | 0.93376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.9358 | 0.02101% | CZ 8 | 0 | 0 | 0 | 0.16715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16715 | 0.02101% | CZ 8 | 13.9311 | 3.2726 | 9.5218 | 26.2424 | 0 | 2.6065 | 0 | 9.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 90.8807 | 0.02101%
US Weighted | 0.13866 | 0.030618 | 0.096682 | 0.047588 | 0 | 0.11542 | 0 | 0.092015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.78022 | 100% | US Weighted | 4.4507 | 0.98277 | 3.1033 | 2.1298 | 0 | 3.7048 | 0 | 2.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.6457 | 100% | US Weighted | 1.3044 | 0.28803 | 0.90952 | 0.36666 | 0 | 1.0858 | 0 | 0.86562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.2588 | 100% | US Weighted | 0 | 0 | 0 | 0.0087873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0087873 | 100% | US Weighted | 13.6561 | 3.0154 | 9.5218 | 4.799 | 0 | 11.3675 | 0 | 9.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 76.9527 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.17162 | 0.029848 | 0.096682 | 0 | 0 | 0.36048 | 0 | 0.10243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 1.0203 | 0% | CZ 0A | 5.5087 | 0.95804 | 3.1033 | 0 | 0 | 11.5706 | 0 | 3.2877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 32.7491 | 0% | CZ 0A | 1.6145 | 0.28079 | 0.90952 | 0 | 0 | 3.3911 | 0 | 0.96356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 9.5982 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 16.9024 | 2.9395 | 9.5218 | 0 | 0 | 35.5019 | 0 | 10.0875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 100.4838 | 0%
CZ 0B | 0.17216 | 0.030384 | 0.096682 | 0 | 0 | 0.33901 | 0 | 0.12046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 1.0179 | 0% | CZ 0B | 5.526 | 0.97527 | 3.1033 | 0 | 0 | 10.8813 | 0 | 3.8666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 32.6733 | 0% | CZ 0B | 1.6196 | 0.28584 | 0.90952 | 0 | 0 | 3.1891 | 0 | 1.1332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 9.576 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 16.9553 | 2.9924 | 9.5218 | 0 | 0 | 33.3871 | 0 | 11.8639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 100.2512 | 0%
CZ 1A | 0.17297 | 0.030545 | 0.096682 | 0 | 0 | 0.26374 | 0 | 0.10092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.92409 | 2.924% | CZ 1A | 5.5518 | 0.98044 | 3.1033 | 0 | 0 | 8.4656 | 0 | 3.2394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.6614 | 2.924% | CZ 1A | 1.6271 | 0.28735 | 0.90952 | 0 | 0 | 2.4811 | 0 | 0.94942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.6932 | 2.924% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.924% | CZ 1A | 17.0346 | 3.0083 | 9.5218 | 0 | 0 | 25.9748 | 0 | 9.9395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 91.0096 | 2.924%
CZ 1B | 0.17237 | 0.030438 | 0.096682 | 0.00021473 | 0 | 0.27383 | 0 | 0.11563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.94841 | 0% | CZ 1B | 5.5329 | 0.97699 | 3.1033 | 0.0068924 | 0 | 8.7895 | 0 | 3.7115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.4419 | 0% | CZ 1B | 1.6216 | 0.28634 | 0.90952 | 0.00202 | 0 | 2.5761 | 0 | 1.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.922 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 16.9764 | 2.9977 | 9.5218 | 0.021148 | 0 | 26.9687 | 0 | 11.3881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 93.4046 | 0%
CZ 2A | 0.17286 | 0.030545 | 0.096682 | 0.0013421 | 0 | 0.21607 | 0 | 0.10398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.88072 | 20.19% | CZ 2A | 5.5484 | 0.98044 | 3.1033 | 0.043077 | 0 | 6.9355 | 0 | 3.3376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.2691 | 20.19% | CZ 2A | 1.6261 | 0.28735 | 0.90952 | 0.012625 | 0 | 2.0327 | 0 | 0.9782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.2852 | 20.19% | CZ 2A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.19% | CZ 2A | 17.024 | 3.0083 | 9.5218 | 0.13217 | 0 | 21.28 | 0 | 10.2408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 86.7377 | 20.19%
CZ 2B | 0.17458 | 0.030545 | 0.096682 | 0.0017715 | 0 | 0.18912 | 0 | 0.12186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.87379 | 4.066% | CZ 2B | 5.6035 | 0.98044 | 3.1033 | 0.056862 | 0 | 6.0705 | 0 | 3.9114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.0468 | 4.066% | CZ 2B | 1.6423 | 0.28735 | 0.90952 | 0.016665 | 0 | 1.7792 | 0 | 1.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.2201 | 4.066% | CZ 2B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.066% | CZ 2B | 17.1932 | 3.0083 | 9.5218 | 0.17447 | 0 | 18.6259 | 0 | 12.0014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 86.0557 | 4.066%
CZ 3A | 0.17361 | 0.03076 | 0.096682 | 0.029939 | 0 | 0.11767 | 0 | 0.099044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.80694 | 18.35% | CZ 3A | 5.5725 | 0.98733 | 3.1033 | 1.1251 | 0 | 3.777 | 0 | 3.1791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.0652 | 18.35% | CZ 3A | 1.6332 | 0.28937 | 0.90952 | 0.25958 | 0 | 1.107 | 0 | 0.93174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.5691 | 18.35% | CZ 3A | 0 | 0 | 0 | 0.0023945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023945 | 18.35% | CZ 3A | 17.098 | 3.0294 | 9.5218 | 2.9792 | 0 | 11.589 | 0 | 9.7544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 79.5026 | 18.35%
CZ 3B | 0.17393 | 0.030277 | 0.096682 | 0.010721 | 0 | 0.13099 | 0 | 0.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.81773 | 7.24% | CZ 3B | 5.5828 | 0.97183 | 3.1033 | 0.36184 | 0 | 4.2044 | 0 | 3.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.2651 | 7.24% | CZ 3B | 1.6362 | 0.28483 | 0.90952 | 0.098477 | 0 | 1.2322 | 0 | 1.0903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.6903 | 7.24% | CZ 3B | 0 | 0 | 0 | 0.0002584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002584 | 7.24% | CZ 3B | 17.1297 | 2.9818 | 9.5218 | 1.0592 | 0 | 12.9002 | 0 | 11.4145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 80.538 | 7.24%
CZ 3C | 0.17372 | 0.030223 | 0.096682 | 0.0013957 | 0 | 0.084496 | 0 | 0.091421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.73717 | 1.232% | CZ 3C | 5.5759 | 0.9701 | 3.1033 | 0.0448 | 0 | 2.7122 | 0 | 2.9344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 23.6615 | 1.232% | CZ 3C | 1.6342 | 0.28432 | 0.90952 | 0.01313 | 0 | 0.79489 | 0 | 0.86003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.9348 | 1.232% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.232% | CZ 3C | 17.1086 | 2.9766 | 9.5218 | 0.13746 | 0 | 8.3217 | 0 | 9.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 72.6004 | 1.232%
CZ 4A | 0.17109 | 0.030545 | 0.096682 | 0.058367 | 0 | 0.085033 | 0 | 0.090938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.79189 | 15.19% | CZ 4A | 5.4915 | 0.98044 | 3.1033 | 2.2123 | 0 | 2.7294 | 0 | 2.9189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.7567 | 15.19% | CZ 4A | 1.6095 | 0.28735 | 0.90952 | 0.5035 | 0 | 0.79994 | 0 | 0.85549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.404 | 15.19% | CZ 4A | 0 | 0 | 0 | 0.0049441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049441 | 15.19% | CZ 4A | 16.8495 | 3.0083 | 9.5218 | 5.8115 | 0 | 8.3745 | 0 | 8.9561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 78.0524 | 15.19%
CZ 4B | 0.17093 | 0.030331 | 0.096682 | 0.021815 | 0 | 0.098508 | 0 | 0.11375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.79125 | 0.8143% | CZ 4B | 5.4863 | 0.97355 | 3.1033 | 0.73919 | 0 | 3.1619 | 0 | 3.6512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 25.4363 | 0.8143% | CZ 4B | 1.608 | 0.28533 | 0.90952 | 0.19998 | 0 | 0.92669 | 0 | 1.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.4383 | 0.8143% | CZ 4B | 0 | 0 | 0 | 0.00056848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00056848 | 0.8143% | CZ 4B | 16.8337 | 2.9871 | 9.5218 | 2.1558 | 0 | 9.7016 | 0 | 11.2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 77.9337 | 0.8143%
CZ 4C | 0.17323 | 0.030975 | 0.096682 | 0.031494 | 0 | 0.041604 | 0 | 0.094965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.72819 | 2.441% | CZ 4C | 5.5604 | 0.99423 | 3.1033 | 1.0735 | 0 | 1.3354 | 0 | 3.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 23.4358 | 2.441% | CZ 4C | 1.6297 | 0.29139 | 0.90952 | 0.28786 | 0 | 0.39138 | 0 | 0.89336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.8419 | 2.441% | CZ 4C | 0 | 0 | 0 | 0.00091302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00091302 | 2.441% | CZ 4C | 17.061 | 3.0506 | 9.5218 | 3.1134 | 0 | 4.0974 | 0 | 9.3526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 71.7274 | 2.441%
CZ 5A | 0.17109 | 0.03076 | 0.096682 | 0.11175 | 0 | 0.052018 | 0 | 0.090777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.81231 | 17.64% | CZ 5A | 5.4915 | 0.98733 | 3.1033 | 5.043 | 0 | 1.6697 | 0 | 2.9138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.5294 | 17.64% | CZ 5A | 1.6095 | 0.28937 | 0.90952 | 0.85549 | 0 | 0.48935 | 0 | 0.85397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.4459 | 17.64% | CZ 5A | 0 | 0 | 0 | 0.021241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021241 | 17.64% | CZ 5A | 16.8495 | 3.0294 | 9.5218 | 11.2777 | 0 | 5.1231 | 0 | 8.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 80.2724 | 17.64%
CZ 5B | 0.17039 | 0.030492 | 0.096682 | 0.060009 | 0 | 0.070109 | 0 | 0.10957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.79648 | 5.428% | CZ 5B | 5.4691 | 0.97872 | 3.1033 | 2.5827 | 0 | 2.2504 | 0 | 3.5168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.2218 | 5.428% | CZ 5B | 1.6029 | 0.28685 | 0.90952 | 0.47622 | 0 | 0.65954 | 0 | 1.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.4045 | 5.428% | CZ 5B | 0 | 0 | 0 | 0.0095781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0095781 | 5.428% | CZ 5B | 16.7808 | 3.003 | 9.5218 | 6.0325 | 0 | 6.9048 | 0 | 10.7907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 78.5642 | 5.428%
CZ 5C | 0.17189 | 0.031029 | 0.096682 | 0.03903 | 0 | 0.030653 | 0 | 0.090079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.7186 | 0.0594% | CZ 5C | 5.5174 | 0.99595 | 3.1033 | 1.3543 | 0 | 0.98389 | 0 | 2.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 23.167 | 0.0594% | CZ 5C | 1.617 | 0.2919 | 0.90952 | 0.35351 | 0 | 0.28836 | 0 | 0.84741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 6.7464 | 0.0594% | CZ 5C | 0 | 0 | 0 | 0.0014815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014815 | 0.0594% | CZ 5C | 16.9288 | 3.0559 | 9.5218 | 3.8628 | 0 | 3.0189 | 0 | 8.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 70.7903 | 0.0594%
CZ 6A | 0.1705 | 0.03076 | 0.096682 | 0.16781 | 0 | 0.054971 | 0 | 0.10098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.88093 | 3.429% | CZ 6A | 5.4726 | 0.98733 | 3.1033 | 9.8097 | 0 | 1.7644 | 0 | 3.2411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 32.6993 | 3.429% | CZ 6A | 1.6039 | 0.28937 | 0.90952 | 0.98376 | 0 | 0.51713 | 0 | 0.94992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.6923 | 3.429% | CZ 6A | 0 | 0 | 0 | 0.064531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064531 | 3.429% | CZ 6A | 16.7914 | 3.0294 | 9.5218 | 17.3523 | 0 | 5.4138 | 0 | 9.9448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 87.5842 | 3.429%
CZ 6B | 0.17076 | 0.031029 | 0.096682 | 0.10487 | 0 | 0.046006 | 0 | 0.10914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.81772 | 0.5733% | CZ 6B | 5.4812 | 0.99595 | 3.1033 | 5.8835 | 0 | 1.4767 | 0 | 3.5031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.7645 | 0.5733% | CZ 6B | 1.6064 | 0.2919 | 0.90952 | 0.64793 | 0 | 0.43279 | 0 | 1.0267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.354 | 0.5733% | CZ 6B | 0 | 0 | 0 | 0.036727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036727 | 0.5733% | CZ 6B | 16.8178 | 3.0559 | 9.5218 | 10.7975 | 0 | 4.5309 | 0 | 10.7484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 81.0029 | 0.5733%
CZ 7 | 0.16991 | 0.031029 | 0.096682 | 0.18791 | 0 | 0.044825 | 0 | 0.10286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.89244 | 0.4129% | CZ 7 | 5.4536 | 0.99595 | 3.1033 | 12.7503 | 0 | 1.4388 | 0 | 3.3015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 35.3642 | 0.4129% | CZ 7 | 1.5984 | 0.2919 | 0.90952 | 0.86407 | 0 | 0.42168 | 0 | 0.9676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.4918 | 0.4129% | CZ 7 | 0 | 0 | 0 | 0.09802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09802 | 0.4129% | CZ 7 | 16.7332 | 3.0559 | 9.5218 | 19.7596 | 0 | 4.4146 | 0 | 10.1298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 89.1456 | 0.4129%
CZ 8 | 0.17404 | 0.03323 | 0.096682 | 0.24322 | 0 | 0.031887 | 0 | 0.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.95049 | 0.02101% | CZ 8 | 5.5863 | 1.0666 | 3.1033 | 19.1224 | 0 | 1.0235 | 0 | 3.6013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 41.8241 | 0.02101% | CZ 8 | 1.6372 | 0.3126 | 0.90952 | 0.7661 | 0 | 0.29998 | 0 | 1.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.4196 | 0.02101% | CZ 8 | 0 | 0 | 0 | 0.16508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16508 | 0.02101% | CZ 8 | 17.1403 | 3.2726 | 9.5218 | 26.064 | 0 | 3.1404 | 0 | 11.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 95.7196 | 0.02101%
US Weighted | 0.17233 | 0.030618 | 0.096682 | 0.046613 | 0 | 0.12121 | 0 | 0.10019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.82687 | 100% | US Weighted | 5.5314 | 0.98277 | 3.1033 | 2.0696 | 0 | 3.8905 | 0 | 3.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.1143 | 100% | US Weighted | 1.6212 | 0.28803 | 0.90952 | 0.36138 | 0 | 1.1402 | 0 | 0.94252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.7015 | 100% | US Weighted | 0 | 0 | 0 | 0.0083658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083658 | 100% | US Weighted | 16.9719 | 3.0154 | 9.5218 | 4.6977 | 0 | 11.9371 | 0 | 9.8673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 81.5419 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.23497 | 0.06399 | 0.096682 | 0 | 0 | 0.37771 | 0 | 0.10688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 1.1395 | 0% | CZ 0A | 7.542 | 2.0539 | 3.1033 | 0 | 0 | 12.1237 | 0 | 3.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 36.5744 | 0% | CZ 0A | 2.2104 | 0.60197 | 0.90952 | 0 | 0 | 3.5533 | 0 | 1.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 10.7193 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 23.141 | 6.302 | 9.5218 | 0 | 0 | 37.199 | 0 | 10.5263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 112.2209 | 0%
CZ 0B | 0.23583 | 0.06399 | 0.096682 | 0 | 0 | 0.35833 | 0 | 0.1261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 1.1402 | 0% | CZ 0B | 7.5696 | 2.0539 | 3.1033 | 0 | 0 | 11.5017 | 0 | 4.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 36.5968 | 0% | CZ 0B | 2.2185 | 0.60197 | 0.90952 | 0 | 0 | 3.3709 | 0 | 1.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 10.7259 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 23.2256 | 6.302 | 9.5218 | 0 | 0 | 35.2904 | 0 | 12.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 112.2896 | 0%
CZ 1A | 0.23883 | 0.06399 | 0.096682 | 0 | 0 | 0.27426 | 0 | 0.10216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 1.0352 | 2.924% | CZ 1A | 7.6661 | 2.0539 | 3.1033 | 0 | 0 | 8.8033 | 0 | 3.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 33.2264 | 2.924% | CZ 1A | 2.2468 | 0.60197 | 0.90952 | 0 | 0 | 2.5801 | 0 | 0.96103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 9.7381 | 2.924% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.924% | CZ 1A | 23.5217 | 6.302 | 9.5218 | 0 | 0 | 27.011 | 0 | 10.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 101.9483 | 2.924%
CZ 1B | 0.23819 | 0.063882 | 0.096682 | 0.00010737 | 0 | 0.28607 | 0 | 0.11762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 1.0618 | 0% | CZ 1B | 7.6454 | 2.0505 | 3.1033 | 0.0034462 | 0 | 9.1824 | 0 | 3.7753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 34.0811 | 0% | CZ 1B | 2.2407 | 0.60096 | 0.90952 | 0.00101 | 0 | 2.6912 | 0 | 1.1065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 9.9886 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 23.4582 | 6.2915 | 9.5218 | 0.010574 | 0 | 28.1742 | 0 | 11.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 104.5706 | 0%
CZ 2A | 0.23873 | 0.063882 | 0.096682 | 0.001181 | 0 | 0.22633 | 0 | 0.10554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.99157 | 20.19% | CZ 2A | 7.6626 | 2.0505 | 3.1033 | 0.037908 | 0 | 7.2646 | 0 | 3.3876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 31.8273 | 20.19% | CZ 2A | 2.2458 | 0.60096 | 0.90952 | 0.01111 | 0 | 2.1291 | 0 | 0.99285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 9.328 | 20.19% | CZ 2A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.19% | CZ 2A | 23.5111 | 6.2915 | 9.5218 | 0.11631 | 0 | 22.2898 | 0 | 10.3941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 97.6553 | 20.19%
CZ 2B | 0.24071 | 0.063936 | 0.096682 | 0.0014494 | 0 | 0.19943 | 0 | 0.12411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.98556 | 4.066% | CZ 2B | 7.7264 | 2.0522 | 3.1033 | 0.046524 | 0 | 6.4013 | 0 | 3.9838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 31.6343 | 4.066% | CZ 2B | 2.2645 | 0.60147 | 0.90952 | 0.013635 | 0 | 1.8761 | 0 | 1.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 9.2715 | 4.066% | CZ 2B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.066% | CZ 2B | 23.7067 | 6.2968 | 9.5218 | 0.14275 | 0 | 19.641 | 0 | 12.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 97.0632 | 4.066%
CZ 3A | 0.23964 | 0.063882 | 0.096682 | 0.027717 | 0 | 0.1247 | 0 | 0.1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.91246 | 18.35% | CZ 3A | 7.6919 | 2.0505 | 3.1033 | 1.0373 | 0 | 4.0028 | 0 | 3.2291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.4356 | 18.35% | CZ 3A | 2.2544 | 0.60096 | 0.90952 | 0.24089 | 0 | 1.1731 | 0 | 0.94639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.564 | 18.35% | CZ 3A | 0 | 0 | 0 | 0.0021533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021533 | 18.35% | CZ 3A | 23.601 | 6.2915 | 9.5218 | 2.7572 | 0 | 12.2816 | 0 | 9.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 89.8915 | 18.35%
CZ 3B | 0.24001 | 0.063882 | 0.096682 | 0.0097581 | 0 | 0.13861 | 0 | 0.1181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.92628 | 7.24% | CZ 3B | 7.704 | 2.0505 | 3.1033 | 0.32738 | 0 | 4.449 | 0 | 3.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.7458 | 7.24% | CZ 3B | 2.2579 | 0.60096 | 0.90952 | 0.089892 | 0 | 1.3039 | 0 | 1.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.7119 | 7.24% | CZ 3B | 0 | 0 | 0 | 0.00020672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00020672 | 7.24% | CZ 3B | 23.638 | 6.2915 | 9.5218 | 0.96367 | 0 | 13.6509 | 0 | 11.6313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 91.2278 | 7.24%
CZ 3C | 0.23964 | 0.06399 | 0.096682 | 0.00102 | 0 | 0.092012 | 0 | 0.092764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.84534 | 1.232% | CZ 3C | 7.6919 | 2.0539 | 3.1033 | 0.032739 | 0 | 2.9534 | 0 | 2.9775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 27.1336 | 1.232% | CZ 3C | 2.2544 | 0.60197 | 0.90952 | 0.0095952 | 0 | 0.86559 | 0 | 0.87266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.9524 | 1.232% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.232% | CZ 3C | 23.601 | 6.302 | 9.5218 | 0.10045 | 0 | 9.0618 | 0 | 9.1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 83.2536 | 1.232%
CZ 4A | 0.23534 | 0.064043 | 0.096682 | 0.052134 | 0 | 0.093891 | 0 | 0.094481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.89581 | 15.19% | CZ 4A | 7.554 | 2.0557 | 3.1033 | 1.9556 | 0 | 3.0137 | 0 | 3.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.0358 | 15.19% | CZ 4A | 2.214 | 0.60248 | 0.90952 | 0.45249 | 0 | 0.88326 | 0 | 0.88882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.3892 | 15.19% | CZ 4A | 0 | 0 | 0 | 0.0041172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041172 | 15.19% | CZ 4A | 23.178 | 6.3073 | 9.5218 | 5.1871 | 0 | 9.2469 | 0 | 9.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 88.2769 | 15.19%
CZ 4B | 0.23508 | 0.063882 | 0.096682 | 0.018412 | 0 | 0.1108 | 0 | 0.11842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.90251 | 0.8143% | CZ 4B | 7.5454 | 2.0505 | 3.1033 | 0.61341 | 0 | 3.5565 | 0 | 3.8011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 28.9911 | 0.8143% | CZ 4B | 2.2114 | 0.60096 | 0.90952 | 0.17019 | 0 | 1.0423 | 0 | 1.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.4872 | 0.8143% | CZ 4B | 0 | 0 | 0 | 0.00032731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00032731 | 0.8143% | CZ 4B | 23.1516 | 6.2915 | 9.5218 | 1.8175 | 0 | 10.9123 | 0 | 11.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 88.8883 | 0.8143%
CZ 4C | 0.23776 | 0.064043 | 0.096682 | 0.026429 | 0 | 0.049656 | 0 | 0.09985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.83365 | 2.441% | CZ 4C | 7.6316 | 2.0557 | 3.1033 | 0.89083 | 0 | 1.5939 | 0 | 3.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.801 | 2.441% | CZ 4C | 2.2367 | 0.60248 | 0.90952 | 0.24291 | 0 | 0.46713 | 0 | 0.93932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.8367 | 2.441% | CZ 4C | 0 | 0 | 0 | 0.00062016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00062016 | 2.441% | CZ 4C | 23.4159 | 6.3073 | 9.5218 | 2.6108 | 0 | 4.8904 | 0 | 9.8337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 82.1107 | 2.441%
CZ 5A | 0.23583 | 0.063936 | 0.096682 | 0.10586 | 0 | 0.05787 | 0 | 0.092925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.91234 | 17.64% | CZ 5A | 7.5696 | 2.0522 | 3.1033 | 4.7535 | 0 | 1.8575 | 0 | 2.9827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.6396 | 17.64% | CZ 5A | 2.2185 | 0.60147 | 0.90952 | 0.81357 | 0 | 0.5444 | 0 | 0.87417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.4003 | 17.64% | CZ 5A | 0 | 0 | 0 | 0.019776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019776 | 17.64% | CZ 5A | 23.2256 | 6.2968 | 9.5218 | 10.6788 | 0 | 5.6993 | 0 | 9.1517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 90.1047 | 17.64%
CZ 5B | 0.23524 | 0.06399 | 0.096682 | 0.054676 | 0 | 0.077571 | 0 | 0.11247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.89985 | 5.428% | CZ 5B | 7.5506 | 2.0539 | 3.1033 | 2.3501 | 0 | 2.4899 | 0 | 3.6099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 29.4785 | 5.428% | CZ 5B | 2.213 | 0.60197 | 0.90952 | 0.43431 | 0 | 0.72974 | 0 | 1.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.3852 | 5.428% | CZ 5B | 0 | 0 | 0 | 0.0086823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086823 | 5.428% | CZ 5B | 23.1674 | 6.302 | 9.5218 | 5.4958 | 0 | 7.6396 | 0 | 11.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 88.7335 | 5.428%
CZ 5C | 0.23685 | 0.06399 | 0.096682 | 0.0339 | 0 | 0.036182 | 0 | 0.092871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.81971 | 0.0594% | CZ 5C | 7.6023 | 2.0539 | 3.1033 | 1.1613 | 0 | 1.1614 | 0 | 2.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 26.384 | 0.0594% | CZ 5C | 2.2281 | 0.60197 | 0.90952 | 0.30907 | 0 | 0.34038 | 0 | 0.87367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 7.7014 | 0.0594% | CZ 5C | 0 | 0 | 0 | 0.0010681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010681 | 0.0594% | CZ 5C | 23.326 | 6.302 | 9.5218 | 3.3524 | 0 | 3.5634 | 0 | 9.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 80.7428 | 0.0594%
CZ 6A | 0.23583 | 0.06399 | 0.096682 | 0.16672 | 0 | 0.05889 | 0 | 0.10232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.98366 | 3.429% | CZ 6A | 7.5696 | 2.0539 | 3.1033 | 9.8028 | 0 | 1.8902 | 0 | 3.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 36.0249 | 3.429% | CZ 6A | 2.2185 | 0.60197 | 0.90952 | 0.96962 | 0 | 0.554 | 0 | 0.96255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.6549 | 3.429% | CZ 6A | 0 | 0 | 0 | 0.064945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064945 | 3.429% | CZ 6A | 23.2256 | 6.302 | 9.5218 | 17.2494 | 0 | 5.7998 | 0 | 10.0769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 97.7063 | 3.429%
CZ 6B | 0.23615 | 0.063882 | 0.096682 | 0.10314 | 0 | 0.049388 | 0 | 0.11064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.91911 | 0.5733% | CZ 6B | 7.5799 | 2.0505 | 3.1033 | 5.8421 | 0 | 1.5852 | 0 | 3.5513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 32.0332 | 0.5733% | CZ 6B | 2.2215 | 0.60096 | 0.90952 | 0.62975 | 0 | 0.46461 | 0 | 1.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.3059 | 0.5733% | CZ 6B | 0 | 0 | 0 | 0.036934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036934 | 0.5733% | CZ 6B | 23.2573 | 6.2915 | 9.5218 | 10.6297 | 0 | 4.864 | 0 | 10.8964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 90.9914 | 0.5733%
CZ 7 | 0.23524 | 0.06399 | 0.096682 | 0.18635 | 0 | 0.048368 | 0 | 0.10409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.99395 | 0.4129% | CZ 7 | 7.5506 | 2.0539 | 3.1033 | 12.7227 | 0 | 1.5525 | 0 | 3.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 38.6449 | 0.4129% | CZ 7 | 2.213 | 0.60197 | 0.90952 | 0.8464 | 0 | 0.45501 | 0 | 0.97921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.4438 | 0.4129% | CZ 7 | 0 | 0 | 0 | 0.098348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.098348 | 0.4129% | CZ 7 | 23.1674 | 6.302 | 9.5218 | 19.6103 | 0 | 4.7635 | 0 | 10.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 99.1473 | 0.4129%
CZ 8 | 0.23996 | 0.064419 | 0.096682 | 0.25236 | 0 | 0.033981 | 0 | 0.11504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 1.0617 | 0.02101% | CZ 8 | 7.7022 | 2.0677 | 3.1033 | 19.9424 | 0 | 1.0907 | 0 | 3.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 45.9197 | 0.02101% | CZ 8 | 2.2574 | 0.60601 | 0.90952 | 0.78125 | 0 | 0.31967 | 0 | 1.0822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.3948 | 0.02101% | CZ 8 | 0 | 0 | 0 | 0.17277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17277 | 0.02101% | CZ 8 | 23.6327 | 6.3443 | 9.5218 | 27.0624 | 0 | 3.3466 | 0 | 11.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 106.7685 | 0.02101%
US Weighted | 0.23769 | 0.063937 | 0.096682 | 0.043604 | 0 | 0.12919 | 0 | 0.10239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25923 | 0.93272 | 100% | US Weighted | 7.6292 | 2.0522 | 3.1033 | 1.9407 | 0 | 4.1467 | 0 | 3.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3208 | 30.4793 | 100% | US Weighted | 2.236 | 0.60148 | 0.90952 | 0.33742 | 0 | 1.2153 | 0 | 0.96319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4387 | 8.7016 | 100% | US Weighted | 0 | 0 | 0 | 0.0078944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078944 | 100% | US Weighted | 23.4085 | 6.2969 | 9.5218 | 4.3953 | 0 | 12.7232 | 0 | 10.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5307 | 91.9601 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.27738 | 0.06399 | 0.096682 | 0 | 0 | 0.52346 | 0 | 0.16287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.3884 | 0% | CZ 0A | 8.9032 | 2.0539 | 3.1033 | 0 | 0 | 16.8019 | 0 | 5.2279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 44.5661 | 0% | CZ 0A | 2.6094 | 0.60197 | 0.90952 | 0 | 0 | 4.9244 | 0 | 1.5322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 13.0616 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 27.3177 | 6.302 | 9.5218 | 0 | 0 | 51.5531 | 0 | 16.0406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 136.7417 | 0%
CZ 0B | 0.27802 | 0.06399 | 0.096682 | 0 | 0 | 0.41379 | 0 | 0.14811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.2647 | 0% | CZ 0B | 8.9239 | 2.0539 | 3.1033 | 0 | 0 | 13.2816 | 0 | 4.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 40.5927 | 0% | CZ 0B | 2.6154 | 0.60197 | 0.90952 | 0 | 0 | 3.8926 | 0 | 1.3933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 11.897 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 27.3811 | 6.302 | 9.5218 | 0 | 0 | 40.7518 | 0 | 14.5867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 124.55 | 0%
CZ 1A | 0.27995 | 0.06399 | 0.096682 | 0 | 0 | 0.3739 | 0 | 0.14757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.2262 | 2.924% | CZ 1A | 8.9859 | 2.0539 | 3.1033 | 0 | 0 | 12.0014 | 0 | 4.7368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 39.3572 | 2.924% | CZ 1A | 2.6336 | 0.60197 | 0.90952 | 0 | 0 | 3.5174 | 0 | 1.3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 11.5349 | 2.924% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.924% | CZ 1A | 27.5715 | 6.302 | 9.5218 | 0 | 0 | 36.8236 | 0 | 14.5338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 120.7593 | 2.924%
CZ 1B | 0.27953 | 0.063882 | 0.096682 | 0.0003221 | 0 | 0.32945 | 0 | 0.13818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.1721 | 0% | CZ 1B | 8.9722 | 2.0505 | 3.1033 | 0.010339 | 0 | 10.5746 | 0 | 4.4352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 37.6221 | 0% | CZ 1B | 2.6296 | 0.60096 | 0.90952 | 0.0030301 | 0 | 3.0992 | 0 | 1.2999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 11.0264 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 27.5292 | 6.2915 | 9.5218 | 0.031722 | 0 | 32.446 | 0 | 13.6086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 115.4353 | 0%
CZ 2A | 0.2799 | 0.063882 | 0.096682 | 0.0021473 | 0 | 0.30009 | 0 | 0.14059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.1474 | 20.19% | CZ 2A | 8.9842 | 2.0505 | 3.1033 | 0.068924 | 0 | 9.6321 | 0 | 4.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 36.8277 | 20.19% | CZ 2A | 2.6331 | 0.60096 | 0.90952 | 0.0202 | 0 | 2.823 | 0 | 1.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 10.7936 | 20.19% | CZ 2A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.19% | CZ 2A | 27.5662 | 6.2915 | 9.5218 | 0.21148 | 0 | 29.5541 | 0 | 13.8465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 112.998 | 20.19%
CZ 2B | 0.28119 | 0.063936 | 0.096682 | 0.0021473 | 0 | 0.22794 | 0 | 0.14151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.0775 | 4.066% | CZ 2B | 9.0256 | 2.0522 | 3.1033 | 0.068924 | 0 | 7.3163 | 0 | 4.5421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 34.5842 | 4.066% | CZ 2B | 2.6452 | 0.60147 | 0.90952 | 0.0202 | 0 | 2.1443 | 0 | 1.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 10.1361 | 4.066% | CZ 2B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.066% | CZ 2B | 27.6931 | 6.2968 | 9.5218 | 0.21148 | 0 | 22.4484 | 0 | 13.9364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 106.1144 | 4.066%
CZ 3A | 0.28071 | 0.063882 | 0.096682 | 0.031285 | 0 | 0.16266 | 0 | 0.12154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.0208 | 18.35% | CZ 3A | 9.0101 | 2.0505 | 3.1033 | 1.1648 | 0 | 5.221 | 0 | 3.9011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.9266 | 18.35% | CZ 3A | 2.6407 | 0.60096 | 0.90952 | 0.27271 | 0 | 1.5302 | 0 | 1.1433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.5816 | 18.35% | CZ 3A | 0 | 0 | 0 | 0.0023428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023428 | 18.35% | CZ 3A | 27.6455 | 6.2915 | 9.5218 | 3.111 | 0 | 16.0195 | 0 | 11.9697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 100.5654 | 18.35%
CZ 3B | 0.28097 | 0.063882 | 0.096682 | 0.011241 | 0 | 0.15504 | 0 | 0.12836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.0002 | 7.24% | CZ 3B | 9.0187 | 2.0505 | 3.1033 | 0.37735 | 0 | 4.9763 | 0 | 4.1199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.1219 | 7.24% | CZ 3B | 2.6432 | 0.60096 | 0.90952 | 0.10353 | 0 | 1.4585 | 0 | 1.2075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.4073 | 7.24% | CZ 3B | 0 | 0 | 0 | 0.00024117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00024117 | 7.24% | CZ 3B | 27.6719 | 6.2915 | 9.5218 | 1.1102 | 0 | 15.2687 | 0 | 12.6411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 98.5117 | 7.24%
CZ 3C | 0.28103 | 0.06399 | 0.096682 | 0.0012884 | 0 | 0.11069 | 0 | 0.10457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 0.92232 | 1.232% | CZ 3C | 9.0204 | 2.0539 | 3.1033 | 0.041354 | 0 | 3.553 | 0 | 3.3566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 29.6045 | 1.232% | CZ 3C | 2.6437 | 0.60197 | 0.90952 | 0.01212 | 0 | 1.0413 | 0 | 0.98376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 8.6766 | 1.232% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.232% | CZ 3C | 27.6772 | 6.302 | 9.5218 | 0.12689 | 0 | 10.9017 | 0 | 10.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 90.8351 | 1.232%
CZ 4A | 0.27829 | 0.064043 | 0.096682 | 0.069374 | 0 | 0.10833 | 0 | 0.10892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 0.98971 | 15.19% | CZ 4A | 8.9325 | 2.0557 | 3.1033 | 2.6259 | 0 | 3.4772 | 0 | 3.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.1666 | 15.19% | CZ 4A | 2.618 | 0.60248 | 0.90952 | 0.59894 | 0 | 1.0191 | 0 | 1.0247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.2568 | 15.19% | CZ 4A | 0 | 0 | 0 | 0.0058226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0058226 | 15.19% | CZ 4A | 27.4076 | 6.3073 | 9.5218 | 6.9067 | 0 | 10.6691 | 0 | 10.7272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 97.5463 | 15.19%
CZ 4B | 0.27818 | 0.063882 | 0.096682 | 0.027759 | 0 | 0.12997 | 0 | 0.13893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 0.99947 | 0.8143% | CZ 4B | 8.9291 | 2.0505 | 3.1033 | 0.94768 | 0 | 4.1716 | 0 | 4.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.1374 | 0.8143% | CZ 4B | 2.617 | 0.60096 | 0.90952 | 0.25352 | 0 | 1.2226 | 0 | 1.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.3947 | 0.8143% | CZ 4B | 0 | 0 | 0 | 0.00082689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00082689 | 0.8143% | CZ 4B | 27.397 | 6.2915 | 9.5218 | 2.7444 | 0 | 12.7997 | 0 | 13.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 98.4436 | 0.8143%
CZ 4C | 0.27979 | 0.064043 | 0.096682 | 0.03939 | 0 | 0.051482 | 0 | 0.10919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 0.90465 | 2.441% | CZ 4C | 8.9808 | 2.0557 | 3.1033 | 1.3423 | 0 | 1.6524 | 0 | 3.5048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 29.1151 | 2.441% | CZ 4C | 2.6321 | 0.60248 | 0.90952 | 0.36007 | 0 | 0.4843 | 0 | 1.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 8.4998 | 2.441% | CZ 4C | 0 | 0 | 0 | 0.001137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001137 | 2.441% | CZ 4C | 27.5556 | 6.3073 | 9.5218 | 3.8939 | 0 | 5.0702 | 0 | 10.7537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 89.109 | 2.441%
CZ 5A | 0.27856 | 0.063936 | 0.096682 | 0.1277 | 0 | 0.063238 | 0 | 0.10205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 0.99623 | 17.64% | CZ 5A | 8.9411 | 2.0522 | 3.1033 | 5.7873 | 0 | 2.0298 | 0 | 3.2756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 33.6652 | 17.64% | CZ 5A | 2.6205 | 0.60147 | 0.90952 | 0.97416 | 0 | 0.5949 | 0 | 0.96002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.1447 | 17.64% | CZ 5A | 0 | 0 | 0 | 0.024634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024634 | 17.64% | CZ 5A | 27.434 | 6.2968 | 9.5218 | 12.8911 | 0 | 6.228 | 0 | 10.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 98.4287 | 17.64%
CZ 5B | 0.27834 | 0.06399 | 0.096682 | 0.073623 | 0 | 0.087395 | 0 | 0.12492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 0.98902 | 5.428% | CZ 5B | 8.9342 | 2.0539 | 3.1033 | 3.1909 | 0 | 2.8052 | 0 | 4.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 32.5731 | 5.428% | CZ 5B | 2.6185 | 0.60197 | 0.90952 | 0.58127 | 0 | 0.82216 | 0 | 1.1752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.1927 | 5.428% | CZ 5B | 0 | 0 | 0 | 0.012076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012076 | 5.428% | CZ 5B | 27.4129 | 6.302 | 9.5218 | 7.4052 | 0 | 8.6072 | 0 | 12.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 97.5583 | 5.428%
CZ 5C | 0.27926 | 0.06399 | 0.096682 | 0.046645 | 0 | 0.035323 | 0 | 0.098078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 0.88404 | 0.0594% | CZ 5C | 8.9635 | 2.0539 | 3.1033 | 1.6283 | 0 | 1.1338 | 0 | 3.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 28.5068 | 0.0594% | CZ 5C | 2.6271 | 0.60197 | 0.90952 | 0.42118 | 0 | 0.3323 | 0 | 0.92265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 8.2988 | 0.0594% | CZ 5C | 0 | 0 | 0 | 0.0019122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019122 | 0.0594% | CZ 5C | 27.5027 | 6.302 | 9.5218 | 4.6183 | 0 | 3.4788 | 0 | 9.6593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 87.0895 | 0.0594%
CZ 6A | 0.27861 | 0.06399 | 0.096682 | 0.18061 | 0 | 0.071505 | 0 | 0.1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.07 | 3.429% | CZ 6A | 8.9429 | 2.0539 | 3.1033 | 10.5971 | 0 | 2.2952 | 0 | 3.6754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 39.1436 | 3.429% | CZ 6A | 2.621 | 0.60197 | 0.90952 | 1.0535 | 0 | 0.67267 | 0 | 1.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.42 | 3.429% | CZ 6A | 0 | 0 | 0 | 0.070027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070027 | 3.429% | CZ 6A | 27.4393 | 6.302 | 9.5218 | 18.6825 | 0 | 7.0422 | 0 | 11.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 106.2715 | 3.429%
CZ 6B | 0.27883 | 0.063882 | 0.096682 | 0.11328 | 0 | 0.061359 | 0 | 0.12352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.0016 | 0.5733% | CZ 6B | 8.9498 | 2.0505 | 3.1033 | 6.3969 | 0 | 1.9695 | 0 | 3.9648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 34.9107 | 0.5733% | CZ 6B | 2.623 | 0.60096 | 0.90952 | 0.69439 | 0 | 0.57723 | 0 | 1.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.0513 | 0.5733% | CZ 6B | 0 | 0 | 0 | 0.040276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040276 | 0.5733% | CZ 6B | 27.4604 | 6.2915 | 9.5218 | 11.6717 | 0 | 6.043 | 0 | 12.1653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 99.1602 | 0.5733%
CZ 7 | 0.27813 | 0.06399 | 0.096682 | 0.20713 | 0 | 0.058997 | 0 | 0.11848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.0875 | 0.4129% | CZ 7 | 8.9274 | 2.0539 | 3.1033 | 14.1181 | 0 | 1.8937 | 0 | 3.8029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 42.3752 | 0.4129% | CZ 7 | 2.6165 | 0.60197 | 0.90952 | 0.94386 | 0 | 0.55501 | 0 | 1.1146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.2255 | 0.4129% | CZ 7 | 0 | 0 | 0 | 0.10898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10898 | 0.4129% | CZ 7 | 27.3917 | 6.302 | 9.5218 | 21.7925 | 0 | 5.8104 | 0 | 11.6683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 108.4932 | 0.4129%
CZ 8 | 0.2813 | 0.064419 | 0.096682 | 0.27889 | 0 | 0.037578 | 0 | 0.12594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.1489 | 0.02101% | CZ 8 | 9.029 | 2.0677 | 3.1033 | 21.9924 | 0 | 1.2062 | 0 | 4.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 49.9169 | 0.02101% | CZ 8 | 2.6463 | 0.60601 | 0.90952 | 0.86963 | 0 | 0.35351 | 0 | 1.1848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.0538 | 0.02101% | CZ 8 | 0 | 0 | 0 | 0.19025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19025 | 0.02101% | CZ 8 | 27.7036 | 6.3443 | 9.5218 | 29.8987 | 0 | 3.7009 | 0 | 12.4032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 115.5791 | 0.02101%
US Weighted | 0.27955 | 0.063937 | 0.096682 | 0.053116 | 0 | 0.16095 | 0 | 0.12166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26406 | 1.04 | 100% | US Weighted | 8.9731 | 2.0522 | 3.1033 | 2.3554 | 0 | 5.1663 | 0 | 3.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4759 | 34.0311 | 100% | US Weighted | 2.6299 | 0.60148 | 0.90952 | 0.41219 | 0 | 1.5141 | 0 | 1.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4841 | 9.6958 | 100% | US Weighted | 0 | 0 | 0 | 0.0094898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0094898 | 100% | US Weighted | 27.532 | 6.2969 | 9.5218 | 5.3525 | 0 | 15.8516 | 0 | 11.9816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0065 | 102.5428 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.38093 | 0.13367 | 0.096843 | 0 | 0 | 0.56479 | 0 | 0.17946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.6391 | 0% | CZ 0A | 12.2271 | 4.2905 | 3.1085 | 0 | 0 | 18.1287 | 0 | 5.7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 52.613 | 0% | CZ 0A | 3.5836 | 1.2575 | 0.91104 | 0 | 0 | 5.3132 | 0 | 1.6882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 15.42 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 37.5162 | 13.1645 | 9.5377 | 0 | 0 | 55.624 | 0 | 17.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 161.4318 | 0%
CZ 0B | 0.38093 | 0.13372 | 0.096843 | 0 | 0 | 0.44734 | 0 | 0.16191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.5042 | 0% | CZ 0B | 12.2271 | 4.2922 | 3.1085 | 0 | 0 | 14.3586 | 0 | 5.1969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 48.2811 | 0% | CZ 0B | 3.5836 | 1.258 | 0.91104 | 0 | 0 | 4.2083 | 0 | 1.5231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 14.1504 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 37.5162 | 13.1698 | 9.5377 | 0 | 0 | 44.0562 | 0 | 15.9454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 148.1404 | 0%
CZ 1A | 0.38093 | 0.13372 | 0.096843 | 0 | 0 | 0.4089 | 0 | 0.16255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.4664 | 2.924% | CZ 1A | 12.2271 | 4.2922 | 3.1085 | 0 | 0 | 13.1248 | 0 | 5.2175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 47.0681 | 2.924% | CZ 1A | 3.5836 | 1.258 | 0.91104 | 0 | 0 | 3.8467 | 0 | 1.5292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 13.7949 | 2.924% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.924% | CZ 1A | 37.5162 | 13.1698 | 9.5377 | 0 | 0 | 40.2707 | 0 | 16.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 144.4184 | 2.924%
CZ 1B | 0.38093 | 0.13356 | 0.096843 | 0.00016105 | 0 | 0.35822 | 0 | 0.1509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.4041 | 0% | CZ 1B | 12.2271 | 4.2871 | 3.1085 | 0.0051693 | 0 | 11.4982 | 0 | 4.8436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 45.0676 | 0% | CZ 1B | 3.5836 | 1.2565 | 0.91104 | 0.001515 | 0 | 3.3699 | 0 | 1.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 13.2085 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 37.5162 | 13.1539 | 9.5377 | 0.015861 | 0 | 35.2798 | 0 | 14.8616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 138.2803 | 0%
CZ 2A | 0.38093 | 0.13351 | 0.096843 | 0.0019863 | 0 | 0.33128 | 0 | 0.15461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.3826 | 20.19% | CZ 2A | 12.2271 | 4.2853 | 3.1085 | 0.063755 | 0 | 10.6332 | 0 | 4.9625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.3783 | 20.19% | CZ 2A | 3.5836 | 1.256 | 0.91104 | 0.018685 | 0 | 3.1164 | 0 | 1.4544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 13.0065 | 20.19% | CZ 2A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.19% | CZ 2A | 37.5162 | 13.1487 | 9.5377 | 0.19562 | 0 | 32.6258 | 0 | 15.2264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 136.1655 | 20.19%
CZ 2B | 0.38093 | 0.13362 | 0.096843 | 0.0018252 | 0 | 0.25193 | 0 | 0.15444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.303 | 4.066% | CZ 2B | 12.2271 | 4.2888 | 3.1085 | 0.058585 | 0 | 8.0865 | 0 | 4.9573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.8247 | 4.066% | CZ 2B | 3.5836 | 1.257 | 0.91104 | 0.01717 | 0 | 2.37 | 0 | 1.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.2581 | 4.066% | CZ 2B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.066% | CZ 2B | 37.5162 | 13.1592 | 9.5377 | 0.17976 | 0 | 24.8117 | 0 | 15.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 128.3302 | 4.066%
CZ 3A | 0.38093 | 0.13362 | 0.096843 | 0.029643 | 0 | 0.18456 | 0 | 0.13458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2436 | 18.35% | CZ 3A | 12.2271 | 4.2888 | 3.1085 | 1.1062 | 0 | 5.924 | 0 | 4.3198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.0722 | 18.35% | CZ 3A | 3.5836 | 1.257 | 0.91104 | 0.25806 | 0 | 1.7362 | 0 | 1.2661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.6784 | 18.35% | CZ 3A | 0 | 0 | 0 | 0.0022567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022567 | 18.35% | CZ 3A | 37.5162 | 13.1592 | 9.5377 | 2.9483 | 0 | 18.1765 | 0 | 13.2544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 122.5074 | 18.35%
CZ 3B | 0.38093 | 0.13356 | 0.096843 | 0.0099391 | 0 | 0.17479 | 0 | 0.14065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2202 | 7.24% | CZ 3B | 12.2271 | 4.2871 | 3.1085 | 0.33083 | 0 | 5.6104 | 0 | 4.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.1763 | 7.24% | CZ 3B | 3.5836 | 1.2565 | 0.91104 | 0.091912 | 0 | 1.6443 | 0 | 1.3231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.4769 | 7.24% | CZ 3B | 0 | 0 | 0 | 0.00017227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00017227 | 7.24% | CZ 3B | 37.5162 | 13.1539 | 9.5377 | 0.98105 | 0 | 17.2143 | 0 | 13.8518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 120.1701 | 7.24%
CZ 3C | 0.38093 | 0.13356 | 0.096843 | 0.00102 | 0 | 0.1334 | 0 | 0.11622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.1454 | 1.232% | CZ 3C | 12.2271 | 4.2871 | 3.1085 | 0.032739 | 0 | 4.2819 | 0 | 3.7305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.7657 | 1.232% | CZ 3C | 3.5836 | 1.2565 | 0.91104 | 0.0095952 | 0 | 1.255 | 0 | 1.0933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 10.7754 | 1.232% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.232% | CZ 3C | 37.5162 | 13.1539 | 9.5377 | 0.10045 | 0 | 13.1381 | 0 | 11.4463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 112.8077 | 1.232%
CZ 4A | 0.38093 | 0.1334 | 0.096843 | 0.076673 | 0 | 0.12589 | 0 | 0.12234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2195 | 15.19% | CZ 4A | 12.2271 | 4.2819 | 3.1085 | 3.0703 | 0 | 4.0407 | 0 | 3.9269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.7533 | 15.19% | CZ 4A | 3.5836 | 1.255 | 0.91104 | 0.63934 | 0 | 1.1842 | 0 | 1.1509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.3905 | 15.19% | CZ 4A | 0 | 0 | 0 | 0.008889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008889 | 15.19% | CZ 4A | 37.5162 | 13.1381 | 9.5377 | 7.6649 | 0 | 12.3979 | 0 | 12.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 120.2188 | 15.19%
CZ 4B | 0.38093 | 0.13351 | 0.096843 | 0.029893 | 0 | 0.14757 | 0 | 0.15391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2261 | 0.8143% | CZ 4B | 12.2271 | 4.2853 | 3.1085 | 1.0528 | 0 | 4.7368 | 0 | 4.9401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.4485 | 0.8143% | CZ 4B | 3.5836 | 1.256 | 0.91104 | 0.26867 | 0 | 1.3883 | 0 | 1.4479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.5218 | 0.8143% | CZ 4B | 0 | 0 | 0 | 0.0013609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013609 | 0.8143% | CZ 4B | 37.5162 | 13.1487 | 9.5377 | 2.9614 | 0 | 14.5338 | 0 | 15.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 120.7706 | 0.8143%
CZ 4C | 0.38093 | 0.13324 | 0.096843 | 0.039725 | 0 | 0.06093 | 0 | 0.12014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.1153 | 2.441% | CZ 4C | 12.2271 | 4.2767 | 3.1085 | 1.3802 | 0 | 1.9557 | 0 | 3.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 35.9024 | 2.441% | CZ 4C | 3.5836 | 1.2534 | 0.91104 | 0.35957 | 0 | 0.57319 | 0 | 1.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 10.4774 | 2.441% | CZ 4C | 0 | 0 | 0 | 0.0015332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015332 | 2.441% | CZ 4C | 37.5162 | 13.1222 | 9.5377 | 3.9319 | 0 | 6.0007 | 0 | 11.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 109.856 | 2.441%
CZ 5A | 0.38093 | 0.13345 | 0.096843 | 0.1398 | 0 | 0.075263 | 0 | 0.11606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2258 | 17.64% | CZ 5A | 12.2271 | 4.2836 | 3.1085 | 6.5229 | 0 | 2.4158 | 0 | 3.7253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.3811 | 17.64% | CZ 5A | 3.5836 | 1.2555 | 0.91104 | 1.0413 | 0 | 0.70802 | 0 | 1.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.2577 | 17.64% | CZ 5A | 0 | 0 | 0 | 0.029699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029699 | 17.64% | CZ 5A | 37.5162 | 13.1434 | 9.5377 | 14.1478 | 0 | 7.4123 | 0 | 11.4304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 121.1028 | 17.64%
CZ 5B | 0.38093 | 0.13345 | 0.096843 | 0.075353 | 0 | 0.10135 | 0 | 0.13947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2108 | 5.428% | CZ 5B | 12.2271 | 4.2836 | 3.1085 | 3.3786 | 0 | 3.2532 | 0 | 4.4766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 39.8256 | 5.428% | CZ 5B | 3.5836 | 1.2555 | 0.91104 | 0.57975 | 0 | 0.95346 | 0 | 1.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.2617 | 5.428% | CZ 5B | 0 | 0 | 0 | 0.014005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014005 | 5.428% | CZ 5B | 37.5162 | 13.1434 | 9.5377 | 7.6002 | 0 | 9.9818 | 0 | 13.7355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 119.4298 | 5.428%
CZ 5C | 0.38093 | 0.13324 | 0.096843 | 0.040636 | 0 | 0.044396 | 0 | 0.10817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.0877 | 0.0594% | CZ 5C | 12.2271 | 4.2767 | 3.1085 | 1.4318 | 0 | 1.425 | 0 | 3.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 35.0391 | 0.0594% | CZ 5C | 3.5836 | 1.2534 | 0.91104 | 0.36512 | 0 | 0.41764 | 0 | 1.0176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 10.2148 | 0.0594% | CZ 5C | 0 | 0 | 0 | 0.0018605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018605 | 0.0594% | CZ 5C | 37.5162 | 13.1222 | 9.5377 | 4.0258 | 0 | 4.3723 | 0 | 10.6532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 107.1425 | 0.0594%
CZ 6A | 0.38093 | 0.13335 | 0.096843 | 0.21092 | 0 | 0.083691 | 0 | 0.13088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.3201 | 3.429% | CZ 6A | 12.2271 | 4.2802 | 3.1085 | 13.1346 | 0 | 2.6863 | 0 | 4.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 48.7355 | 3.429% | CZ 6A | 3.5836 | 1.2544 | 0.91104 | 1.1282 | 0 | 0.78731 | 0 | 1.2312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.5622 | 3.429% | CZ 6A | 0 | 0 | 0 | 0.092852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092852 | 3.429% | CZ 6A | 37.5162 | 13.1328 | 9.5377 | 21.9598 | 0 | 8.2424 | 0 | 12.8896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 131.1935 | 3.429%
CZ 6B | 0.38093 | 0.13329 | 0.096843 | 0.12507 | 0 | 0.070915 | 0 | 0.13786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2284 | 0.5733% | CZ 6B | 12.2271 | 4.2784 | 3.1085 | 7.5735 | 0 | 2.2762 | 0 | 4.4249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.9865 | 0.5733% | CZ 6B | 3.5836 | 1.2539 | 0.91104 | 0.69792 | 0 | 0.66712 | 0 | 1.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.0769 | 0.5733% | CZ 6B | 0 | 0 | 0 | 0.051921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051921 | 0.5733% | CZ 6B | 37.5162 | 13.1275 | 9.5377 | 12.9816 | 0 | 6.9841 | 0 | 13.5769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 121.639 | 0.5733%
CZ 7 | 0.38093 | 0.13319 | 0.096951 | 0.23884 | 0 | 0.069519 | 0 | 0.13453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.3374 | 0.4129% | CZ 7 | 12.2271 | 4.275 | 3.1119 | 17.0915 | 0 | 2.2314 | 0 | 4.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 52.3529 | 0.4129% | CZ 7 | 3.5836 | 1.2529 | 0.91205 | 0.97921 | 0 | 0.65399 | 0 | 1.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.3137 | 0.4129% | CZ 7 | 0 | 0 | 0 | 0.1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1375 | 0.4129% | CZ 7 | 37.5162 | 13.1169 | 9.5482 | 25.2806 | 0 | 6.8466 | 0 | 13.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 133.4728 | 0.4129%
CZ 8 | 0.38093 | 0.13243 | 0.097219 | 0.31252 | 0 | 0.044503 | 0 | 0.14006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.3911 | 0.02101% | CZ 8 | 12.2271 | 4.2509 | 3.1205 | 25.3 | 0 | 1.4284 | 0 | 4.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 59.9204 | 0.02101% | CZ 8 | 3.5836 | 1.2459 | 0.91457 | 0.88629 | 0 | 0.41865 | 0 | 1.3176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.033 | 0.02101% | CZ 8 | 0 | 0 | 0 | 0.22276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22276 | 0.02101% | CZ 8 | 37.5162 | 13.0429 | 9.5747 | 33.6262 | 0 | 4.3829 | 0 | 13.7937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 139.8517 | 0.02101%
US Weighted | 0.38093 | 0.1335 | 0.096844 | 0.057276 | 0 | 0.18142 | 0 | 0.13528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2687 | 100% | US Weighted | 12.2271 | 4.2851 | 3.1085 | 2.6555 | 0 | 5.8232 | 0 | 4.3424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.5396 | 100% | US Weighted | 3.5836 | 1.2559 | 0.91104 | 0.42891 | 0 | 1.7067 | 0 | 1.2727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.8252 | 100% | US Weighted | 0 | 0 | 0 | 0.011921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011921 | 100% | US Weighted | 37.5162 | 13.1478 | 9.5377 | 5.7932 | 0 | 17.8671 | 0 | 13.3236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 125.1008 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.38093 | 0.13367 | 0.096843 | 0 | 0 | 0.7281 | 0 | 0.1793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.8023 | 0% | CZ 0A | 12.2271 | 4.2905 | 3.1085 | 0 | 0 | 23.3703 | 0 | 5.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 57.8495 | 0% | CZ 0A | 3.5836 | 1.2575 | 0.91104 | 0 | 0 | 6.8495 | 0 | 1.6867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 16.9547 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 37.5162 | 13.1645 | 9.5377 | 0 | 0 | 71.7069 | 0 | 17.6584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 177.4989 | 0%
CZ 0B | 0.38093 | 0.13372 | 0.096843 | 0 | 0 | 0.56861 | 0 | 0.16196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.6255 | 0% | CZ 0B | 12.2271 | 4.2922 | 3.1085 | 0 | 0 | 18.251 | 0 | 5.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 52.1753 | 0% | CZ 0B | 3.5836 | 1.258 | 0.91104 | 0 | 0 | 5.3491 | 0 | 1.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 15.2917 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 37.5162 | 13.1698 | 9.5377 | 0 | 0 | 55.9994 | 0 | 15.9507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 160.0889 | 0%
CZ 1A | 0.38093 | 0.13372 | 0.096843 | 0 | 0 | 0.51911 | 0 | 0.16218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.5762 | 2.924% | CZ 1A | 12.2271 | 4.2922 | 3.1085 | 0 | 0 | 16.6623 | 0 | 5.2055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 50.5935 | 2.924% | CZ 1A | 3.5836 | 1.258 | 0.91104 | 0 | 0 | 4.8834 | 0 | 1.5256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 14.8281 | 2.924% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.924% | CZ 1A | 37.5162 | 13.1698 | 9.5377 | 0 | 0 | 51.1248 | 0 | 15.9719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 155.2355 | 2.924%
CZ 1B | 0.38093 | 0.13356 | 0.096843 | 0.00026841 | 0 | 0.45324 | 0 | 0.15096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.4992 | 0% | CZ 1B | 12.2271 | 4.2871 | 3.1085 | 0.0086155 | 0 | 14.5481 | 0 | 4.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 48.1226 | 0% | CZ 1B | 3.5836 | 1.2565 | 0.91104 | 0.0025251 | 0 | 4.2638 | 0 | 1.4201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 14.1039 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 37.5162 | 13.1539 | 9.5377 | 0.026435 | 0 | 44.6377 | 0 | 14.8669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 147.654 | 0%
CZ 2A | 0.38093 | 0.13351 | 0.096843 | 0.0025936 | 0 | 0.42527 | 0 | 0.15729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.4799 | 20.19% | CZ 2A | 12.2271 | 4.2853 | 3.1085 | 0.084431 | 0 | 13.6504 | 0 | 5.0487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 47.5023 | 20.19% | CZ 2A | 3.5836 | 1.256 | 0.91104 | 0.02424 | 0 | 4.0007 | 0 | 1.4797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 13.9216 | 20.19% | CZ 2A | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 20.19% | CZ 2A | 37.5162 | 13.1487 | 9.5377 | 0.25566 | 0 | 41.8832 | 0 | 15.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 145.7473 | 20.19%
CZ 2B | 0.38093 | 0.13362 | 0.096843 | 0.0024326 | 0 | 0.31785 | 0 | 0.15804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.3732 | 4.066% | CZ 2B | 12.2271 | 4.2888 | 3.1085 | 0.079262 | 0 | 10.2024 | 0 | 5.0728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.0768 | 4.066% | CZ 2B | 3.5836 | 1.257 | 0.91104 | 0.022725 | 0 | 2.9902 | 0 | 1.4868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.9177 | 4.066% | CZ 2B | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 4.066% | CZ 2B | 37.5162 | 13.1592 | 9.5377 | 0.2398 | 0 | 31.304 | 0 | 15.5648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 135.2368 | 4.066%
CZ 3A | 0.38093 | 0.13362 | 0.096843 | 0.043842 | 0 | 0.23636 | 0 | 0.14349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.3185 | 18.35% | CZ 3A | 12.2271 | 4.2888 | 3.1085 | 1.6351 | 0 | 7.5868 | 0 | 4.6058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.55 | 18.35% | CZ 3A | 3.5836 | 1.257 | 0.91104 | 0.38179 | 0 | 2.2236 | 0 | 1.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.3733 | 18.35% | CZ 3A | 0 | 0 | 0 | 0.0033248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033248 | 18.35% | CZ 3A | 37.5162 | 13.1592 | 9.5377 | 4.3603 | 0 | 23.2785 | 0 | 14.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 129.899 | 18.35%
CZ 3B | 0.38093 | 0.13356 | 0.096843 | 0.015832 | 0 | 0.2201 | 0 | 0.15133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.282 | 7.24% | CZ 3B | 12.2271 | 4.2871 | 3.1085 | 0.53415 | 0 | 7.0647 | 0 | 4.8574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.1768 | 7.24% | CZ 3B | 3.5836 | 1.2565 | 0.91104 | 0.14544 | 0 | 2.0705 | 0 | 1.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.0571 | 7.24% | CZ 3B | 0 | 0 | 0 | 0.00037899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00037899 | 7.24% | CZ 3B | 37.5162 | 13.1539 | 9.5377 | 1.5641 | 0 | 21.6765 | 0 | 14.9039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 126.2674 | 7.24%
CZ 3C | 0.38093 | 0.13356 | 0.096843 | 0.0013957 | 0 | 0.1632 | 0 | 0.11762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.177 | 1.232% | CZ 3C | 12.2271 | 4.2871 | 3.1085 | 0.0448 | 0 | 5.2382 | 0 | 3.7753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 37.7789 | 1.232% | CZ 3C | 3.5836 | 1.2565 | 0.91104 | 0.01313 | 0 | 1.5352 | 0 | 1.1065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.0724 | 1.232% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.232% | CZ 3C | 37.5162 | 13.1539 | 9.5377 | 0.13746 | 0 | 16.0723 | 0 | 11.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 115.9164 | 1.232%
CZ 4A | 0.38093 | 0.1334 | 0.096843 | 0.10081 | 0 | 0.15595 | 0 | 0.1247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2761 | 15.19% | CZ 4A | 12.2271 | 4.2819 | 3.1085 | 3.9715 | 0 | 5.0056 | 0 | 4.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 41.6952 | 15.19% | CZ 4A | 3.5836 | 1.255 | 0.91104 | 0.84943 | 0 | 1.4671 | 0 | 1.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.9056 | 15.19% | CZ 4A | 0 | 0 | 0 | 0.010732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010732 | 15.19% | CZ 4A | 37.5162 | 13.1381 | 9.5377 | 10.0657 | 0 | 15.3586 | 0 | 12.2816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 125.813 | 15.19%
CZ 4B | 0.38093 | 0.13351 | 0.096843 | 0.040598 | 0 | 0.17866 | 0 | 0.15648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2705 | 0.8143% | CZ 4B | 12.2271 | 4.2853 | 3.1085 | 1.4542 | 0 | 5.7345 | 0 | 5.0228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 40.9303 | 0.8143% | CZ 4B | 3.5836 | 1.256 | 0.91104 | 0.36159 | 0 | 1.6807 | 0 | 1.4721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.9314 | 0.8143% | CZ 4B | 0 | 0 | 0 | 0.002205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002205 | 0.8143% | CZ 4B | 37.5162 | 13.1487 | 9.5377 | 4.0265 | 0 | 17.595 | 0 | 15.4115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 125.1506 | 0.8143%
CZ 4C | 0.38093 | 0.13324 | 0.096843 | 0.055914 | 0 | 0.068445 | 0 | 0.12095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.1398 | 2.441% | CZ 4C | 12.2271 | 4.2767 | 3.1085 | 1.947 | 0 | 2.1969 | 0 | 3.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.7363 | 2.441% | CZ 4C | 3.5836 | 1.2534 | 0.91104 | 0.50552 | 0 | 0.64389 | 0 | 1.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 10.7017 | 2.441% | CZ 4C | 0 | 0 | 0 | 0.0022223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022223 | 2.441% | CZ 4C | 37.5162 | 13.1222 | 9.5377 | 5.5351 | 0 | 6.7409 | 0 | 11.9115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 112.2787 | 2.441%
CZ 5A | 0.38093 | 0.13345 | 0.096843 | 0.20222 | 0 | 0.089059 | 0 | 0.12309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.3091 | 17.64% | CZ 5A | 12.2271 | 4.2836 | 3.1085 | 9.5173 | 0 | 2.8586 | 0 | 3.9511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 45.0441 | 17.64% | CZ 5A | 3.5836 | 1.2555 | 0.91104 | 1.4953 | 0 | 0.83781 | 0 | 1.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.9076 | 17.64% | CZ 5A | 0 | 0 | 0 | 0.044152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044152 | 17.64% | CZ 5A | 37.5162 | 13.1434 | 9.5377 | 20.4805 | 0 | 8.7711 | 0 | 12.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 129.4869 | 17.64%
CZ 5B | 0.38093 | 0.13345 | 0.096843 | 0.11944 | 0 | 0.12089 | 0 | 0.14773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.2827 | 5.428% | CZ 5B | 12.2271 | 4.2836 | 3.1085 | 5.4823 | 0 | 3.8804 | 0 | 4.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 42.8218 | 5.428% | CZ 5B | 3.5836 | 1.2555 | 0.91104 | 0.90195 | 0 | 1.1373 | 0 | 1.3898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.8455 | 5.428% | CZ 5B | 0 | 0 | 0 | 0.024049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024049 | 5.428% | CZ 5B | 37.5162 | 13.1434 | 9.5377 | 12.071 | 0 | 11.9062 | 0 | 14.5497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 126.6393 | 5.428%
CZ 5C | 0.38093 | 0.13324 | 0.096843 | 0.071764 | 0 | 0.044073 | 0 | 0.11053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.1208 | 0.0594% | CZ 5C | 12.2271 | 4.2767 | 3.1085 | 2.6069 | 0 | 1.4147 | 0 | 3.5479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 36.2797 | 0.0594% | CZ 5C | 3.5836 | 1.2534 | 0.91104 | 0.63429 | 0 | 0.41461 | 0 | 1.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 10.5032 | 0.0594% | CZ 5C | 0 | 0 | 0 | 0.0044273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044273 | 0.0594% | CZ 5C | 37.5162 | 13.1222 | 9.5377 | 7.1243 | 0 | 4.3406 | 0 | 10.8858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 110.4419 | 0.0594%
CZ 6A | 0.38093 | 0.13335 | 0.096843 | 0.3031 | 0 | 0.091421 | 0 | 0.14129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.4304 | 3.429% | CZ 6A | 12.2271 | 4.2802 | 3.1085 | 18.3427 | 0 | 2.9344 | 0 | 4.5352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 54.526 | 3.429% | CZ 6A | 3.5836 | 1.2544 | 0.91104 | 1.6928 | 0 | 0.86003 | 0 | 1.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.2975 | 3.429% | CZ 6A | 0 | 0 | 0 | 0.12567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12567 | 3.429% | CZ 6A | 37.5162 | 13.1328 | 9.5377 | 31.4575 | 0 | 9.0037 | 0 | 13.9153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 142.4782 | 3.429%
CZ 6B | 0.38093 | 0.13329 | 0.096843 | 0.19598 | 0 | 0.073438 | 0 | 0.14108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.305 | 0.5733% | CZ 6B | 12.2271 | 4.2784 | 3.1085 | 11.753 | 0 | 2.3572 | 0 | 4.5283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 47.3504 | 0.5733% | CZ 6B | 3.5836 | 1.2539 | 0.91104 | 1.109 | 0 | 0.69085 | 0 | 1.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.542 | 0.5733% | CZ 6B | 0 | 0 | 0 | 0.079691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079691 | 0.5733% | CZ 6B | 37.5162 | 13.1275 | 9.5377 | 20.3204 | 0 | 7.2326 | 0 | 13.8941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 129.5435 | 0.5733%
CZ 7 | 0.38093 | 0.13319 | 0.096951 | 0.35939 | 0 | 0.07376 | 0 | 0.15031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.478 | 0.4129% | CZ 7 | 12.2271 | 4.275 | 3.1119 | 25.4125 | 0 | 2.3675 | 0 | 4.8247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 61.3166 | 0.4129% | CZ 7 | 3.5836 | 1.2529 | 0.91205 | 1.5145 | 0 | 0.69388 | 0 | 1.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.0374 | 0.4129% | CZ 7 | 0 | 0 | 0 | 0.20245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20245 | 0.4129% | CZ 7 | 37.5162 | 13.1169 | 9.5482 | 37.9833 | 0 | 7.2643 | 0 | 14.8035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 148.1475 | 0.4129%
CZ 8 | 0.38093 | 0.13243 | 0.097219 | 0.41874 | 0 | 0.047831 | 0 | 0.15144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.512 | 0.02101% | CZ 8 | 12.2271 | 4.2509 | 3.1205 | 33.8482 | 0 | 1.5353 | 0 | 4.8609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 68.9407 | 0.02101% | CZ 8 | 3.5836 | 1.2459 | 0.91457 | 1.1943 | 0 | 0.44996 | 0 | 1.4246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 11.4794 | 0.02101% | CZ 8 | 0 | 0 | 0 | 0.29773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29773 | 0.02101% | CZ 8 | 37.5162 | 13.0429 | 9.5747 | 45.0456 | 0 | 4.7107 | 0 | 14.9145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 152.7197 | 0.02101%
US Weighted | 0.38093 | 0.1335 | 0.096844 | 0.082117 | 0 | 0.22824 | 0 | 0.14092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28344 | 1.346 | 100% | US Weighted | 12.2271 | 4.2851 | 3.1085 | 3.8082 | 0 | 7.3261 | 0 | 4.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0979 | 44.3761 | 100% | US Weighted | 3.5836 | 1.2559 | 0.91104 | 0.61482 | 0 | 2.1472 | 0 | 1.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6665 | 12.5046 | 100% | US Weighted | 0 | 0 | 0 | 0.017104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017104 | 100% | US Weighted | 37.5162 | 13.1478 | 9.5377 | 8.306 | 0 | 22.4787 | 0 | 13.8786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.9151 | 132.7801 | 100%
Building Type: | Small Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Small Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 5502 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 5502 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 5502 | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.24377 | 0.10382 | 0.00016105 | 0 | 0 | 0.37717 | 0 | 0.082403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.83154 | 0% | CZ 0A | 7.8246 | 3.3325 | 0.0051693 | 0 | 0 | 12.1065 | 0 | 2.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 26.6907 | 0% | CZ 0A | 2.2933 | 0.97669 | 0.001515 | 0 | 0 | 3.5482 | 0 | 0.77519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 7.8226 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 24.0081 | 10.225 | 0.015861 | 0 | 0 | 37.1461 | 0 | 8.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 81.8949 | 0%
CZ 0B | 0.24313 | 0.10334 | 0.00016105 | 0 | 0 | 0.23959 | 0 | 0.047563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.65799 | 0% | CZ 0B | 7.8039 | 3.317 | 0.0051693 | 0 | 0 | 7.6902 | 0 | 1.5267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 21.12 | 0% | CZ 0B | 2.2872 | 0.97214 | 0.001515 | 0 | 0 | 2.2539 | 0 | 0.44744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 6.1899 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 23.9446 | 10.1774 | 0.015861 | 0 | 0 | 23.5957 | 0 | 4.6842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 64.8022 | 0%
CZ 1A | 0.2413 | 0.10318 | 0.00016105 | 0 | 0 | 0.26782 | 0 | 0.06968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.70636 | 2.924% | CZ 1A | 7.7453 | 3.3118 | 0.0051693 | 0 | 0 | 8.5965 | 0 | 2.2366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 22.6725 | 2.924% | CZ 1A | 2.27 | 0.97063 | 0.001515 | 0 | 0 | 2.5195 | 0 | 0.6555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 6.6449 | 2.924% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.924% | CZ 1A | 23.7649 | 10.1615 | 0.015861 | 0 | 0 | 26.3766 | 0 | 6.8625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 69.5657 | 2.924%
CZ 1B | 0.24168 | 0.10312 | 0.00016105 | 5.3683e-05 | 0 | 0.1931 | 0 | 0.044664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.60699 | 0% | CZ 1B | 7.7574 | 3.3101 | 0.0051693 | 0.0017231 | 0 | 6.198 | 0 | 1.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 19.483 | 0% | CZ 1B | 2.2736 | 0.97012 | 0.001515 | 0.00050501 | 0 | 1.8165 | 0 | 0.42017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 5.7102 | 0% | CZ 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 1B | 23.8019 | 10.1562 | 0.015861 | 0.005287 | 0 | 19.0172 | 0 | 4.3987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 59.7796 | 0%
CZ 2A | 0.24211 | 0.10296 | 0.00016105 | 0.0013053 | 0 | 0.21725 | 0 | 0.061628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.64963 | 20.19% | CZ 2A | 7.7712 | 3.3049 | 0.0051693 | 0.043077 | 0 | 6.9734 | 0 | 1.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 20.8529 | 20.19% | CZ 2A | 2.2776 | 0.96861 | 0.001515 | 0.01212 | 0 | 2.0438 | 0 | 0.57975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 6.1111 | 20.19% | CZ 2A | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 20.19% | CZ 2A | 23.8442 | 10.1404 | 0.015861 | 0.12877 | 0 | 21.3963 | 0 | 6.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 63.9793 | 20.19%
CZ 2B | 0.24077 | 0.10307 | 0.00016105 | 0.00076844 | 0 | 0.13689 | 0 | 0.04563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.5515 | 4.066% | CZ 2B | 7.7281 | 3.3083 | 0.0051693 | 0.025846 | 0 | 4.3939 | 0 | 1.4646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 17.7031 | 4.066% | CZ 2B | 2.265 | 0.96962 | 0.001515 | 0.0070701 | 0 | 1.2878 | 0 | 0.42926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 5.188 | 4.066% | CZ 2B | 0 | 0 | 0 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7227e-05 | 4.066% | CZ 2B | 23.712 | 10.1509 | 0.015861 | 0.0759 | 0 | 13.4817 | 0 | 4.4939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 54.3147 | 4.066%
CZ 3A | 0.24146 | 0.10286 | 0.00016105 | 0.013214 | 0 | 0.12449 | 0 | 0.052341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.55874 | 18.35% | CZ 3A | 7.7505 | 3.3015 | 0.0051693 | 0.47728 | 0 | 3.9959 | 0 | 1.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 17.9874 | 18.35% | CZ 3A | 2.2715 | 0.9676 | 0.001515 | 0.11716 | 0 | 1.1711 | 0 | 0.49239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 5.2491 | 18.35% | CZ 3A | 0 | 0 | 0 | 0.0007752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007752 | 18.35% | CZ 3A | 23.7807 | 10.1298 | 0.015861 | 1.3113 | 0 | 12.2604 | 0 | 5.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 55.0373 | 18.35%
CZ 3B | 0.2412 | 0.10329 | 0.00016105 | 0.0047011 | 0 | 0.095823 | 0 | 0.044234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.51361 | 7.24% | CZ 3B | 7.7419 | 3.3152 | 0.0051693 | 0.1568 | 0 | 3.0757 | 0 | 1.4198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.4917 | 7.24% | CZ 3B | 2.269 | 0.97164 | 0.001515 | 0.043431 | 0 | 0.90144 | 0 | 0.41613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.8309 | 7.24% | CZ 3B | 0 | 0 | 0 | 8.6134e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6134e-05 | 7.24% | CZ 3B | 23.7543 | 10.1721 | 0.015861 | 0.46409 | 0 | 9.4372 | 0 | 4.3564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 50.5844 | 7.24%
CZ 3C | 0.24141 | 0.10334 | 0.00016105 | -0.00010737 | 0 | 0.085033 | 0 | 0.034249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.4883 | 1.232% | CZ 3C | 7.7488 | 3.317 | 0.0051693 | -0.0034462 | 0 | 2.7294 | 0 | 1.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 15.6733 | 1.232% | CZ 3C | 2.271 | 0.97214 | 0.001515 | -0.00101 | 0 | 0.79994 | 0 | 0.3222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.5936 | 1.232% | CZ 3C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.232% | CZ 3C | 23.7754 | 10.1774 | 0.015861 | -0.010574 | 0 | 8.3745 | 0 | 3.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 48.0901 | 1.232%
CZ 4A | 0.24302 | 0.10286 | 0.00016105 | 0.040695 | 0 | 0.075209 | 0 | 0.041121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.52727 | 15.19% | CZ 4A | 7.8005 | 3.3015 | 0.0051693 | 1.6782 | 0 | 2.4141 | 0 | 1.3199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 17.2963 | 15.19% | CZ 4A | 2.2862 | 0.9676 | 0.001515 | 0.3328 | 0 | 0.70752 | 0 | 0.38684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.9102 | 15.19% | CZ 4A | 0 | 0 | 0 | 0.0054264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054264 | 15.19% | CZ 4A | 23.934 | 10.1298 | 0.015861 | 4.0772 | 0 | 7.407 | 0 | 4.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 51.9982 | 15.19%
CZ 4B | 0.24324 | 0.10318 | 0.00016105 | 0.017876 | 0 | 0.085785 | 0 | 0.051804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.52625 | 0.8143% | CZ 4B | 7.8073 | 3.3118 | 0.0051693 | 0.67886 | 0 | 2.7535 | 0 | 1.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 16.9966 | 0.8143% | CZ 4B | 2.2882 | 0.97063 | 0.001515 | 0.15403 | 0 | 0.80701 | 0 | 0.48733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.9365 | 0.8143% | CZ 4B | 0 | 0 | 0 | 0.0015332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015332 | 0.8143% | CZ 4B | 23.9552 | 10.1615 | 0.015861 | 1.7801 | 0 | 8.4486 | 0 | 5.1019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 51.8475 | 0.8143%
CZ 4C | 0.24152 | 0.10227 | 0.00016105 | 0.022389 | 0 | 0.030331 | 0 | 0.034142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.45502 | 2.441% | CZ 4C | 7.7522 | 3.2825 | 0.0051693 | 0.79777 | 0 | 0.97355 | 0 | 1.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 14.6842 | 2.441% | CZ 4C | 2.272 | 0.96204 | 0.001515 | 0.19998 | 0 | 0.28533 | 0 | 0.32119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.2699 | 2.441% | CZ 4C | 0 | 0 | 0 | 0.0011542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011542 | 2.441% | CZ 4C | 23.786 | 10.0716 | 0.015861 | 2.2198 | 0 | 2.9871 | 0 | 3.3625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 44.8273 | 2.441%
CZ 5A | 0.24318 | 0.10269 | 0.00016105 | 0.088858 | 0 | 0.040369 | 0 | 0.03994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.53942 | 17.64% | CZ 5A | 7.8056 | 3.2963 | 0.0051693 | 4.34 | 0 | 1.2958 | 0 | 1.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 18.8019 | 17.64% | CZ 5A | 2.2877 | 0.96608 | 0.001515 | 0.63581 | 0 | 0.37977 | 0 | 0.37573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.8744 | 17.64% | CZ 5A | 0 | 0 | 0 | 0.021706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021706 | 17.64% | CZ 5A | 23.9499 | 10.1139 | 0.015861 | 9.0287 | 0 | 3.9758 | 0 | 3.9335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 53.4021 | 17.64%
CZ 5B | 0.2434 | 0.10296 | 0.00016105 | 0.057842 | 0 | 0.055293 | 0 | 0.047455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.53132 | 5.428% | CZ 5B | 7.8125 | 3.3049 | 0.0051693 | 2.8083 | 0 | 1.7748 | 0 | 1.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 18.006 | 5.428% | CZ 5B | 2.2897 | 0.96861 | 0.001515 | 0.41613 | 0 | 0.52016 | 0 | 0.44643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.8703 | 5.428% | CZ 5B | 0 | 0 | 0 | 0.013885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013885 | 5.428% | CZ 5B | 23.971 | 10.1404 | 0.015861 | 5.8741 | 0 | 5.4456 | 0 | 4.6737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 52.505 | 5.428%
CZ 5C | 0.24243 | 0.10221 | 0.00016105 | 0.030427 | 0 | 0.01632 | 0 | 0.028452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.44421 | 0.0594% | CZ 5C | 7.7815 | 3.2808 | 0.0051693 | 1.1561 | 0 | 0.52382 | 0 | 0.91324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 14.4378 | 0.0594% | CZ 5C | 2.2806 | 0.96154 | 0.001515 | 0.2621 | 0 | 0.15352 | 0 | 0.26766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.1547 | 0.0594% | CZ 5C | 0 | 0 | 0 | 0.0026185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026185 | 0.0594% | CZ 5C | 23.8759 | 10.0664 | 0.015861 | 3.0301 | 0 | 1.6072 | 0 | 2.8021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 43.782 | 0.0594%
CZ 6A | 0.24307 | 0.10259 | 0.00016105 | 0.1323 | 0 | 0.041228 | 0 | 0.049656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.59322 | 3.429% | CZ 6A | 7.8022 | 3.2928 | 0.0051693 | 8.3073 | 0 | 1.3233 | 0 | 1.5939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 23.1018 | 3.429% | CZ 6A | 2.2867 | 0.96507 | 0.001515 | 0.69843 | 0 | 0.38785 | 0 | 0.46713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 5.0344 | 3.429% | CZ 6A | 0 | 0 | 0 | 0.059243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059243 | 3.429% | CZ 6A | 23.9393 | 10.1034 | 0.015861 | 13.7871 | 0 | 4.0604 | 0 | 4.8904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 59.1809 | 3.429%
CZ 6B | 0.24286 | 0.10227 | 0.00016105 | 0.087154 | 0 | 0.03221 | 0 | 0.04257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.53143 | 0.5733% | CZ 6B | 7.7953 | 3.2825 | 0.0051693 | 5.6266 | 0 | 1.0339 | 0 | 1.3664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 19.887 | 0.5733% | CZ 6B | 2.2847 | 0.96204 | 0.001515 | 0.43936 | 0 | 0.30301 | 0 | 0.40047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.6188 | 0.5733% | CZ 6B | 0 | 0 | 0 | 0.041275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041275 | 0.5733% | CZ 6B | 23.9182 | 10.0716 | 0.015861 | 9.111 | 0 | 3.1722 | 0 | 4.1926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 52.8659 | 0.5733%
CZ 7 | 0.24297 | 0.10216 | 0.00026841 | 0.16856 | 0 | 0.035055 | 0 | 0.060232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.63346 | 0.4129% | CZ 7 | 7.7987 | 3.2791 | 0.0086155 | 12.3831 | 0 | 1.1252 | 0 | 1.9333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 27.3051 | 0.4129% | CZ 7 | 2.2857 | 0.96103 | 0.0025251 | 0.64793 | 0 | 0.32977 | 0 | 0.56662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 5.0213 | 0.4129% | CZ 7 | 0 | 0 | 0 | 0.10172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10172 | 0.4129% | CZ 7 | 23.9287 | 10.0611 | 0.026435 | 17.9016 | 0 | 3.4524 | 0 | 5.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 63.6866 | 0.4129%
CZ 8 | 0.23948 | 0.099205 | 0.00053683 | 0.17397 | 0 | 0.021366 | 0 | 0.052179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.61095 | 0.02101% | CZ 8 | 7.6867 | 3.1843 | 0.017231 | 14.5346 | 0 | 0.68579 | 0 | 1.6748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 28.5606 | 0.02101% | CZ 8 | 2.2529 | 0.93326 | 0.0050501 | 0.43279 | 0 | 0.20099 | 0 | 0.49087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 4.5436 | 0.02101% | CZ 8 | 0 | 0 | 0 | 0.13058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13058 | 0.02101% | CZ 8 | 23.5851 | 9.7703 | 0.05287 | 18.8032 | 0 | 2.1042 | 0 | 5.1389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 61.839 | 0.02101%
US Weighted | 0.24227 | 0.10288 | 0.00016157 | 0.034529 | 0 | 0.11282 | 0 | 0.048905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024211 | 0.56578 | 100% | US Weighted | 7.7764 | 3.3023 | 0.0051861 | 1.6784 | 0 | 3.6213 | 0 | 1.5698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77712 | 18.7304 | 100% | US Weighted | 2.2791 | 0.96784 | 0.0015199 | 0.24816 | 0 | 1.0613 | 0 | 0.46007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22776 | 5.2458 | 100% | US Weighted | 0 | 0 | 0 | 0.0083167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083167 | 100% | US Weighted | 23.8601 | 10.1324 | 0.015912 | 3.507 | 0 | 11.1112 | 0 | 4.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3844 | 55.8274 | 100%
Building Type: | Small Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Small Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 5502 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 5502 | [17 empty] | Prototype Floor Area: | 5502 | Building Type: | Small Office | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 63.99% | 77.67% | 0.1663% |  |  | 51.8% |  | 45.96% | [7 empty] | 8.542% | 46.14% | 0% | CZ 0A | 63.99% | 77.67% | 0.1663% |  |  | 51.8% |  | 45.96% | [7 empty] | 8.542% | 46.14% | 0% | CZ 0A | 63.99% | 77.67% | 0.1663% |  |  | 51.8% |  | 45.96% | [7 empty] | 8.542% | 46.14% | 0% | CZ 0A | [16 empty] | 0% | 0% | CZ 0A | 63.99% | 77.67% | 0.1663% |  |  | 51.8% |  | 45.96% | [7 empty] | 8.542% | 46.14% | 0%
CZ 0B | 63.82% | 77.28% | 0.1663% |  |  | 42.14% |  | 29.37% | [7 empty] | 8.542% | 40.48% | 0% | CZ 0B | 63.82% | 77.28% | 0.1663% |  |  | 42.14% |  | 29.37% | [7 empty] | 8.542% | 40.48% | 0% | CZ 0B | 63.82% | 77.28% | 0.1663% |  |  | 42.14% |  | 29.37% | [7 empty] | 8.542% | 40.48% | 0% | CZ 0B | [16 empty] | 0% | 0% | CZ 0B | 63.82% | 77.28% | 0.1663% |  |  | 42.14% |  | 29.37% | [7 empty] | 8.542% | 40.48% | 0%
CZ 1A | 63.35% | 77.16% | 0.1663% |  |  | 51.59% |  | 42.97% | [7 empty] | 8.542% | 44.81% | 2.924% | CZ 1A | 63.35% | 77.16% | 0.1663% |  |  | 51.59% |  | 42.97% | [7 empty] | 8.542% | 44.81% | 2.924% | CZ 1A | 63.35% | 77.16% | 0.1663% |  |  | 51.59% |  | 42.97% | [7 empty] | 8.542% | 44.81% | 2.924% | CZ 1A | [16 empty] | 0% | 2.924% | CZ 1A | 63.35% | 77.16% | 0.1663% |  |  | 51.59% |  | 42.97% | [7 empty] | 8.542% | 44.81% | 2.924%
CZ 1B | 63.44% | 77.21% | 0.1663% | 20% |  | 42.6% |  | 29.59% | [7 empty] | 8.542% | 40.49% | 0% | CZ 1B | 63.44% | 77.21% | 0.1663% | 20% |  | 42.6% |  | 29.59% | [7 empty] | 8.542% | 40.49% | 0% | CZ 1B | 63.44% | 77.21% | 0.1663% | 20% |  | 42.6% |  | 29.59% | [7 empty] | 8.542% | 40.49% | 0% | CZ 1B | [16 empty] | 0% | 0% | CZ 1B | 63.44% | 77.21% | 0.1663% | 20% |  | 42.6% |  | 29.59% | [7 empty] | 8.542% | 40.49% | 0%
CZ 2A | 63.56% | 77.12% | 0.1663% | 50.33% |  | 51.09% |  | 39.18% | [7 empty] | 8.542% | 43.9% | 20.19% | CZ 2A | 63.56% | 77.12% | 0.1663% | 51.02% |  | 51.09% |  | 39.18% | [7 empty] | 8.542% | 43.9% | 20.19% | CZ 2A | 63.56% | 77.12% | 0.1663% | 50% |  | 51.09% |  | 39.18% | [7 empty] | 8.542% | 43.9% | 20.19% | CZ 2A |  |  |  | 100% | [12 empty] | 100% | 20.19% | CZ 2A | 63.56% | 77.12% | 0.1663% | 50.37% |  | 51.09% |  | 39.18% | [7 empty] | 8.542% | 43.9% | 20.19%
CZ 2B | 63.2% | 77.14% | 0.1663% | 31.59% |  | 43.07% |  | 28.87% | [7 empty] | 8.542% | 40.16% | 4.066% | CZ 2B | 63.2% | 77.14% | 0.1663% | 32.61% |  | 43.07% |  | 28.87% | [7 empty] | 8.542% | 40.16% | 4.066% | CZ 2B | 63.2% | 77.14% | 0.1663% | 31.11% |  | 43.07% |  | 28.87% | [7 empty] | 8.542% | 40.16% | 4.066% | CZ 2B |  |  |  | 100% | [12 empty] | 100% | 4.066% | CZ 2B | 63.2% | 77.14% | 0.1663% | 31.65% |  | 43.07% |  | 28.87% | [7 empty] | 8.542% | 40.16% | 4.066%
CZ 3A | 63.39% | 76.98% | 0.1663% | 30.14% |  | 52.67% |  | 36.48% | [7 empty] | 8.542% | 42.38% | 18.35% | CZ 3A | 63.39% | 76.98% | 0.1663% | 29.19% |  | 52.67% |  | 36.48% | [7 empty] | 8.542% | 42.27% | 18.35% | CZ 3A | 63.39% | 76.98% | 0.1663% | 30.69% |  | 52.67% |  | 36.48% | [7 empty] | 8.542% | 42.42% | 18.35% | CZ 3A |  |  |  | 23.32% | [12 empty] | 23.32% | 18.35% | CZ 3A | 63.39% | 76.98% | 0.1663% | 30.07% |  | 52.67% |  | 36.48% | [7 empty] | 8.542% | 42.37% | 18.35%
CZ 3B | 63.32% | 77.33% | 0.1663% | 29.69% |  | 43.54% |  | 29.23% | [7 empty] | 8.542% | 40.06% | 7.24% | CZ 3B | 63.32% | 77.33% | 0.1663% | 29.35% |  | 43.54% |  | 29.23% | [7 empty] | 8.542% | 40.05% | 7.24% | CZ 3B | 63.32% | 77.33% | 0.1663% | 29.86% |  | 43.54% |  | 29.23% | [7 empty] | 8.542% | 40.07% | 7.24% | CZ 3B |  |  |  | 22.73% | [12 empty] | 22.73% | 7.24% | CZ 3B | 63.32% | 77.33% | 0.1663% | 29.67% |  | 43.54% |  | 29.23% | [7 empty] | 8.542% | 40.06% | 7.24%
CZ 3C | 63.37% | 77.37% | 0.1663% | -7.692% |  | 52.11% |  | 29.12% | [7 empty] | 8.542% | 41.49% | 1.232% | CZ 3C | 63.37% | 77.37% | 0.1663% | -7.692% |  | 52.11% |  | 29.12% | [7 empty] | 8.542% | 41.49% | 1.232% | CZ 3C | 63.37% | 77.37% | 0.1663% | -7.692% |  | 52.11% |  | 29.12% | [7 empty] | 8.542% | 41.49% | 1.232% | CZ 3C | [16 empty] | 0% | 1.232% | CZ 3C | 63.37% | 77.37% | 0.1663% | -7.692% |  | 52.11% |  | 29.12% | [7 empty] | 8.542% | 41.49% | 1.232%
CZ 4A | 63.8% | 77.1% | 0.1663% | 40.37% |  | 48.23% |  | 32.97% | [7 empty] | 8.542% | 41.32% | 15.19% | CZ 4A | 63.8% | 77.1% | 0.1663% | 42.26% |  | 48.23% |  | 32.97% | [7 empty] | 8.542% | 41.48% | 15.19% | CZ 4A | 63.8% | 77.1% | 0.1663% | 39.18% |  | 48.23% |  | 32.97% | [7 empty] | 8.542% | 41.24% | 15.19% | CZ 4A |  |  |  | 50.56% | [12 empty] | 50.56% | 15.19% | CZ 4A | 63.8% | 77.1% | 0.1663% | 40.51% |  | 48.23% |  | 32.97% | [7 empty] | 8.542% | 41.33% | 15.19%
CZ 4B | 63.85% | 77.28% | 0.1663% | 44.03% |  | 48.02% |  | 33.1% | [7 empty] | 8.542% | 41.42% | 0.8143% | CZ 4B | 63.85% | 77.28% | 0.1663% | 46.68% |  | 48.02% |  | 33.1% | [7 empty] | 8.542% | 41.53% | 0.8143% | CZ 4B | 63.85% | 77.28% | 0.1663% | 42.6% |  | 48.02% |  | 33.1% | [7 empty] | 8.542% | 41.37% | 0.8143% | CZ 4B |  |  |  | 69.53% | [12 empty] | 69.53% | 0.8143% | CZ 4B | 63.85% | 77.28% | 0.1663% | 44.21% |  | 48.02% |  | 33.1% | [7 empty] | 8.542% | 41.43% | 0.8143%
CZ 4C | 63.4% | 76.75% | 0.1663% | 40.04% |  | 44.31% |  | 28.23% | [7 empty] | 8.542% | 39.92% | 2.441% | CZ 4C | 63.4% | 76.75% | 0.1663% | 40.97% |  | 44.31% |  | 28.23% | [7 empty] | 8.542% | 39.97% | 2.441% | CZ 4C | 63.4% | 76.75% | 0.1663% | 39.56% |  | 44.31% |  | 28.23% | [7 empty] | 8.542% | 39.9% | 2.441% | CZ 4C |  |  |  | 51.94% | [12 empty] | 51.94% | 2.441% | CZ 4C | 63.4% | 76.75% | 0.1663% | 40.1% |  | 44.31% |  | 28.23% | [7 empty] | 8.542% | 39.93% | 2.441%
CZ 5A | 63.84% | 76.95% | 0.1663% | 43.94% |  | 45.33% |  | 32.45% | [7 empty] | 8.542% | 41.21% | 17.64% | CZ 5A | 63.84% | 76.95% | 0.1663% | 45.6% |  | 45.33% |  | 32.45% | [7 empty] | 8.542% | 41.74% | 17.64% | CZ 5A | 63.84% | 76.95% | 0.1663% | 42.52% |  | 45.33% |  | 32.45% | [7 empty] | 8.542% | 40.93% | 17.64% | CZ 5A |  |  |  | 49.16% | [12 empty] | 49.16% | 17.64% | CZ 5A | 63.84% | 76.95% | 0.1663% | 44.08% |  | 45.33% |  | 32.45% | [7 empty] | 8.542% | 41.24% | 17.64%
CZ 5B | 63.9% | 77.15% | 0.1663% | 48.43% |  | 45.74% |  | 32.12% | [7 empty] | 8.542% | 41.42% | 5.428% | CZ 5B | 63.9% | 77.15% | 0.1663% | 51.22% |  | 45.74% |  | 32.12% | [7 empty] | 8.542% | 42.05% | 5.428% | CZ 5B | 63.9% | 77.15% | 0.1663% | 46.14% |  | 45.74% |  | 32.12% | [7 empty] | 8.542% | 41.12% | 5.428% | CZ 5B |  |  |  | 57.74% | [12 empty] | 57.74% | 5.428% | CZ 5B | 63.9% | 77.15% | 0.1663% | 48.66% |  | 45.74% |  | 32.12% | [7 empty] | 8.542% | 41.46% | 5.428%
CZ 5C | 63.64% | 76.71% | 0.1663% | 42.4% |  | 37.03% |  | 25.74% | [7 empty] | 8.542% | 39.63% | 0.0594% | CZ 5C | 63.64% | 76.71% | 0.1663% | 44.35% |  | 37.03% |  | 25.74% | [7 empty] | 8.542% | 39.8% | 0.0594% | CZ 5C | 63.64% | 76.71% | 0.1663% | 41.32% |  | 37.03% |  | 25.74% | [7 empty] | 8.542% | 39.56% | 0.0594% | CZ 5C |  |  |  | 59.14% | [12 empty] | 59.14% | 0.0594% | CZ 5C | 63.64% | 76.71% | 0.1663% | 42.53% |  | 37.03% |  | 25.74% | [7 empty] | 8.542% | 39.64% | 0.0594%
CZ 6A | 63.81% | 76.93% | 0.1663% | 43.65% |  | 45.1% |  | 35.14% | [7 empty] | 8.542% | 41.47% | 3.429% | CZ 6A | 63.81% | 76.93% | 0.1663% | 45.29% |  | 45.1% |  | 35.14% | [7 empty] | 8.542% | 42.37% | 3.429% | CZ 6A | 63.81% | 76.93% | 0.1663% | 41.26% |  | 45.1% |  | 35.14% | [7 empty] | 8.542% | 40.94% | 3.429% | CZ 6A |  |  |  | 47.14% | [12 empty] | 47.14% | 3.429% | CZ 6A | 63.81% | 76.93% | 0.1663% | 43.83% |  | 45.1% |  | 35.14% | [7 empty] | 8.542% | 41.54% | 3.429%
CZ 6B | 63.75% | 76.72% | 0.1663% | 44.47% |  | 43.86% |  | 30.18% | [7 empty] | 8.542% | 40.72% | 0.5733% | CZ 6B | 63.75% | 76.72% | 0.1663% | 47.87% |  | 43.86% |  | 30.18% | [7 empty] | 8.542% | 42% | 0.5733% | CZ 6B | 63.75% | 76.72% | 0.1663% | 39.62% |  | 43.86% |  | 30.18% | [7 empty] | 8.542% | 40.02% | 0.5733% | CZ 6B |  |  |  | 51.79% | [12 empty] | 51.79% | 0.5733% | CZ 6B | 63.75% | 76.72% | 0.1663% | 44.84% |  | 43.86% |  | 30.18% | [7 empty] | 8.542% | 40.81% | 0.5733%
CZ 7 | 63.78% | 76.7% | 0.2769% | 46.9% |  | 47.53% |  | 40.07% | [7 empty] | 8.542% | 42.86% | 0.4129% | CZ 7 | 63.78% | 76.7% | 0.2769% | 48.73% |  | 47.53% |  | 40.07% | [7 empty] | 8.542% | 44.53% | 0.4129% | CZ 7 | 63.78% | 76.7% | 0.2769% | 42.78% |  | 47.53% |  | 40.07% | [7 empty] | 8.542% | 41.71% | 0.4129% | CZ 7 |  |  |  | 50.25% | [12 empty] | 50.25% | 0.4129% | CZ 7 | 63.78% | 76.7% | 0.2769% | 47.13% |  | 47.53% |  | 40.07% | [7 empty] | 8.542% | 42.99% | 0.4129%
CZ 8 | 62.87% | 74.91% | 0.5522% | 41.55% |  | 44.67% |  | 34.46% | [7 empty] | 8.542% | 40.41% | 0.02101% | CZ 8 | 62.87% | 74.91% | 0.5522% | 42.94% |  | 44.67% |  | 34.46% | [7 empty] | 8.542% | 41.43% | 0.02101% | CZ 8 | 62.87% | 74.91% | 0.5522% | 36.24% |  | 44.67% |  | 34.46% | [7 empty] | 8.542% | 39.58% | 0.02101% | CZ 8 |  |  |  | 43.86% | [12 empty] | 43.86% | 0.02101% | CZ 8 | 62.87% | 74.91% | 0.5522% | 41.74% |  | 44.67% |  | 34.46% | [7 empty] | 8.542% | 40.49% | 0.02101%
US Weighted | 63.6% | 77.07% | 0.1668% | 38.85% | 0% | 48.33% | 0% | 34.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 41.96% | 100% | US Weighted | 63.6% | 77.07% | 0.1668% | 39.7% | 0% | 48.33% | 0% | 34.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 42.14% | 100% | US Weighted | 63.6% | 77.07% | 0.1668% | 38.17% | 0% | 48.33% | 0% | 34.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 270.4% | 100% | US Weighted | 0% | 0% | 0% | 53.66% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 53.66% | 100% | US Weighted | 63.6% | 77.07% | 0.1668% | 38.92% | 0% | 48.33% | 0% | 34.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.542% | 41.97% | 100%

## OffM
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Medium Office |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 53628 |  | Building Type: | Medium Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 |  | Building Type: | Medium Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Medium Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Medium Office | [14 empty] | Prototype Floor Area: | 53628 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.13597 | 0.025854 | 0.013955 | 0.05761 | 0 | 0.15767 | 0 | 0.039715 | 5.2186e-05 | 8.2614e-05 | 0 | 0.09109 | 0.0064454 | 0 | 0 | 0.32202 | 0.85045 |  | STD2019 | 4.3642 | 0.82984 | 1.4239 | 3.2402 | 0 | 5.0607 | 0 | 1.2748 | 0.0016751 | 0.0026517 | 0 | 2.9238 | 0.20688 | 0 | 0 | 10.3361 | 29.6648 |  | STD2019 | 1.2791 | 0.24321 | 0 | 0.35486 | 0 | 1.4832 | 0 | 0.37362 | 0.00049093 | 0.00077718 | 0 | 0.85692 | 0.060634 | 0 | 0 | 3.0293 | 7.6821 |  | STD2019 | 0 | 0 | 0.014239 | 0.020294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034533 |  | STD2019 | 13.3907 | 2.5462 | 1.5564 | 5.9332 | 0 | 15.5278 | 0 | 3.9114 | 0.0051396 | 0.0081363 | 0 | 8.9711 | 0.63478 | 0 | 0 | 31.7141 | 84.1988
STD2016 | 0.16727 | 0.025854 | 0.013956 | 0.06332 | 0 | 0.16034 | 0 | 0.042075 | 0.0013565 | 8.2614e-05 | 0 | 0.09109 | 0.0064807 | 0 | 0 | 0.32202 | 0.89385 |  | STD2016 | 5.3691 | 0.82984 | 1.424 | 3.1458 | 0 | 5.1466 | 0 | 1.3505 | 0.04354 | 0.0026517 | 0 | 2.9238 | 0.20802 | 0 | 0 | 10.3361 | 30.7801 |  | STD2016 | 1.5736 | 0.24321 | 0 | 0.44592 | 0 | 1.5084 | 0 | 0.39582 | 0.012761 | 0.00077718 | 0 | 0.85692 | 0.060966 | 0 | 0 | 3.0293 | 8.1277 |  | STD2016 | 0 | 0 | 0.01424 | 0.016243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030483 |  | STD2016 | 16.4741 | 2.5462 | 1.5565 | 6.4437 | 0 | 15.7914 | 0 | 4.1438 | 0.13359 | 0.0081363 | 0 | 8.9711 | 0.63826 | 0 | 0 | 31.7141 | 88.4208
STD2013 | 0.18078 | 0.056746 | 0.014262 | 0.066723 | 0 | 0.16376 | 0 | 0.043044 | 0.001276 | 8.2614e-05 | 0 | 0.09109 | 0.0093959 | 0 | 0 | 0.32202 | 0.94918 |  | STD2013 | 5.8026 | 1.8214 | 1.4553 | 3.2507 | 0 | 5.2565 | 0 | 1.3816 | 0.040957 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 32.5732 |  | STD2013 | 1.7006 | 0.53383 | 0 | 0.47852 | 0 | 1.5406 | 0 | 0.40493 | 0.012004 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.6459 |  | STD2013 | 0 | 0 | 0.014553 | 0.01618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030733 |  | STD2013 | 17.8041 | 5.5887 | 1.5907 | 6.7781 | 0 | 16.1283 | 0 | 4.2392 | 0.12567 | 0.0081363 | 0 | 8.9711 | 0.92536 | 0 | 0 | 31.7141 | 93.8734
STD2010 | 0.20518 | 0.056746 | 0.014267 | 0.087912 | 0 | 0.18463 | 0 | 0.044822 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.009576 | 0 | 0 | 0.32596 | 1.0205 |  | STD2010 | 6.5859 | 1.8214 | 1.4558 | 4.0011 | 0 | 5.9262 | 0 | 1.4387 | 0 | 0.0026517 | 0 | 2.9318 | 0.30737 | 0 | 0 | 10.4627 | 34.9336 |  | STD2010 | 1.9302 | 0.53383 | 0 | 0.6684 | 0 | 1.7369 | 0 | 0.42165 | 0 | 0.00077718 | 0 | 0.85925 | 0.090085 | 0 | 0 | 3.0664 | 9.3075 |  | STD2010 | 0 | 0 | 0.014558 | 0.017205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031763 |  | STD2010 | 20.2073 | 5.5887 | 1.5912 | 8.878 | 0 | 18.1834 | 0 | 4.4143 | 0 | 0.0081363 | 0 | 8.9955 | 0.94309 | 0 | 0 | 32.1025 | 100.912
STD2007 | 0.30444 | 0.12408 | 0.014607 | 0.14204 | 0 | 0.25174 | 0 | 0.053007 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3581 |  | STD2007 | 9.772 | 3.9826 | 1.4905 | 6.0967 | 0 | 8.0804 | 0 | 1.7014 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 46.1526 |  | STD2007 | 2.864 | 1.1672 | 0 | 1.1295 | 0 | 2.3682 | 0 | 0.49865 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.4324 |  | STD2007 | 0 | 0 | 0.014905 | 0.022429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037334 |  | STD2007 | 29.9833 | 12.2196 | 1.6291 | 14.276 | 0 | 24.793 | 0 | 5.2204 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 134.2351
STD2004 | 0.30444 | 0.12408 | 0.014609 | 0.19525 | 0 | 0.26654 | 0 | 0.062225 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.4354 |  | STD2004 | 9.772 | 3.9826 | 1.4908 | 8.5074 | 0 | 8.5552 | 0 | 1.9973 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 49.3343 |  | STD2004 | 2.864 | 1.1672 | 0 | 1.5355 | 0 | 2.5074 | 0 | 0.58537 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.0643 |  | STD2004 | 0 | 0 | 0.014908 | 0.032682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04759 |  | STD2004 | 29.9833 | 12.2196 | 1.6294 | 19.6474 | 0 | 26.2499 | 0 | 6.1283 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 141.9715
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 2.3942e-06 | 0.05321 | 0 | 0.014792 | 0 | 0.0092185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077223 |  | 2004-2007 | 0 | 0 | 0.00024431 | 2.4107 | 0 | 0.4748 | 0 | 0.29589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1817 |  | 2004-2007 | 0 | 0 | 0 | 0.40603 | 0 | 0.13916 | 0 | 0.086722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63191 |  | 2004-2007 | 0 | 0 | 2.4431e-06 | 0.010253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010256 |  | 2004-2007 | 0 | 0 | 0.00026703 | 5.3715 | 0 | 1.4568 | 0 | 0.90789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7364
2007-2010 | 0.099263 | 0.067329 | 0.00033974 | 0.054132 | 0 | 0.067113 | 0 | 0.0081848 | 0 | 0 | 0 | 0.0050229 | 0.0090177 | 0 | 0 | 0.02723 | 0.33763 |  | 2007-2010 | 3.1861 | 2.1611 | 0.034668 | 2.0956 | 0 | 2.1542 | 0 | 0.26272 | 0 | 0 | 0 | 0.16123 | 0.28945 | 0 | 0 | 0.87401 | 11.2191 |  | 2007-2010 | 0.9338 | 0.63339 | 0 | 0.46108 | 0 | 0.63136 | 0 | 0.076998 | 0 | 0 | 0 | 0.047252 | 0.084832 | 0 | 0 | 0.25616 | 3.1249 |  | 2007-2010 | 0 | 0 | 0.00034668 | 0.0052237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055704 |  | 2007-2010 | 9.776 | 6.631 | 0.037892 | 5.398 | 0 | 6.6097 | 0 | 0.80609 | 0 | 0 | 0 | 0.49469 | 0.88811 | 0 | 0 | 2.6817 | 33.3231
2010-2013 | 0.024402 | 0 | 5.0147e-06 | 0.021189 | 0 | 0.020866 | 0 | 0.0017776 | -0.001276 | 0 | 0 | 0.00024784 | 0.00018004 | 0 | 0 | 0.0039434 | 0.071335 |  | 2010-2013 | 0.78324 | 0 | 0.00051171 | 0.75038 | 0 | 0.66976 | 0 | 0.057057 | -0.040957 | 0 | 0 | 0.0079552 | 0.0057788 | 0 | 0 | 0.12658 | 2.3603 |  | 2010-2013 | 0.22955 | 0 | 0 | 0.18988 | 0 | 0.1963 | 0 | 0.016722 | -0.012004 | 0 | 0 | 0.0023315 | 0.0016937 | 0 | 0 | 0.037097 | 0.66157 |  | 2010-2013 | 0 | 0 | 5.1171e-06 | 0.0010252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010303 |  | 2010-2013 | 2.4032 | 0 | 0.0005593 | 2.0999 | 0 | 2.055 | 0 | 0.17507 | -0.12567 | 0 | 0 | 0.024409 | 0.017731 | 0 | 0 | 0.38837 | 7.0386
2013-2016 | 0.013505 | 0.030892 | 0.00030657 | 0.0034035 | 0 | 0.0034215 | 0 | 0.00096885 | -8.0474e-05 | 0 | 0 | 0 | 0.0029152 | 0 | 0 | 0 | 0.055332 |  | 2013-2016 | 0.43347 | 0.99158 | 0.031283 | 0.10493 | 0 | 0.10982 | 0 | 0.031098 | -0.002583 | 0 | 0 | 0 | 0.093573 | 0 | 0 | 0 | 1.7932 |  | 2013-2016 | 0.12704 | 0.29062 | 0 | 0.032599 | 0 | 0.032188 | 0 | 0.0091143 | -0.00075704 | 0 | 0 | 0 | 0.027425 | 0 | 0 | 0 | 0.51823 |  | 2013-2016 | 0 | 0 | 0.00031283 | -6.2961e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00024986 |  | 2013-2016 | 1.33 | 3.0425 | 0.034192 | 0.33439 | 0 | 0.33697 | 0 | 0.095418 | -0.0079255 | 0 | 0 | 0 | 0.28711 | 0 | 0 | 0 | 5.4526
2016-2019 | 0.031308 | 0 | 9.7574e-07 | 0.0057098 | 0 | 0.0026767 | 0 | 0.0023598 | 0.0013043 | 0 | 0 | 0 | 3.5335e-05 | 0 | 0 | 0 | 0.043395 |  | 2016-2019 | 1.0049 | 0 | 9.9565e-05 | -0.094405 | 0 | 0.085916 | 0 | 0.075745 | 0.041865 | 0 | 0 | 0 | 0.0011342 | 0 | 0 | 0 | 1.1153 |  | 2016-2019 | 0.29453 | 0 | 0 | 0.091062 | 0 | 0.025181 | 0 | 0.0222 | 0.01227 | 0 | 0 | 0 | 0.0003324 | 0 | 0 | 0 | 0.44557 |  | 2016-2019 | 0 | 0 | 9.9565e-07 | -0.0040511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0040501 |  | 2016-2019 | 3.0834 | 0 | 0.00010883 | 0.51054 | 0 | 0.26362 | 0 | 0.23241 | 0.12845 | 0 | 0 | 0 | 0.0034799 | 0 | 0 | 0 | 4.222
2004-2019 | 0.16848 | 0.098222 | 0.0006547 | 0.13764 | 0 | 0.10887 | 0 | 0.02251 | -5.2186e-05 | 0 | 0 | 0.0052708 | 0.012148 | 0 | 0 | 0.031173 | 0.58492 |  | 2004-2019 | 5.4078 | 3.1527 | 0.066806 | 5.2672 | 0 | 3.4945 | 0 | 0.72251 | -0.0016751 | 0 | 0 | 0.16918 | 0.38993 | 0 | 0 | 1.0006 | 19.6695 |  | 2004-2019 | 1.5849 | 0.92401 | 0 | 1.1807 | 0 | 1.0242 | 0 | 0.21176 | -0.00049093 | 0 | 0 | 0.049584 | 0.11428 | 0 | 0 | 0.29326 | 5.3821 |  | 2004-2019 | 0 | 0 | 0.00066806 | 0.012388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013056 |  | 2004-2019 | 16.5926 | 9.6734 | 0.073019 | 13.7143 | 0 | 10.7221 | 0 | 2.2169 | -0.0051396 | 0 | 0 | 0.51909 | 1.1964 | 0 | 0 | 3.0701 | 57.7727
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.01639% | 27.25% |  | 5.55% |  | 14.81% |  | 0% |  | 0% | 0% |  |  | 0% | 5.38% |  | 2004-2007 | 0% | 0% | 0.01639% | 28.34% |  | 5.55% |  | 14.81% |  | 0% |  | 0% | 0% |  |  | 0% | 6.449% |  | 2004-2007 | 0% | 0% |  | 26.44% |  | 5.55% |  | 14.81% |  | 0% |  | 0% | 0% |  |  | 0% | 4.837% |  | 2004-2007 |  |  | 0.01639% | 31.37% | [12 empty] | 21.55% |  | 2004-2007 | 0% | 0% | 0.01639% | 27.34% |  | 5.55% |  | 14.81% |  | 0% |  | 0% | 0% |  |  | 0% | 5.449%
2007-2010 | 32.6% | 54.26% | 2.326% | 38.11% |  | 26.66% |  | 15.44% |  | 0% |  | 5.213% | 48.5% |  |  | 7.71% | 24.86% |  | 2007-2010 | 32.6% | 54.26% | 2.326% | 34.37% |  | 26.66% |  | 15.44% |  | 0% |  | 5.213% | 48.5% |  |  | 7.71% | 24.31% |  | 2007-2010 | 32.6% | 54.26% |  | 40.82% |  | 26.66% |  | 15.44% |  | 0% |  | 5.213% | 48.5% |  |  | 7.71% | 25.13% |  | 2007-2010 |  |  | 2.326% | 23.29% | [12 empty] | 14.92% |  | 2007-2010 | 32.6% | 54.26% | 2.326% | 37.81% |  | 26.66% |  | 15.44% |  | 0% |  | 5.213% | 48.5% |  |  | 7.71% | 24.82%
2010-2013 | 11.89% | 0% | 0.03515% | 24.1% |  | 11.3% |  | 3.966% |  | 0% |  | 0.2713% | 1.88% |  |  | 1.21% | 6.99% |  | 2010-2013 | 11.89% | 0% | 0.03515% | 18.75% |  | 11.3% |  | 3.966% |  | 0% |  | 0.2713% | 1.88% |  |  | 1.21% | 6.757% |  | 2010-2013 | 11.89% | 0% |  | 28.41% |  | 11.3% |  | 3.966% |  | 0% |  | 0.2713% | 1.88% |  |  | 1.21% | 7.108% |  | 2010-2013 |  |  | 0.03515% | 5.958% | [12 empty] | 3.244% |  | 2010-2013 | 11.89% | 0% | 0.03515% | 23.65% |  | 11.3% |  | 3.966% |  | 0% |  | 0.2713% | 1.88% |  |  | 1.21% | 6.975%
2013-2016 | 7.47% | 54.44% | 2.15% | 5.101% |  | 2.089% |  | 2.251% | -6.307% | 0% |  | 0% | 31.03% |  |  | 0% | 5.829% |  | 2013-2016 | 7.47% | 54.44% | 2.15% | 3.228% |  | 2.089% |  | 2.251% | -6.307% | 0% |  | 0% | 31.03% |  |  | 0% | 5.505% |  | 2013-2016 | 7.47% | 54.44% |  | 6.812% |  | 2.089% |  | 2.251% | -6.307% | 0% |  | 0% | 31.03% |  |  | 0% | 5.994% |  | 2013-2016 |  |  | 2.15% | -0.3891% | [12 empty] | 0.813% |  | 2013-2016 | 7.47% | 54.44% | 2.15% | 4.933% |  | 2.089% |  | 2.251% | -6.307% | 0% |  | 0% | 31.03% |  |  | 0% | 5.808%
2016-2019 | 18.72% | 0% | 0.006992% | 9.017% |  | 1.669% |  | 5.609% | 96.15% | 0% |  | 0% | 0.5452% |  |  | 0% | 4.855% |  | 2016-2019 | 18.72% | 0% | 0.006992% | -3.001% |  | 1.669% |  | 5.609% | 96.15% | 0% |  | 0% | 0.5452% |  |  | 0% | 3.623% |  | 2016-2019 | 18.72% | 0% |  | 20.42% |  | 1.669% |  | 5.609% | 96.15% | 0% |  | 0% | 0.5452% |  |  | 0% | 5.482% |  | 2016-2019 |  |  | 0.006992% | -24.94% | [12 empty] | -13.29% |  | 2016-2019 | 18.72% | 0% | 0.006992% | 7.923% |  | 1.669% |  | 5.609% | 96.15% | 0% |  | 0% | 0.5452% |  |  | 0% | 4.775%
2004-2019 | 55.34% | 79.16% | 4.481% | 70.49% |  | 40.85% |  | 36.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 40.75% |  | 2004-2019 | 55.34% | 79.16% | 4.481% | 61.91% |  | 40.85% |  | 36.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.87% |  | 2004-2019 | 55.34% | 79.16% |  | 76.89% |  | 40.85% |  | 36.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 41.2% |  | 2004-2019 |  |  | 4.481% | 37.91% | [12 empty] | 27.44% |  | 2004-2019 | 55.34% | 79.16% | 4.481% | 69.8% |  | 40.85% |  | 36.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 40.69%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.13531 | 0.025109 | 0.011206 | 0 | 0 | 0.52055 | 0 | 0.064439 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 1.1762 | 0% | CZ 0A | 4.3432 | 0.80595 | 1.1435 | 0 | 0 | 16.7084 | 0 | 2.0684 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 38.5387 | 0% | CZ 0A | 1.2729 | 0.23621 | 0 | 0 | 0 | 4.8969 | 0 | 0.6062 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 10.9599 | 0% | CZ 0A | 0 | 0 | 0.011435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011435 | 0% | CZ 0A | 13.3261 | 2.4729 | 1.2498 | 0 | 0 | 51.2661 | 0 | 6.3463 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 115.9892 | 0%
CZ 0B | 0.13548 | 0.025643 | 0.011238 | 0.0002148 | 0 | 0.47984 | 0 | 0.05805 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 1.1301 | 0% | CZ 0B | 4.3485 | 0.8231 | 1.1467 | 0.0068945 | 0 | 15.4018 | 0 | 1.8633 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 37.0596 | 0% | CZ 0B | 1.2745 | 0.24124 | 0 | 0.0020207 | 0 | 4.514 | 0 | 0.5461 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 10.5255 | 0% | CZ 0B | 0 | 0 | 0.011467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011467 | 0% | CZ 0B | 13.3424 | 2.5255 | 1.2533 | 0.021154 | 0 | 47.2571 | 0 | 5.7171 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 111.4445 | 0%
CZ 1A | 0.13577 | 0.025781 | 0.011726 | 5.5076e-06 | 0 | 0.35191 | 0 | 0.054096 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.99893 | 2.823% | CZ 1A | 4.358 | 0.82752 | 1.1965 | 0.00017678 | 0 | 11.2957 | 0 | 1.7364 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 32.8837 | 2.823% | CZ 1A | 1.2773 | 0.24253 | 0 | 5.1812e-05 | 0 | 3.3106 | 0 | 0.5089 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 9.287 | 2.823% | CZ 1A | 0 | 0 | 0.011965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011965 | 2.823% | CZ 1A | 13.3717 | 2.5391 | 1.3078 | 0.00054242 | 0 | 34.6584 | 0 | 5.3276 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 98.533 | 2.823%
CZ 1B | 0.13582 | 0.025687 | 0.011783 | 0.0022776 | 0 | 0.38636 | 0 | 0.053694 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 1.0353 | 0% | CZ 1B | 4.3596 | 0.82451 | 1.2024 | 0.10182 | 0 | 12.4014 | 0 | 1.7234 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 34.0826 | 0% | CZ 1B | 1.2777 | 0.24165 | 0 | 0.017564 | 0 | 3.6347 | 0 | 0.50511 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 9.6244 | 0% | CZ 1B | 0 | 0 | 0.012024 | 0.00041887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012442 | 0% | CZ 1B | 13.3766 | 2.5298 | 1.3142 | 0.22966 | 0 | 38.0512 | 0 | 5.288 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 102.1174 | 0%
CZ 2A | 0.13555 | 0.025798 | 0.012382 | 0.0039015 | 0 | 0.30197 | 0 | 0.045118 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.94435 | 15.52% | CZ 2A | 4.3508 | 0.82805 | 1.2635 | 0.16775 | 0 | 9.6924 | 0 | 1.4482 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 31.2201 | 15.52% | CZ 2A | 1.2751 | 0.24269 | 0 | 0.030983 | 0 | 2.8407 | 0 | 0.42444 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 8.7616 | 15.52% | CZ 2A | 0 | 0 | 0.012635 | 0.00062035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013255 | 15.52% | CZ 2A | 13.3495 | 2.5407 | 1.381 | 0.39217 | 0 | 29.7392 | 0 | 4.4435 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 93.1739 | 15.52%
CZ 2B | 0.13569 | 0.025803 | 0.012426 | 0.0037748 | 0 | 0.23856 | 0 | 0.053181 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.88907 | 3.865% | CZ 2B | 4.3554 | 0.82822 | 1.2679 | 0.24727 | 0 | 7.6573 | 0 | 1.707 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 29.5325 | 3.865% | CZ 2B | 1.2765 | 0.24274 | 0 | 0.018549 | 0 | 2.2442 | 0 | 0.5003 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 8.23 | 3.865% | CZ 2B | 0 | 0 | 0.012679 | 0.0018399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014519 | 3.865% | CZ 2B | 13.3636 | 2.5412 | 1.3858 | 0.39528 | 0 | 23.4949 | 0 | 5.2376 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 87.7463 | 3.865%
CZ 3A | 0.13608 | 0.026045 | 0.013532 | 0.043275 | 0 | 0.17516 | 0 | 0.036675 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.8504 | 14.49% | CZ 3A | 4.3679 | 0.836 | 1.3809 | 1.9435 | 0 | 5.6222 | 0 | 1.1772 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 28.7971 | 14.49% | CZ 3A | 1.2802 | 0.24502 | 0 | 0.33253 | 0 | 1.6478 | 0 | 0.34502 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 7.7982 | 14.49% | CZ 3A | 0 | 0 | 0.013809 | 0.0080894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021898 | 14.49% | CZ 3A | 13.4021 | 2.5651 | 1.5093 | 4.3654 | 0 | 17.2505 | 0 | 3.612 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 84.0323 | 14.49%
CZ 3B | 0.13577 | 0.025544 | 0.013233 | 0.012271 | 0 | 0.16813 | 0 | 0.047861 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.82244 | 8.895% | CZ 3B | 4.3579 | 0.81992 | 1.3503 | 0.87119 | 0 | 5.3966 | 0 | 1.5362 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 27.8015 | 8.895% | CZ 3B | 1.2772 | 0.2403 | 0 | 0.051242 | 0 | 1.5817 | 0 | 0.45025 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 7.5483 | 8.895% | CZ 3B | 0 | 0 | 0.013503 | 0.0069635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020466 | 8.895% | CZ 3B | 13.3712 | 2.5157 | 1.4759 | 1.2976 | 0 | 16.5584 | 0 | 4.7136 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 81.2603 | 8.895%
CZ 3C | 0.13604 | 0.025445 | 0.013652 | 0.002795 | 0 | 0.10659 | 0 | 0.034081 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.73823 | 3.286% | CZ 3C | 4.3665 | 0.81673 | 1.3931 | 0.17233 | 0 | 3.4213 | 0 | 1.0939 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 24.7332 | 3.286% | CZ 3C | 1.2798 | 0.23937 | 0 | 0.015181 | 0 | 1.0027 | 0 | 0.32061 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 6.8053 | 3.286% | CZ 3C | 0 | 0 | 0.013931 | 0.0012054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015136 | 3.286% | CZ 3C | 13.3977 | 2.506 | 1.5226 | 0.29067 | 0 | 10.4974 | 0 | 3.3565 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 72.8988 | 3.286%
CZ 4A | 0.1362 | 0.025781 | 0.014454 | 0.073732 | 0 | 0.11999 | 0 | 0.035524 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064494 | 0 | 0 | 0.32202 | 0.82532 | 18.98% | CZ 4A | 4.3716 | 0.82752 | 1.4749 | 4.2736 | 0 | 3.8516 | 0 | 1.1402 | 0 | 0.0026517 | 0 | 2.9238 | 0.20701 | 0 | 0 | 10.3361 | 29.409 | 18.98% | CZ 4A | 1.2813 | 0.24253 | 0 | 0.43714 | 0 | 1.1288 | 0 | 0.33419 | 0 | 0.00077718 | 0 | 0.85692 | 0.060672 | 0 | 0 | 3.0293 | 7.3716 | 18.98% | CZ 4A | 0 | 0 | 0.014749 | 0.027821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042569 | 18.98% | CZ 4A | 13.4135 | 2.5391 | 1.6121 | 7.6172 | 0 | 11.8177 | 0 | 3.4986 | 0 | 0.0081363 | 0 | 8.9711 | 0.63517 | 0 | 0 | 31.7141 | 81.8265 | 18.98%
CZ 4B | 0.13547 | 0.02561 | 0.014185 | 0.021146 | 0 | 0.12037 | 0 | 0.049541 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.78596 | 0.5078% | CZ 4B | 4.3483 | 0.82204 | 1.4475 | 1.5441 | 0 | 3.8637 | 0 | 1.5902 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 27.0852 | 0.5078% | CZ 4B | 1.2744 | 0.24093 | 0 | 0.082536 | 0 | 1.1324 | 0 | 0.46605 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 7.144 | 0.5078% | CZ 4B | 0 | 0 | 0.014475 | 0.012624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027099 | 0.5078% | CZ 4B | 13.3419 | 2.5222 | 1.5821 | 2.2439 | 0 | 11.8551 | 0 | 4.8791 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 77.7522 | 0.5078%
CZ 4C | 0.13687 | 0.026189 | 0.014738 | 0.044266 | 0 | 0.04514 | 0 | 0.031333 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064494 | 0 | 0 | 0.32202 | 0.71818 | 3.396% | CZ 4C | 4.3932 | 0.8406 | 1.5039 | 2.5334 | 0 | 1.4489 | 0 | 1.0057 | 0 | 0.0026517 | 0 | 2.9238 | 0.20701 | 0 | 0 | 10.3361 | 25.1953 | 3.396% | CZ 4C | 1.2876 | 0.24637 | 0 | 0.26678 | 0 | 0.42465 | 0 | 0.29476 | 0 | 0.00077718 | 0 | 0.85692 | 0.060672 | 0 | 0 | 3.0293 | 6.4678 | 3.396% | CZ 4C | 0 | 0 | 0.015039 | 0.016232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03127 | 3.396% | CZ 4C | 13.4796 | 2.5792 | 1.6437 | 4.567 | 0 | 4.4457 | 0 | 3.0858 | 0 | 0.0081363 | 0 | 8.9711 | 0.63517 | 0 | 0 | 31.7141 | 71.1296 | 3.396%
CZ 5A | 0.13597 | 0.025996 | 0.015242 | 0.12741 | 0 | 0.078004 | 0 | 0.033905 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.83616 | 17.55% | CZ 5A | 4.3642 | 0.83441 | 1.5553 | 7.2393 | 0 | 2.5038 | 0 | 1.0883 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 31.0547 | 17.55% | CZ 5A | 1.2791 | 0.24455 | 0 | 0.775 | 0 | 0.73381 | 0 | 0.31895 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 7.299 | 17.55% | CZ 5A | 0 | 0 | 0.015553 | 0.04595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061503 | 17.55% | CZ 5A | 13.3907 | 2.5602 | 1.6999 | 13.1359 | 0 | 7.6823 | 0 | 3.3391 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 83.1361 | 17.55%
CZ 5B | 0.13591 | 0.025759 | 0.015013 | 0.058162 | 0 | 0.090908 | 0 | 0.045328 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064439 | 0 | 0 | 0.32202 | 0.79071 | 6.239% | CZ 5B | 4.3623 | 0.82681 | 1.532 | 3.7222 | 0 | 2.918 | 0 | 1.4549 | 0 | 0.0026517 | 0 | 2.9238 | 0.20684 | 0 | 0 | 10.3361 | 28.2855 | 6.239% | CZ 5B | 1.2785 | 0.24232 | 0 | 0.29761 | 0 | 0.85521 | 0 | 0.42641 | 0 | 0.00077718 | 0 | 0.85692 | 0.06062 | 0 | 0 | 3.0293 | 7.0477 | 6.239% | CZ 5B | 0 | 0 | 0.01532 | 0.027068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042387 | 6.239% | CZ 5B | 13.3847 | 2.5369 | 1.6744 | 6.0741 | 0 | 8.9532 | 0 | 4.4641 | 0 | 0.0081363 | 0 | 8.9711 | 0.63463 | 0 | 0 | 31.7141 | 78.4154 | 6.239%
CZ 5C | 0.13699 | 0.026249 | 0.015183 | 0.04481 | 0 | 0.025902 | 0 | 0.031906 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064494 | 0 | 0 | 0.32202 | 0.70068 | 0.04746% | CZ 5C | 4.3971 | 0.84254 | 1.5493 | 2.8817 | 0 | 0.83141 | 0 | 1.0241 | 0 | 0.0026517 | 0 | 2.9238 | 0.20701 | 0 | 0 | 10.3361 | 24.9957 | 0.04746% | CZ 5C | 1.2887 | 0.24694 | 0 | 0.2274 | 0 | 0.24367 | 0 | 0.30015 | 0 | 0.00077718 | 0 | 0.85692 | 0.060672 | 0 | 0 | 3.0293 | 6.2546 | 0.04746% | CZ 5C | 0 | 0 | 0.015493 | 0.021058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036551 | 0.04746% | CZ 5C | 13.4916 | 2.5852 | 1.6934 | 4.6824 | 0 | 2.551 | 0 | 3.1422 | 0 | 0.0081363 | 0 | 8.9711 | 0.63517 | 0 | 0 | 31.7141 | 69.4742 | 0.04746%
CZ 6A | 0.13613 | 0.026001 | 0.015848 | 0.1897 | 0 | 0.085781 | 0 | 0.035563 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064494 | 0 | 0 | 0.32202 | 0.90866 | 3.432% | CZ 6A | 4.3695 | 0.83459 | 1.6172 | 10.702 | 0 | 2.7534 | 0 | 1.1415 | 0 | 0.0026517 | 0 | 2.9238 | 0.20701 | 0 | 0 | 10.3361 | 34.8877 | 3.432% | CZ 6A | 1.2806 | 0.2446 | 0 | 1.1641 | 0 | 0.80697 | 0 | 0.33455 | 0 | 0.00077718 | 0 | 0.85692 | 0.060672 | 0 | 0 | 3.0293 | 7.7785 | 3.432% | CZ 6A | 0 | 0 | 0.016172 | 0.067302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083474 | 3.432% | CZ 6A | 13.407 | 2.5608 | 1.7676 | 19.5427 | 0 | 8.4482 | 0 | 3.5024 | 0 | 0.0081363 | 0 | 8.9711 | 0.63517 | 0 | 0 | 31.7141 | 90.557 | 3.432%
CZ 6B | 0.13625 | 0.026277 | 0.015684 | 0.11622 | 0 | 0.058606 | 0 | 0.039214 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064494 | 0 | 0 | 0.32202 | 0.81189 | 0.5173% | CZ 6B | 4.3734 | 0.84343 | 1.6004 | 6.9096 | 0 | 1.8811 | 0 | 1.2587 | 0 | 0.0026517 | 0 | 2.9238 | 0.20701 | 0 | 0 | 10.3361 | 30.3362 | 0.5173% | CZ 6B | 1.2818 | 0.24719 | 0 | 0.66568 | 0 | 0.55133 | 0 | 0.3689 | 0 | 0.00077718 | 0 | 0.85692 | 0.060672 | 0 | 0 | 3.0293 | 7.0626 | 0.5173% | CZ 6B | 0 | 0 | 0.016004 | 0.046383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062387 | 0.5173% | CZ 6B | 13.4189 | 2.5879 | 1.7492 | 12.0387 | 0 | 5.7719 | 0 | 3.862 | 0 | 0.0081363 | 0 | 8.9711 | 0.63517 | 0 | 0 | 31.7141 | 80.7571 | 0.5173%
CZ 7 | 0.13631 | 0.026271 | 0.01656 | 0.14272 | 0 | 0.064208 | 0 | 0.036279 | 0.011423 | 8.2614e-05 | 0 | 0.09109 | 0.0064494 | 0 | 0 | 0.32202 | 0.85341 | 0.4099% | CZ 7 | 4.3754 | 0.84325 | 1.6898 | 5.7713 | 0 | 2.0609 | 0 | 1.1645 | 0.36665 | 0.0026517 | 0 | 2.9238 | 0.20701 | 0 | 0 | 10.3361 | 29.7413 | 0.4099% | CZ 7 | 1.2823 | 0.24714 | 0 | 1.1825 | 0 | 0.60402 | 0 | 0.34128 | 0.10746 | 0.00077718 | 0 | 0.85692 | 0.060672 | 0 | 0 | 3.0293 | 7.7124 | 0.4099% | CZ 7 | 0 | 0 | 0.016898 | 0.017368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034266 | 0.4099% | CZ 7 | 13.4249 | 2.5873 | 1.847 | 14.2774 | 0 | 6.3235 | 0 | 3.5729 | 1.125 | 0.0081363 | 0 | 8.9711 | 0.63517 | 0 | 0 | 31.7141 | 84.4864 | 0.4099%
CZ 8 | 0.14124 | 0.028414 | 0.01753 | 0.20725 | 0 | 0.028766 | 0 | 0.037556 | 0.011665 | 8.2614e-05 | 0 | 0.09109 | 0.0064549 | 0 | 0 | 0.32202 | 0.89206 | 0.04597% | CZ 8 | 4.5334 | 0.91202 | 1.7888 | 9.1619 | 0 | 0.92333 | 0 | 1.2055 | 0.37442 | 0.0026517 | 0 | 2.9238 | 0.20719 | 0 | 0 | 10.3361 | 32.3691 | 0.04597% | CZ 8 | 1.3287 | 0.2673 | 0 | 1.6121 | 0 | 0.27061 | 0 | 0.35331 | 0.10974 | 0.00077718 | 0 | 0.85692 | 0.060724 | 0 | 0 | 3.0293 | 7.8895 | 0.04597% | CZ 8 | 0 | 0 | 0.017888 | 0.036613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054501 | 0.04597% | CZ 8 | 13.9098 | 2.7983 | 1.9551 | 20.8792 | 0 | 2.8331 | 0 | 3.6988 | 1.1488 | 0.0081363 | 0 | 8.9711 | 0.63571 | 0 | 0 | 31.7141 | 88.5521 | 0.04597%
US Weighted | 0.13597 | 0.025854 | 0.013955 | 0.05761 | 0 | 0.15767 | 0 | 0.039715 | 5.2186e-05 | 8.2614e-05 | 0 | 0.09109 | 0.0064454 | 0 | 0 | 0.32202 | 0.85045 | 100% | US Weighted | 4.3642 | 0.82984 | 1.4239 | 3.2402 | 0 | 5.0607 | 0 | 1.2748 | 0.0016751 | 0.0026517 | 0 | 2.9238 | 0.20688 | 0 | 0 | 10.3361 | 29.6648 | 100% | US Weighted | 1.2791 | 0.24321 | 0 | 0.35486 | 0 | 1.4832 | 0 | 0.37362 | 0.00049093 | 0.00077718 | 0 | 0.85692 | 0.060634 | 0 | 0 | 3.0293 | 7.6821 | 100% | US Weighted | 0 | 0 | 0.014239 | 0.020294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034533 | 100% | US Weighted | 13.3907 | 2.5462 | 1.5564 | 5.9332 | 0 | 15.5278 | 0 | 3.9114 | 0.0051396 | 0.0081363 | 0 | 8.9711 | 0.63478 | 0 | 0 | 31.7141 | 84.1988 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.16625 | 0.025109 | 0.011205 | 0 | 0 | 0.49225 | 0 | 0.063767 | 0.0094566 | 8.2614e-05 | 0 | 0.09109 | 0.0064769 | 0 | 0 | 0.32202 | 1.1877 | 0% | CZ 0A | 5.3363 | 0.80595 | 1.1433 | 0 | 0 | 15.8003 | 0 | 2.0468 | 0.30353 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 38.9066 | 0% | CZ 0A | 1.564 | 0.23621 | 0 | 0 | 0 | 4.6308 | 0 | 0.59988 | 0.088961 | 0.00077718 | 0 | 0.85692 | 0.060931 | 0 | 0 | 3.0293 | 11.0678 | 0% | CZ 0A | 0 | 0 | 0.011433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011433 | 0% | CZ 0A | 16.3734 | 2.4729 | 1.2497 | 0 | 0 | 48.4797 | 0 | 6.2801 | 0.93133 | 0.0081363 | 0 | 8.9711 | 0.63788 | 0 | 0 | 31.7141 | 117.1184 | 0%
CZ 0B | 0.16666 | 0.025643 | 0.011238 | 0.00028089 | 0 | 0.48589 | 0 | 0.057488 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064769 | 0 | 0 | 0.32202 | 1.1669 | 0% | CZ 0B | 5.3494 | 0.8231 | 1.1467 | 0.0090159 | 0 | 15.5961 | 0 | 1.8453 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 38.24 | 0% | CZ 0B | 1.5678 | 0.24124 | 0 | 0.0026424 | 0 | 4.5709 | 0 | 0.54081 | 0 | 0.00077718 | 0 | 0.85692 | 0.060931 | 0 | 0 | 3.0293 | 10.8714 | 0% | CZ 0B | 0 | 0 | 0.011467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011467 | 0% | CZ 0B | 16.4136 | 2.5255 | 1.2533 | 0.027663 | 0 | 47.8532 | 0 | 5.6618 | 0 | 0.0081363 | 0 | 8.9711 | 0.63788 | 0 | 0 | 31.7141 | 115.0663 | 0%
CZ 1A | 0.16675 | 0.025781 | 0.011726 | 1.1015e-05 | 0 | 0.35442 | 0 | 0.055704 | 0.0092473 | 8.2614e-05 | 0 | 0.09109 | 0.0064769 | 0 | 0 | 0.32202 | 1.0433 | 2.823% | CZ 1A | 5.3524 | 0.82752 | 1.1965 | 0.00035356 | 0 | 11.3761 | 0 | 1.788 | 0.29682 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 34.3082 | 2.823% | CZ 1A | 1.5687 | 0.24253 | 0 | 0.00010362 | 0 | 3.3341 | 0 | 0.52403 | 0.086992 | 0.00077718 | 0 | 0.85692 | 0.060931 | 0 | 0 | 3.0293 | 9.7045 | 2.823% | CZ 1A | 0 | 0 | 0.011965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011965 | 2.823% | CZ 1A | 16.4228 | 2.5391 | 1.3078 | 0.0010848 | 0 | 34.9052 | 0 | 5.486 | 0.91072 | 0.0081363 | 0 | 8.9711 | 0.63788 | 0 | 0 | 31.7141 | 102.9039 | 2.823%
CZ 1B | 0.16685 | 0.025687 | 0.011783 | 0.0029855 | 0 | 0.40422 | 0 | 0.05517 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064769 | 0 | 0 | 0.32202 | 1.0864 | 0% | CZ 1B | 5.3556 | 0.82451 | 1.2024 | 0.11897 | 0 | 12.9747 | 0 | 1.7708 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 35.7175 | 0% | CZ 1B | 1.5696 | 0.24165 | 0 | 0.024973 | 0 | 3.8027 | 0 | 0.519 | 0 | 0.00077718 | 0 | 0.85692 | 0.060931 | 0 | 0 | 3.0293 | 10.1059 | 0% | CZ 1B | 0 | 0 | 0.012024 | 0.00033757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012361 | 0% | CZ 1B | 16.4326 | 2.5298 | 1.3142 | 0.29834 | 0 | 39.8103 | 0 | 5.4334 | 0 | 0.0081363 | 0 | 8.9711 | 0.63788 | 0 | 0 | 31.7141 | 107.1498 | 0%
CZ 2A | 0.16678 | 0.025798 | 0.012384 | 0.0068769 | 0 | 0.29647 | 0 | 0.045999 | 0.0066807 | 8.2614e-05 | 0 | 0.09109 | 0.0064769 | 0 | 0 | 0.32202 | 0.98066 | 15.52% | CZ 2A | 5.3533 | 0.82805 | 1.2637 | 0.23176 | 0 | 9.516 | 0 | 1.4765 | 0.21444 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 32.3542 | 15.52% | CZ 2A | 1.569 | 0.24269 | 0 | 0.06321 | 0 | 2.789 | 0 | 0.43273 | 0.062848 | 0.00077718 | 0 | 0.85692 | 0.060931 | 0 | 0 | 3.0293 | 9.1074 | 15.52% | CZ 2A | 0 | 0 | 0.012637 | 0.00016083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012798 | 15.52% | CZ 2A | 16.4255 | 2.5407 | 1.3812 | 0.67933 | 0 | 29.1978 | 0 | 4.5303 | 0.65795 | 0.0081363 | 0 | 8.9711 | 0.63788 | 0 | 0 | 31.7141 | 96.744 | 15.52%
CZ 2B | 0.16705 | 0.025803 | 0.012426 | 0.0050567 | 0 | 0.2461 | 0 | 0.053517 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064769 | 0 | 0 | 0.32202 | 0.92961 | 3.865% | CZ 2B | 5.3618 | 0.82822 | 1.2679 | 0.22785 | 0 | 7.8992 | 0 | 1.7178 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 30.7732 | 3.865% | CZ 2B | 1.5715 | 0.24274 | 0 | 0.038755 | 0 | 2.3151 | 0 | 0.50346 | 0 | 0.00077718 | 0 | 0.85692 | 0.060931 | 0 | 0 | 3.0293 | 8.6195 | 3.865% | CZ 2B | 0 | 0 | 0.012679 | 0.00095616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013635 | 3.865% | CZ 2B | 16.4516 | 2.5412 | 1.3858 | 0.51024 | 0 | 24.2369 | 0 | 5.2707 | 0 | 0.0081363 | 0 | 8.9711 | 0.63788 | 0 | 0 | 31.7141 | 91.7276 | 3.865%
CZ 3A | 0.16776 | 0.026045 | 0.013534 | 0.052172 | 0 | 0.18177 | 0 | 0.038961 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.89992 | 14.49% | CZ 3A | 5.3846 | 0.836 | 1.381 | 2.0401 | 0 | 5.8345 | 0 | 1.2506 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 30.1975 | 14.49% | CZ 3A | 1.5781 | 0.24502 | 0 | 0.44164 | 0 | 1.71 | 0 | 0.36652 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 8.2893 | 14.49% | CZ 3A | 0 | 0 | 0.01381 | 0.0053322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019143 | 14.49% | CZ 3A | 16.5215 | 2.5651 | 1.5095 | 5.2064 | 0 | 17.902 | 0 | 3.8371 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 88.8733 | 14.49%
CZ 3B | 0.16701 | 0.025544 | 0.013233 | 0.013175 | 0 | 0.17168 | 0 | 0.048698 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064769 | 0 | 0 | 0.32202 | 0.85901 | 8.895% | CZ 3B | 5.3606 | 0.81992 | 1.3503 | 0.73071 | 0 | 5.5107 | 0 | 1.5631 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 28.8057 | 8.895% | CZ 3B | 1.5711 | 0.2403 | 0 | 0.082536 | 0 | 1.6151 | 0 | 0.45812 | 0 | 0.00077718 | 0 | 0.85692 | 0.060931 | 0 | 0 | 3.0293 | 7.9151 | 8.895% | CZ 3B | 0 | 0 | 0.013503 | 0.0044909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017994 | 8.895% | CZ 3B | 16.4478 | 2.5157 | 1.4759 | 1.3549 | 0 | 16.9083 | 0 | 4.7961 | 0 | 0.0081363 | 0 | 8.9711 | 0.63788 | 0 | 0 | 31.7141 | 84.8298 | 8.895%
CZ 3C | 0.16725 | 0.025445 | 0.013652 | 0.0029223 | 0 | 0.11332 | 0 | 0.035557 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.77782 | 3.286% | CZ 3C | 5.3683 | 0.81673 | 1.3931 | 0.13063 | 0 | 3.6373 | 0 | 1.1413 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 25.958 | 3.286% | CZ 3C | 1.5734 | 0.23937 | 0 | 0.022538 | 0 | 1.066 | 0 | 0.3345 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 7.1838 | 3.286% | CZ 3C | 0 | 0 | 0.013931 | 0.00053729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014468 | 3.286% | CZ 3C | 16.4716 | 2.506 | 1.5226 | 0.29468 | 0 | 11.1603 | 0 | 3.5019 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 76.7887 | 3.286%
CZ 4A | 0.16747 | 0.025781 | 0.014456 | 0.078405 | 0 | 0.12404 | 0 | 0.038922 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.86875 | 18.98% | CZ 4A | 5.3754 | 0.82752 | 1.4751 | 3.9962 | 0 | 3.9815 | 0 | 1.2493 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 30.3756 | 18.98% | CZ 4A | 1.5754 | 0.24253 | 0 | 0.53858 | 0 | 1.1669 | 0 | 0.36615 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 7.8376 | 18.98% | CZ 4A | 0 | 0 | 0.014751 | 0.021585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036336 | 18.98% | CZ 4A | 16.4933 | 2.5391 | 1.6122 | 7.9977 | 0 | 12.2163 | 0 | 3.8333 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 86.0237 | 18.98%
CZ 4B | 0.1664 | 0.02561 | 0.014187 | 0.022543 | 0 | 0.12287 | 0 | 0.050587 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064769 | 0 | 0 | 0.32202 | 0.82186 | 0.5078% | CZ 4B | 5.3409 | 0.82204 | 1.4477 | 1.2714 | 0 | 3.9438 | 0 | 1.6237 | 0 | 0.0026517 | 0 | 2.9238 | 0.2079 | 0 | 0 | 10.3361 | 27.9201 | 0.5078% | CZ 4B | 1.5653 | 0.24093 | 0 | 0.13839 | 0 | 1.1559 | 0 | 0.47589 | 0 | 0.00077718 | 0 | 0.85692 | 0.060931 | 0 | 0 | 3.0293 | 7.5244 | 0.5078% | CZ 4B | 0 | 0 | 0.014477 | 0.0079921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022469 | 0.5078% | CZ 4B | 16.3875 | 2.5222 | 1.5823 | 2.3223 | 0 | 12.1008 | 0 | 4.9821 | 0 | 0.0081363 | 0 | 8.9711 | 0.63788 | 0 | 0 | 31.7141 | 81.2286 | 0.5078%
CZ 4C | 0.16864 | 0.026189 | 0.014736 | 0.049445 | 0 | 0.046286 | 0 | 0.03412 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.75909 | 3.396% | CZ 4C | 5.4131 | 0.8406 | 1.5037 | 2.3184 | 0 | 1.4857 | 0 | 1.0952 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 26.1272 | 3.396% | CZ 4C | 1.5865 | 0.24637 | 0 | 0.36678 | 0 | 0.43543 | 0 | 0.32097 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 6.904 | 3.396% | CZ 4C | 0 | 0 | 0.015037 | 0.01067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025707 | 3.396% | CZ 4C | 16.6089 | 2.5792 | 1.6435 | 5.006 | 0 | 4.5585 | 0 | 3.3603 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 75.0881 | 3.396%
CZ 5A | 0.16722 | 0.025996 | 0.015242 | 0.13688 | 0 | 0.080989 | 0 | 0.037391 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.88339 | 17.55% | CZ 5A | 5.3673 | 0.83441 | 1.5553 | 7.0689 | 0 | 2.5996 | 0 | 1.2002 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 32.0963 | 17.55% | CZ 5A | 1.5731 | 0.24455 | 0 | 0.92785 | 0 | 0.76189 | 0 | 0.35175 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 7.8071 | 17.55% | CZ 5A | 0 | 0 | 0.015553 | 0.039031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054584 | 17.55% | CZ 5A | 16.4684 | 2.5602 | 1.6999 | 13.9797 | 0 | 7.9763 | 0 | 3.6825 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 87.6987 | 17.55%
CZ 5B | 0.16698 | 0.025759 | 0.015015 | 0.064956 | 0 | 0.092908 | 0 | 0.047663 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.83295 | 6.239% | CZ 5B | 5.3597 | 0.82681 | 1.5322 | 3.4975 | 0 | 2.9821 | 0 | 1.5299 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 29.1988 | 6.239% | CZ 5B | 1.5708 | 0.24232 | 0 | 0.42108 | 0 | 0.87401 | 0 | 0.44838 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 7.5046 | 6.239% | CZ 5B | 0 | 0 | 0.015322 | 0.020608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035929 | 6.239% | CZ 5B | 16.445 | 2.5369 | 1.6746 | 6.6607 | 0 | 9.1501 | 0 | 4.6941 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 82.4931 | 6.239%
CZ 5C | 0.16864 | 0.026249 | 0.015183 | 0.048965 | 0 | 0.027152 | 0 | 0.035293 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.74115 | 0.04746% | CZ 5C | 5.4129 | 0.84254 | 1.5493 | 2.5326 | 0 | 0.87154 | 0 | 1.1328 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 25.8123 | 0.04746% | CZ 5C | 1.5864 | 0.24694 | 0 | 0.33139 | 0 | 0.25543 | 0 | 0.33201 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 6.7002 | 0.04746% | CZ 5C | 0 | 0 | 0.015493 | 0.014019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029512 | 0.04746% | CZ 5C | 16.6083 | 2.5852 | 1.6934 | 5.0016 | 0 | 2.6741 | 0 | 3.4758 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 73.3701 | 0.04746%
CZ 6A | 0.16727 | 0.026001 | 0.01585 | 0.20409 | 0 | 0.090573 | 0 | 0.040139 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.9636 | 3.432% | CZ 6A | 5.369 | 0.83459 | 1.6173 | 10.6937 | 0 | 2.9072 | 0 | 1.2884 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 36.1808 | 3.432% | CZ 6A | 1.5736 | 0.2446 | 0 | 1.3627 | 0 | 0.85205 | 0 | 0.3776 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 8.3585 | 3.432% | CZ 6A | 0 | 0 | 0.016173 | 0.060441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076615 | 3.432% | CZ 6A | 16.4738 | 2.5608 | 1.7678 | 20.8724 | 0 | 8.9201 | 0 | 3.9531 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 95.8796 | 3.432%
CZ 6B | 0.16742 | 0.026277 | 0.015685 | 0.12665 | 0 | 0.061322 | 0 | 0.043978 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.861 | 0.5173% | CZ 6B | 5.3738 | 0.84343 | 1.6006 | 6.7129 | 0 | 1.9683 | 0 | 1.4116 | 0 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 31.3812 | 0.5173% | CZ 6B | 1.575 | 0.24719 | 0 | 0.83526 | 0 | 0.57687 | 0 | 0.41372 | 0 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 7.596 | 0.5173% | CZ 6B | 0 | 0 | 0.016006 | 0.03863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054635 | 0.5173% | CZ 6B | 16.4884 | 2.5879 | 1.7494 | 12.9666 | 0 | 6.0393 | 0 | 4.3312 | 0 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 85.4945 | 0.5173%
CZ 7 | 0.16732 | 0.026271 | 0.01656 | 0.16787 | 0 | 0.069864 | 0 | 0.041665 | 0.012822 | 8.2614e-05 | 0 | 0.09109 | 0.0064824 | 0 | 0 | 0.32202 | 0.92204 | 0.4099% | CZ 7 | 5.3706 | 0.84325 | 1.6898 | 6.3997 | 0 | 2.2425 | 0 | 1.3374 | 0.41155 | 0.0026517 | 0 | 2.9238 | 0.20807 | 0 | 0 | 10.3361 | 31.7654 | 0.4099% | CZ 7 | 1.574 | 0.24714 | 0 | 1.4431 | 0 | 0.65723 | 0 | 0.39196 | 0.12062 | 0.00077718 | 0 | 0.85692 | 0.060983 | 0 | 0 | 3.0293 | 8.3821 | 0.4099% | CZ 7 | 0 | 0 | 0.016898 | 0.014758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031656 | 0.4099% | CZ 7 | 16.4787 | 2.5873 | 1.847 | 16.721 | 0 | 6.8806 | 0 | 4.1034 | 1.2628 | 0.0081363 | 0 | 8.9711 | 0.63843 | 0 | 0 | 31.7141 | 91.2124 | 0.4099%
CZ 8 | 0.17368 | 0.028414 | 0.017532 | 0.24412 | 0 | 0.031906 | 0 | 0.043471 | 0.013406 | 8.2614e-05 | 0 | 0.09109 | 0.006488 | 0 | 0 | 0.32202 | 0.97221 | 0.04597% | CZ 8 | 5.5746 | 0.91202 | 1.789 | 10.1247 | 0 | 1.0241 | 0 | 1.3953 | 0.43029 | 0.0026517 | 0 | 2.9238 | 0.20825 | 0 | 0 | 10.3361 | 34.7209 | 0.04597% | CZ 8 | 1.6338 | 0.2673 | 0 | 1.9887 | 0 | 0.30015 | 0 | 0.40895 | 0.12611 | 0.00077718 | 0 | 0.85692 | 0.061034 | 0 | 0 | 3.0293 | 8.6731 | 0.04597% | CZ 8 | 0 | 0 | 0.01789 | 0.033393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051283 | 0.04597% | CZ 8 | 17.1046 | 2.7983 | 1.9553 | 24.4695 | 0 | 3.1422 | 0 | 4.2813 | 1.3202 | 0.0081363 | 0 | 8.9711 | 0.63897 | 0 | 0 | 31.7141 | 96.4039 | 0.04597%
US Weighted | 0.16727 | 0.025854 | 0.013956 | 0.06332 | 0 | 0.16034 | 0 | 0.042075 | 0.0013565 | 8.2614e-05 | 0 | 0.09109 | 0.0064807 | 0 | 0 | 0.32202 | 0.89385 | 100% | US Weighted | 5.3691 | 0.82984 | 1.424 | 3.1458 | 0 | 5.1466 | 0 | 1.3505 | 0.04354 | 0.0026517 | 0 | 2.9238 | 0.20802 | 0 | 0 | 10.3361 | 30.7801 | 100% | US Weighted | 1.5736 | 0.24321 | 0 | 0.44592 | 0 | 1.5084 | 0 | 0.39582 | 0.012761 | 0.00077718 | 0 | 0.85692 | 0.060966 | 0 | 0 | 3.0293 | 8.1277 | 100% | US Weighted | 0 | 0 | 0.01424 | 0.016243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030483 | 100% | US Weighted | 16.4741 | 2.5462 | 1.5565 | 6.4437 | 0 | 15.7914 | 0 | 4.1438 | 0.13359 | 0.0081363 | 0 | 8.9711 | 0.63826 | 0 | 0 | 31.7141 | 88.4208 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.17959 | 0.056789 | 0.011631 | 0 | 0 | 0.54172 | 0 | 0.06711 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0093905 | 0 | 0 | 0.32202 | 1.2794 | 0% | CZ 0A | 5.7643 | 1.8228 | 1.1868 | 0 | 0 | 17.3881 | 0 | 2.1541 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 41.8801 | 0% | CZ 0A | 1.6894 | 0.53423 | 0 | 0 | 0 | 5.0962 | 0 | 0.63133 | 0 | 0.00077718 | 0 | 0.85692 | 0.088339 | 0 | 0 | 3.0293 | 11.9265 | 0% | CZ 0A | 0 | 0 | 0.011868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011868 | 0% | CZ 0A | 17.6866 | 5.5929 | 1.2972 | 0 | 0 | 53.3517 | 0 | 6.6094 | 0 | 0.0081363 | 0 | 8.9711 | 0.92482 | 0 | 0 | 31.7141 | 126.1559 | 0%
CZ 0B | 0.17991 | 0.056772 | 0.011709 | 0.00028089 | 0 | 0.5036 | 0 | 0.059934 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0093905 | 0 | 0 | 0.32202 | 1.2348 | 0% | CZ 0B | 5.7748 | 1.8223 | 1.1948 | 0.0090159 | 0 | 16.1646 | 0 | 1.9237 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 40.4531 | 0% | CZ 0B | 1.6925 | 0.53408 | 0 | 0.0026424 | 0 | 4.7376 | 0 | 0.56382 | 0 | 0.00077718 | 0 | 0.85692 | 0.088339 | 0 | 0 | 3.0293 | 11.506 | 0% | CZ 0B | 0 | 0 | 0.011948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011948 | 0% | CZ 0B | 17.7186 | 5.5912 | 1.3059 | 0.027663 | 0 | 49.5977 | 0 | 5.9026 | 0 | 0.0081363 | 0 | 8.9711 | 0.92482 | 0 | 0 | 31.7141 | 121.7618 | 0%
CZ 1A | 0.18038 | 0.056783 | 0.012142 | 1.1015e-05 | 0 | 0.36379 | 0 | 0.056635 | 0.0092638 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 1.1016 | 2.823% | CZ 1A | 5.79 | 1.8226 | 1.2389 | 0.00035356 | 0 | 11.677 | 0 | 1.8179 | 0.29735 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 36.2082 | 2.823% | CZ 1A | 1.6969 | 0.53418 | 0 | 0.00010362 | 0 | 3.4223 | 0 | 0.53278 | 0.087148 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 10.2489 | 2.823% | CZ 1A | 0 | 0 | 0.012389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012389 | 2.823% | CZ 1A | 17.7653 | 5.5923 | 1.3542 | 0.0010848 | 0 | 35.8284 | 0 | 5.5777 | 0.91235 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 108.6499 | 2.823%
CZ 1B | 0.18047 | 0.056695 | 0.012187 | 0.0027696 | 0 | 0.40816 | 0 | 0.055957 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 1.1388 | 0% | CZ 1B | 5.7928 | 1.8198 | 1.2435 | 0.11119 | 0 | 13.1011 | 0 | 1.7961 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 37.4287 | 0% | CZ 1B | 1.6978 | 0.53335 | 0 | 0.023056 | 0 | 3.8397 | 0 | 0.52641 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 10.5957 | 0% | CZ 1B | 0 | 0 | 0.012435 | 0.0003252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012761 | 0% | CZ 1B | 17.774 | 5.5837 | 1.3592 | 0.27692 | 0 | 40.1981 | 0 | 5.511 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 112.3215 | 0%
CZ 2A | 0.18038 | 0.056673 | 0.012748 | 0.0071523 | 0 | 0.30357 | 0 | 0.046688 | 0.0061079 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 1.0359 | 15.52% | CZ 2A | 5.79 | 1.8191 | 1.3008 | 0.2406 | 0 | 9.7441 | 0 | 1.4986 | 0.19605 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 34.1533 | 15.52% | CZ 2A | 1.6969 | 0.53314 | 0 | 0.065801 | 0 | 2.8558 | 0 | 0.43921 | 0.057459 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 9.6238 | 15.52% | CZ 2A | 0 | 0 | 0.013008 | 0.00016083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013169 | 15.52% | CZ 2A | 17.7653 | 5.5815 | 1.4218 | 0.70645 | 0 | 29.8976 | 0 | 4.5981 | 0.60154 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 102.1909 | 15.52%
CZ 2B | 0.18066 | 0.056723 | 0.012789 | 0.0052156 | 0 | 0.24911 | 0 | 0.054255 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.98135 | 3.865% | CZ 2B | 5.7988 | 1.8207 | 1.305 | 0.23174 | 0 | 7.996 | 0 | 1.7415 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 32.4579 | 3.865% | CZ 2B | 1.6995 | 0.53361 | 0 | 0.040413 | 0 | 2.3435 | 0 | 0.5104 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 9.1029 | 3.865% | CZ 2B | 0 | 0 | 0.01305 | 0.00093849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013989 | 3.865% | CZ 2B | 17.7924 | 5.5864 | 1.4264 | 0.52566 | 0 | 24.5341 | 0 | 5.3434 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 96.827 | 3.865%
CZ 3A | 0.18139 | 0.056706 | 0.013842 | 0.056904 | 0 | 0.18329 | 0 | 0.039412 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.95414 | 14.49% | CZ 3A | 5.8223 | 1.8201 | 1.4125 | 2.2043 | 0 | 5.8833 | 0 | 1.2651 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 31.9718 | 14.49% | CZ 3A | 1.7064 | 0.53345 | 0 | 0.48449 | 0 | 1.7243 | 0 | 0.37077 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.7949 | 14.49% | CZ 3A | 0 | 0 | 0.014125 | 0.0055125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019637 | 14.49% | CZ 3A | 17.8646 | 5.5847 | 1.5439 | 5.6747 | 0 | 18.0517 | 0 | 3.8815 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 94.2197 | 14.49%
CZ 3B | 0.18063 | 0.056706 | 0.013557 | 0.014842 | 0 | 0.17367 | 0 | 0.049023 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.91101 | 8.895% | CZ 3B | 5.7979 | 1.8201 | 1.3833 | 0.78569 | 0 | 5.5743 | 0 | 1.5735 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 30.4991 | 8.895% | CZ 3B | 1.6993 | 0.53345 | 0 | 0.098028 | 0 | 1.6337 | 0 | 0.46118 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.4011 | 8.895% | CZ 3B | 0 | 0 | 0.013833 | 0.0045122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018346 | 8.895% | CZ 3B | 17.7897 | 5.5847 | 1.512 | 1.5194 | 0 | 17.1035 | 0 | 4.8281 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 89.9561 | 8.895%
CZ 3C | 0.18089 | 0.056805 | 0.013939 | 0.0032418 | 0 | 0.11389 | 0 | 0.035574 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.82693 | 3.286% | CZ 3C | 5.8062 | 1.8233 | 1.4224 | 0.14088 | 0 | 3.6557 | 0 | 1.1418 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 27.5545 | 3.286% | CZ 3C | 1.7017 | 0.53439 | 0 | 0.025543 | 0 | 1.0714 | 0 | 0.33465 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 7.6431 | 3.286% | CZ 3C | 0 | 0 | 0.014224 | 0.00053729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014761 | 3.286% | CZ 3C | 17.8152 | 5.5945 | 1.5547 | 0.32614 | 0 | 11.2167 | 0 | 3.5035 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 81.6293 | 3.286%
CZ 4A | 0.18078 | 0.056827 | 0.014735 | 0.079809 | 0 | 0.12872 | 0 | 0.04091 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.92437 | 18.98% | CZ 4A | 5.8027 | 1.824 | 1.5035 | 3.9992 | 0 | 4.1318 | 0 | 1.3131 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 32.1385 | 18.98% | CZ 4A | 1.7007 | 0.53459 | 0 | 0.55744 | 0 | 1.2109 | 0 | 0.38486 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.3639 | 18.98% | CZ 4A | 0 | 0 | 0.015035 | 0.020972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036007 | 18.98% | CZ 4A | 17.8043 | 5.5967 | 1.6433 | 8.1281 | 0 | 12.6774 | 0 | 4.0291 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 91.4976 | 18.98%
CZ 4B | 0.17975 | 0.056684 | 0.014473 | 0.022767 | 0 | 0.12873 | 0 | 0.053534 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.0093905 | 0 | 0 | 0.32202 | 0.87852 | 0.5078% | CZ 4B | 5.7696 | 1.8194 | 1.4768 | 1.2488 | 0 | 4.1319 | 0 | 1.7183 | 0 | 0.0026517 | 0 | 2.9238 | 0.30141 | 0 | 0 | 10.3361 | 29.7289 | 0.5078% | CZ 4B | 1.691 | 0.53325 | 0 | 0.1445 | 0 | 1.211 | 0 | 0.50361 | 0 | 0.00077718 | 0 | 0.85692 | 0.088339 | 0 | 0 | 3.0293 | 8.0587 | 0.5078% | CZ 4B | 0 | 0 | 0.014768 | 0.0075574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022326 | 0.5078% | CZ 4B | 17.7029 | 5.5826 | 1.6142 | 2.3388 | 0 | 12.6779 | 0 | 5.2723 | 0 | 0.0081363 | 0 | 8.9711 | 0.92482 | 0 | 0 | 31.7141 | 86.8069 | 0.5078%
CZ 4C | 0.18186 | 0.056822 | 0.01502 | 0.051685 | 0 | 0.048731 | 0 | 0.035843 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.81254 | 3.396% | CZ 4C | 5.8372 | 1.8239 | 1.5327 | 2.3529 | 0 | 1.5642 | 0 | 1.1505 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 27.8254 | 3.396% | CZ 4C | 1.7108 | 0.53454 | 0 | 0.39289 | 0 | 0.45843 | 0 | 0.33719 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 7.4093 | 3.396% | CZ 4C | 0 | 0 | 0.015327 | 0.010124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02545 | 3.396% | CZ 4C | 17.9101 | 5.5961 | 1.6752 | 5.2197 | 0 | 4.7993 | 0 | 3.5301 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 80.3492 | 3.396%
CZ 5A | 0.18065 | 0.056728 | 0.015521 | 0.14261 | 0 | 0.083038 | 0 | 0.038349 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.93948 | 17.55% | CZ 5A | 5.7986 | 1.8209 | 1.5838 | 7.2344 | 0 | 2.6653 | 0 | 1.2309 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 33.8981 | 17.55% | CZ 5A | 1.6995 | 0.53366 | 0 | 0.98417 | 0 | 0.78117 | 0 | 0.36077 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.3347 | 17.55% | CZ 5A | 0 | 0 | 0.015838 | 0.038764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054602 | 17.55% | CZ 5A | 17.7919 | 5.5869 | 1.731 | 14.5402 | 0 | 8.178 | 0 | 3.7769 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 93.2236 | 17.55%
CZ 5B | 0.18044 | 0.056794 | 0.01529 | 0.068703 | 0 | 0.095419 | 0 | 0.049067 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.8883 | 6.239% | CZ 5B | 5.7917 | 1.823 | 1.5603 | 3.6025 | 0 | 3.0627 | 0 | 1.575 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 30.9793 | 6.239% | CZ 5B | 1.6975 | 0.53428 | 0 | 0.45838 | 0 | 0.89764 | 0 | 0.46159 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.0248 | 6.239% | CZ 5B | 0 | 0 | 0.015603 | 0.020385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035988 | 6.239% | CZ 5B | 17.7707 | 5.5934 | 1.7054 | 7.0269 | 0 | 9.3974 | 0 | 4.8324 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 87.9448 | 6.239%
CZ 5C | 0.18209 | 0.056789 | 0.015462 | 0.052185 | 0 | 0.027907 | 0 | 0.03608 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.7931 | 0.04746% | CZ 5C | 5.8446 | 1.8228 | 1.5778 | 2.6146 | 0 | 0.89575 | 0 | 1.1581 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 27.4778 | 0.04746% | CZ 5C | 1.713 | 0.53423 | 0 | 0.36455 | 0 | 0.26253 | 0 | 0.33942 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 7.1891 | 0.04746% | CZ 5C | 0 | 0 | 0.015778 | 0.013708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029485 | 0.04746% | CZ 5C | 17.9329 | 5.5929 | 1.7245 | 5.3147 | 0 | 2.7484 | 0 | 3.5534 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 78.4855 | 0.04746%
CZ 6A | 0.18086 | 0.056767 | 0.016101 | 0.22324 | 0 | 0.090639 | 0 | 0.04031 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 1.0305 | 3.432% | CZ 6A | 5.8053 | 1.8221 | 1.643 | 11.3414 | 0 | 2.9093 | 0 | 1.2939 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 38.3791 | 3.432% | CZ 6A | 1.7014 | 0.53402 | 0 | 1.5384 | 0 | 0.85267 | 0 | 0.37921 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.9812 | 3.432% | CZ 6A | 0 | 0 | 0.01643 | 0.060924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077353 | 3.432% | CZ 6A | 17.8125 | 5.5907 | 1.7958 | 22.7645 | 0 | 8.9266 | 0 | 3.97 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 102.4786 | 3.432%
CZ 6B | 0.18101 | 0.056695 | 0.015954 | 0.14194 | 0 | 0.061272 | 0 | 0.043719 | 0 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 0.92318 | 0.5173% | CZ 6B | 5.8101 | 1.8198 | 1.6279 | 7.2354 | 0 | 1.9667 | 0 | 1.4033 | 0 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 33.4274 | 0.5173% | CZ 6B | 1.7028 | 0.53335 | 0 | 0.97484 | 0 | 0.57641 | 0 | 0.41128 | 0 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.1742 | 0.5173% | CZ 6B | 0 | 0 | 0.016279 | 0.039093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055372 | 0.5173% | CZ 6B | 17.8271 | 5.5837 | 1.7793 | 14.4785 | 0 | 6.0344 | 0 | 4.3057 | 0 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 91.6274 | 0.5173%
CZ 7 | 0.1809 | 0.056794 | 0.016808 | 0.20488 | 0 | 0.070442 | 0 | 0.041819 | 0.01459 | 8.2614e-05 | 0 | 0.09109 | 0.009396 | 0 | 0 | 0.32202 | 1.0088 | 0.4099% | CZ 7 | 5.8064 | 1.823 | 1.7151 | 8.8104 | 0 | 2.261 | 0 | 1.3423 | 0.4683 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 35.7906 | 0.4099% | CZ 7 | 1.7018 | 0.53428 | 0 | 1.6269 | 0 | 0.66267 | 0 | 0.39341 | 0.13725 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 9.0317 | 0.4099% | CZ 7 | 0 | 0 | 0.017151 | 0.032594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049745 | 0.4099% | CZ 7 | 17.8157 | 5.5934 | 1.8746 | 20.5945 | 0 | 6.9375 | 0 | 4.1186 | 1.4369 | 0.0081363 | 0 | 8.9711 | 0.92537 | 0 | 0 | 31.7141 | 99.9899 | 0.4099%
CZ 8 | 0.18732 | 0.057196 | 0.017762 | 0.32836 | 0 | 0.031713 | 0 | 0.043692 | 0.014926 | 8.2614e-05 | 0 | 0.09109 | 0.009407 | 0 | 0 | 0.32202 | 1.1036 | 0.04597% | CZ 8 | 6.0127 | 1.8359 | 1.8125 | 15.1684 | 0 | 1.0179 | 0 | 1.4024 | 0.47908 | 0.0026517 | 0 | 2.9238 | 0.30194 | 0 | 0 | 10.3361 | 41.2933 | 0.04597% | CZ 8 | 1.7622 | 0.53807 | 0 | 2.4665 | 0 | 0.29833 | 0 | 0.41102 | 0.14041 | 0.00077718 | 0 | 0.85692 | 0.088495 | 0 | 0 | 3.0293 | 9.592 | 0.04597% | CZ 8 | 0 | 0 | 0.018125 | 0.067529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085653 | 0.04597% | CZ 8 | 18.4487 | 5.633 | 1.981 | 33.2022 | 0 | 3.1232 | 0 | 4.303 | 1.47 | 0.0081363 | 0 | 8.9711 | 0.92645 | 0 | 0 | 31.7141 | 109.7809 | 0.04597%
US Weighted | 0.18078 | 0.056746 | 0.014262 | 0.066723 | 0 | 0.16376 | 0 | 0.043044 | 0.001276 | 8.2614e-05 | 0 | 0.09109 | 0.0093959 | 0 | 0 | 0.32202 | 0.94918 | 100% | US Weighted | 5.8026 | 1.8214 | 1.4553 | 3.2507 | 0 | 5.2565 | 0 | 1.3816 | 0.040957 | 0.0026517 | 0 | 2.9238 | 0.30159 | 0 | 0 | 10.3361 | 32.5732 | 100% | US Weighted | 1.7006 | 0.53383 | 0 | 0.47852 | 0 | 1.5406 | 0 | 0.40493 | 0.012004 | 0.00077718 | 0 | 0.85692 | 0.088391 | 0 | 0 | 3.0293 | 8.6459 | 100% | US Weighted | 0 | 0 | 0.014553 | 0.01618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030733 | 100% | US Weighted | 17.8041 | 5.5887 | 1.5907 | 6.7781 | 0 | 16.1283 | 0 | 4.2392 | 0.12567 | 0.0081363 | 0 | 8.9711 | 0.92536 | 0 | 0 | 31.7141 | 93.8734 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.20385 | 0.056789 | 0.011631 | 0 | 0 | 0.66166 | 0 | 0.071654 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095722 | 0 | 0 | 0.32596 | 1.4325 | 0% | CZ 0A | 6.5432 | 1.8228 | 1.1868 | 0 | 0 | 21.2377 | 0 | 2.2999 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 46.7948 | 0% | CZ 0A | 1.9177 | 0.53423 | 0 | 0 | 0 | 6.2244 | 0 | 0.67407 | 0 | 0.00077718 | 0 | 0.85925 | 0.090049 | 0 | 0 | 3.0664 | 13.3669 | 0% | CZ 0A | 0 | 0 | 0.011868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011868 | 0% | CZ 0A | 20.0765 | 5.5929 | 1.2972 | 0 | 0 | 65.1634 | 0 | 7.0569 | 0 | 0.0081363 | 0 | 8.9955 | 0.94272 | 0 | 0 | 32.1025 | 141.2357 | 0%
CZ 0B | 0.20414 | 0.056772 | 0.011709 | 0.00069947 | 0 | 0.55731 | 0 | 0.069258 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095722 | 0 | 0 | 0.32596 | 1.3268 | 0% | CZ 0B | 6.5524 | 1.8223 | 1.1948 | 0.022451 | 0 | 17.8886 | 0 | 2.223 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 43.4078 | 0% | CZ 0B | 1.9204 | 0.53408 | 0 | 0.0065801 | 0 | 5.2428 | 0 | 0.65153 | 0 | 0.00077718 | 0 | 0.85925 | 0.090049 | 0 | 0 | 3.0664 | 12.3719 | 0% | CZ 0B | 0 | 0 | 0.011948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011948 | 0% | CZ 0B | 20.1047 | 5.5912 | 1.3059 | 0.068887 | 0 | 54.8873 | 0 | 6.8209 | 0 | 0.0081363 | 0 | 8.9955 | 0.94272 | 0 | 0 | 32.1025 | 130.8278 | 0%
CZ 1A | 0.20471 | 0.056783 | 0.012143 | 7.1599e-05 | 0 | 0.44057 | 0 | 0.061046 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095722 | 0 | 0 | 0.32596 | 1.2023 | 2.823% | CZ 1A | 6.5706 | 1.8226 | 1.2391 | 0.0022982 | 0 | 14.1413 | 0 | 1.9595 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 39.4398 | 2.823% | CZ 1A | 1.9257 | 0.53418 | 0 | 0.00067355 | 0 | 4.1446 | 0 | 0.57428 | 0 | 0.00077718 | 0 | 0.85925 | 0.090049 | 0 | 0 | 3.0664 | 11.196 | 2.823% | CZ 1A | 0 | 0 | 0.012391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012391 | 2.823% | CZ 1A | 20.1606 | 5.5923 | 1.3544 | 0.0070514 | 0 | 43.3897 | 0 | 6.0122 | 0 | 0.0081363 | 0 | 8.9955 | 0.94272 | 0 | 0 | 32.1025 | 118.565 | 2.823%
CZ 1B | 0.20472 | 0.056695 | 0.012187 | 0.0080336 | 0 | 0.4494 | 0 | 0.064802 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095722 | 0 | 0 | 0.32596 | 1.2228 | 0% | CZ 1B | 6.5712 | 1.8198 | 1.2435 | 0.28161 | 0 | 14.4249 | 0 | 2.08 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 40.1253 | 0% | CZ 1B | 1.9259 | 0.53335 | 0 | 0.072381 | 0 | 4.2277 | 0 | 0.60962 | 0 | 0.00077718 | 0 | 0.85925 | 0.090049 | 0 | 0 | 3.0664 | 11.3855 | 0% | CZ 1B | 0 | 0 | 0.012435 | 0.00034641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012782 | 0% | CZ 1B | 20.1622 | 5.5837 | 1.3592 | 0.79562 | 0 | 44.2597 | 0 | 6.3821 | 0 | 0.0081363 | 0 | 8.9955 | 0.94272 | 0 | 0 | 32.1025 | 120.5913 | 0%
CZ 2A | 0.2046 | 0.056673 | 0.01275 | 0.015761 | 0 | 0.37104 | 0 | 0.050268 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095722 | 0 | 0 | 0.32596 | 1.138 | 15.52% | CZ 2A | 6.5671 | 1.8191 | 1.301 | 0.52733 | 0 | 11.9096 | 0 | 1.6135 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 37.4419 | 15.52% | CZ 2A | 1.9247 | 0.53314 | 0 | 0.14538 | 0 | 3.4905 | 0 | 0.47289 | 0 | 0.00077718 | 0 | 0.85925 | 0.090049 | 0 | 0 | 3.0664 | 10.5831 | 15.52% | CZ 2A | 0 | 0 | 0.01301 | 0.00031283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013323 | 15.52% | CZ 2A | 20.1498 | 5.5815 | 1.422 | 1.5562 | 0 | 36.5422 | 0 | 4.9507 | 0 | 0.0081363 | 0 | 8.9955 | 0.94272 | 0 | 0 | 32.1025 | 112.2511 | 15.52%
CZ 2B | 0.20501 | 0.056723 | 0.012786 | 0.011059 | 0 | 0.26942 | 0 | 0.060727 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095722 | 0 | 0 | 0.32596 | 1.0427 | 3.865% | CZ 2B | 6.5804 | 1.8207 | 1.3047 | 0.43203 | 0 | 8.6476 | 0 | 1.9492 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 34.4389 | 3.865% | CZ 2B | 1.9286 | 0.53361 | 0 | 0.093676 | 0 | 2.5345 | 0 | 0.57128 | 0 | 0.00077718 | 0 | 0.85925 | 0.090049 | 0 | 0 | 3.0664 | 9.6781 | 3.865% | CZ 2B | 0 | 0 | 0.013047 | 0.0011241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014171 | 3.865% | CZ 2B | 20.1904 | 5.5864 | 1.426 | 1.1036 | 0 | 26.5335 | 0 | 5.9807 | 0 | 0.0081363 | 0 | 8.9955 | 0.94272 | 0 | 0 | 32.1025 | 102.8694 | 3.865%
CZ 3A | 0.20582 | 0.056706 | 0.013844 | 0.079879 | 0 | 0.20722 | 0 | 0.040999 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 1.0314 | 14.49% | CZ 3A | 6.6063 | 1.8201 | 1.4127 | 2.9924 | 0 | 6.6514 | 0 | 1.316 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 34.5035 | 14.49% | CZ 3A | 1.9362 | 0.53345 | 0 | 0.69381 | 0 | 1.9494 | 0 | 0.38569 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 9.5151 | 14.49% | CZ 3A | 0 | 0 | 0.014127 | 0.0062513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020378 | 14.49% | CZ 3A | 20.2702 | 5.5847 | 1.5441 | 7.9468 | 0 | 20.4085 | 0 | 4.0378 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 101.8414 | 14.49%
CZ 3B | 0.20508 | 0.056706 | 0.013558 | 0.023747 | 0 | 0.18056 | 0 | 0.052366 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095722 | 0 | 0 | 0.32596 | 0.95897 | 8.895% | CZ 3B | 6.5825 | 1.8201 | 1.3835 | 1.1076 | 0 | 5.7956 | 0 | 1.6808 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 32.0745 | 8.895% | CZ 3B | 1.9292 | 0.53345 | 0 | 0.17694 | 0 | 1.6986 | 0 | 0.49263 | 0 | 0.00077718 | 0 | 0.85925 | 0.090049 | 0 | 0 | 3.0664 | 8.8473 | 8.895% | CZ 3B | 0 | 0 | 0.013835 | 0.0050388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018874 | 8.895% | CZ 3B | 20.1969 | 5.5847 | 1.5122 | 2.4031 | 0 | 17.7826 | 0 | 5.1573 | 0 | 0.0081363 | 0 | 8.9955 | 0.94272 | 0 | 0 | 32.1025 | 94.6858 | 8.895%
CZ 3C | 0.20537 | 0.056805 | 0.013948 | 0.0091102 | 0 | 0.11929 | 0 | 0.038762 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 0.87024 | 3.286% | CZ 3C | 6.5919 | 1.8233 | 1.4233 | 0.34948 | 0 | 3.8289 | 0 | 1.2442 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 28.9656 | 3.286% | CZ 3C | 1.932 | 0.53439 | 0 | 0.078029 | 0 | 1.1222 | 0 | 0.36465 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 8.0478 | 3.286% | CZ 3C | 0 | 0 | 0.014233 | 0.00083244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015065 | 3.286% | CZ 3C | 20.2257 | 5.5945 | 1.5556 | 0.90787 | 0 | 11.7482 | 0 | 3.8175 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 85.8989 | 3.286%
CZ 4A | 0.20524 | 0.056827 | 0.014743 | 0.10522 | 0 | 0.13746 | 0 | 0.040944 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 0.98739 | 18.98% | CZ 4A | 6.5876 | 1.824 | 1.5044 | 4.8624 | 0 | 4.4123 | 0 | 1.3142 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 34.2094 | 18.98% | CZ 4A | 1.9307 | 0.53459 | 0 | 0.79008 | 0 | 1.2932 | 0 | 0.38517 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 8.9503 | 18.98% | CZ 4A | 0 | 0 | 0.015044 | 0.021666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036711 | 18.98% | CZ 4A | 20.2127 | 5.5967 | 1.6443 | 10.6395 | 0 | 13.5382 | 0 | 4.0323 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 97.7131 | 18.98%
CZ 4B | 0.20421 | 0.056684 | 0.014482 | 0.038984 | 0 | 0.1353 | 0 | 0.055021 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095722 | 0 | 0 | 0.32596 | 0.93164 | 0.5078% | CZ 4B | 6.5547 | 1.8194 | 1.4777 | 1.8245 | 0 | 4.3428 | 0 | 1.7661 | 0 | 0.0026517 | 0 | 2.9318 | 0.30725 | 0 | 0 | 10.4627 | 31.4896 | 0.5078% | CZ 4B | 1.9211 | 0.53325 | 0 | 0.28963 | 0 | 1.2728 | 0 | 0.5176 | 0 | 0.00077718 | 0 | 0.85925 | 0.090049 | 0 | 0 | 3.0664 | 8.5509 | 0.5078% | CZ 4B | 0 | 0 | 0.014777 | 0.0083633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02314 | 0.5078% | CZ 4B | 20.1118 | 5.5826 | 1.6151 | 3.9462 | 0 | 13.3251 | 0 | 5.4188 | 0 | 0.0081363 | 0 | 8.9955 | 0.94272 | 0 | 0 | 32.1025 | 92.0484 | 0.5078%
CZ 4C | 0.20635 | 0.056822 | 0.015024 | 0.077023 | 0 | 0.050108 | 0 | 0.038173 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 0.87046 | 3.396% | CZ 4C | 6.6233 | 1.8239 | 1.533 | 3.1933 | 0 | 1.6084 | 0 | 1.2253 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 29.7117 | 3.396% | CZ 4C | 1.9412 | 0.53454 | 0 | 0.6276 | 0 | 0.47138 | 0 | 0.35911 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 7.9504 | 3.396% | CZ 4C | 0 | 0 | 0.01533 | 0.01052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02585 | 3.396% | CZ 4C | 20.3222 | 5.5961 | 1.6756 | 7.7201 | 0 | 4.9349 | 0 | 3.7595 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 86.0579 | 3.396%
CZ 5A | 0.20506 | 0.056728 | 0.01553 | 0.17442 | 0 | 0.089069 | 0 | 0.038388 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 1.0062 | 17.55% | CZ 5A | 6.582 | 1.8209 | 1.5846 | 8.3582 | 0 | 2.8589 | 0 | 1.2322 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 36.1412 | 17.55% | CZ 5A | 1.9291 | 0.53366 | 0 | 1.2696 | 0 | 0.8379 | 0 | 0.36113 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 8.948 | 17.55% | CZ 5A | 0 | 0 | 0.015846 | 0.040261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056108 | 17.55% | CZ 5A | 20.1953 | 5.5869 | 1.732 | 17.6925 | 0 | 8.772 | 0 | 3.7807 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 99.8088 | 17.55%
CZ 5B | 0.20495 | 0.056794 | 0.015297 | 0.096507 | 0 | 0.097562 | 0 | 0.050367 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 0.94844 | 6.239% | CZ 5B | 6.5784 | 1.823 | 1.561 | 4.6006 | 0 | 3.1315 | 0 | 1.6167 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 33.0156 | 6.239% | CZ 5B | 1.928 | 0.53428 | 0 | 0.70573 | 0 | 0.9178 | 0 | 0.47382 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 8.5762 | 6.239% | CZ 5B | 0 | 0 | 0.01561 | 0.021926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037536 | 6.239% | CZ 5B | 20.1845 | 5.5934 | 1.7061 | 9.7848 | 0 | 9.6084 | 0 | 4.9604 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 93.887 | 6.239%
CZ 5C | 0.20665 | 0.056789 | 0.015465 | 0.079704 | 0 | 0.027163 | 0 | 0.03765 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 0.85038 | 0.04746% | CZ 5C | 6.6329 | 1.8228 | 1.5781 | 3.5459 | 0 | 0.87189 | 0 | 1.2085 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 29.3645 | 0.04746% | CZ 5C | 1.944 | 0.53423 | 0 | 0.61698 | 0 | 0.25554 | 0 | 0.35419 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 7.7215 | 0.04746% | CZ 5C | 0 | 0 | 0.015781 | 0.014408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030189 | 0.04746% | CZ 5C | 20.3515 | 5.5929 | 1.7249 | 8.0339 | 0 | 2.6752 | 0 | 3.708 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 84.1357 | 0.04746%
CZ 6A | 0.20531 | 0.056767 | 0.01611 | 0.26831 | 0 | 0.097171 | 0 | 0.041109 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 1.1117 | 3.432% | CZ 6A | 6.5901 | 1.8221 | 1.6439 | 12.9591 | 0 | 3.119 | 0 | 1.3195 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 41.1581 | 3.432% | CZ 6A | 1.9314 | 0.53402 | 0 | 1.9394 | 0 | 0.91412 | 0 | 0.38672 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 9.7223 | 3.432% | CZ 6A | 0 | 0 | 0.016439 | 0.063418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079856 | 3.432% | CZ 6A | 20.2203 | 5.5907 | 1.7967 | 27.2353 | 0 | 9.5699 | 0 | 4.0486 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 110.5109 | 3.432%
CZ 6B | 0.20559 | 0.056695 | 0.015963 | 0.18263 | 0 | 0.063607 | 0 | 0.044408 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 0.99585 | 0.5173% | CZ 6B | 6.5989 | 1.8198 | 1.6288 | 8.6871 | 0 | 2.0417 | 0 | 1.4254 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 35.9062 | 0.5173% | CZ 6B | 1.934 | 0.53335 | 0 | 1.338 | 0 | 0.59838 | 0 | 0.41776 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 8.8381 | 0.5173% | CZ 6B | 0 | 0 | 0.016288 | 0.041217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057506 | 0.5173% | CZ 6B | 20.2474 | 5.5837 | 1.7803 | 18.513 | 0 | 6.2644 | 0 | 4.3735 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 98.8116 | 0.5173%
CZ 7 | 0.20543 | 0.056794 | 0.016816 | 0.30062 | 0 | 0.075217 | 0 | 0.042458 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095777 | 0 | 0 | 0.32596 | 1.1243 | 0.4099% | CZ 7 | 6.5938 | 1.823 | 1.716 | 15.2237 | 0 | 2.4143 | 0 | 1.3628 | 0 | 0.0026517 | 0 | 2.9318 | 0.30742 | 0 | 0 | 10.4627 | 42.8381 | 0.4099% | CZ 7 | 1.9325 | 0.53428 | 0 | 2.0782 | 0 | 0.70759 | 0 | 0.39942 | 0 | 0.00077718 | 0 | 0.85925 | 0.090101 | 0 | 0 | 3.0664 | 9.6686 | 0.4099% | CZ 7 | 0 | 0 | 0.01716 | 0.081328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.098488 | 0.4099% | CZ 7 | 20.2317 | 5.5934 | 1.8755 | 30.6461 | 0 | 7.4078 | 0 | 4.1815 | 0 | 0.0081363 | 0 | 8.9955 | 0.94327 | 0 | 0 | 32.1025 | 111.9854 | 0.4099%
CZ 8 | 0.21313 | 0.057196 | 0.017773 | 0.47139 | 0 | 0.032286 | 0 | 0.044298 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.0095887 | 0 | 0 | 0.32596 | 1.263 | 0.04597% | CZ 8 | 6.8411 | 1.8359 | 1.8135 | 23.6267 | 0 | 1.0363 | 0 | 1.4219 | 0 | 0.0026517 | 0 | 2.9318 | 0.30778 | 0 | 0 | 10.4627 | 50.2803 | 0.04597% | CZ 8 | 2.005 | 0.53807 | 0 | 3.2918 | 0 | 0.30372 | 0 | 0.41672 | 0 | 0.00077718 | 0 | 0.85925 | 0.090204 | 0 | 0 | 3.0664 | 10.572 | 0.04597% | CZ 8 | 0 | 0 | 0.018135 | 0.12395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14209 | 0.04597% | CZ 8 | 20.9905 | 5.633 | 1.9822 | 48.0095 | 0 | 3.1797 | 0 | 4.3627 | 0 | 0.0081363 | 0 | 8.9955 | 0.94435 | 0 | 0 | 32.1025 | 126.208 | 0.04597%
US Weighted | 0.20518 | 0.056746 | 0.014267 | 0.087912 | 0 | 0.18463 | 0 | 0.044822 | 0 | 8.2614e-05 | 0 | 0.091338 | 0.009576 | 0 | 0 | 0.32596 | 1.0205 | 100% | US Weighted | 6.5859 | 1.8214 | 1.4558 | 4.0011 | 0 | 5.9262 | 0 | 1.4387 | 0 | 0.0026517 | 0 | 2.9318 | 0.30737 | 0 | 0 | 10.4627 | 34.9336 | 100% | US Weighted | 1.9302 | 0.53383 | 0 | 0.6684 | 0 | 1.7369 | 0 | 0.42165 | 0 | 0.00077718 | 0 | 0.85925 | 0.090085 | 0 | 0 | 3.0664 | 9.3075 | 100% | US Weighted | 0 | 0 | 0.014558 | 0.017205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031763 | 100% | US Weighted | 20.2073 | 5.5887 | 1.5912 | 8.878 | 0 | 18.1834 | 0 | 4.4143 | 0 | 0.0081363 | 0 | 8.9955 | 0.94309 | 0 | 0 | 32.1025 | 100.912 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.30444 | 0.12427 | 0.012043 | 3.3046e-05 | 0 | 0.8542 | 0 | 0.082014 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.8452 | 0% | CZ 0A | 9.772 | 3.9889 | 1.2289 | 0.0010607 | 0 | 27.418 | 0 | 2.6325 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 60.0704 | 0% | CZ 0A | 2.864 | 1.1691 | 0 | 0.00031087 | 0 | 8.0358 | 0 | 0.77153 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 17.2455 | 0% | CZ 0A | 0 | 0 | 0.012289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012289 | 0% | CZ 0A | 29.9833 | 12.2391 | 1.3432 | 0.0032545 | 0 | 84.1264 | 0 | 8.0772 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 181.886 | 0%
CZ 0B | 0.30444 | 0.1243 | 0.012164 | 0.0038939 | 0 | 0.69346 | 0 | 0.079376 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.6859 | 0% | CZ 0B | 9.772 | 3.9896 | 1.2412 | 0.12498 | 0 | 22.2585 | 0 | 2.5478 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 54.9632 | 0% | CZ 0B | 2.864 | 1.1693 | 0 | 0.036631 | 0 | 6.5236 | 0 | 0.74671 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 15.745 | 0% | CZ 0B | 0 | 0 | 0.012412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012412 | 0% | CZ 0B | 29.9833 | 12.2413 | 1.3567 | 0.38349 | 0 | 68.2954 | 0 | 7.8173 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 166.1911 | 0%
CZ 1A | 0.30444 | 0.12431 | 0.012531 | 0.00093629 | 0 | 0.55485 | 0 | 0.07226 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.5376 | 2.823% | CZ 1A | 9.772 | 3.9901 | 1.2787 | 0.030053 | 0 | 17.8096 | 0 | 2.3194 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 50.229 | 2.823% | CZ 1A | 2.864 | 1.1694 | 0 | 0.008808 | 0 | 5.2197 | 0 | 0.67977 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 14.3465 | 2.823% | CZ 1A | 0 | 0 | 0.012787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012787 | 2.823% | CZ 1A | 29.9833 | 12.2429 | 1.3976 | 0.092211 | 0 | 54.6449 | 0 | 7.1165 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 151.5911 | 2.823%
CZ 1B | 0.30444 | 0.12415 | 0.012611 | 0.020234 | 0 | 0.5617 | 0 | 0.074424 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.5658 | 0% | CZ 1B | 9.772 | 3.985 | 1.2868 | 0.65445 | 0 | 18.0293 | 0 | 2.3889 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 51.1456 | 0% | CZ 1B | 2.864 | 1.1679 | 0 | 0.18968 | 0 | 5.2841 | 0 | 0.70013 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 14.6106 | 0% | CZ 1B | 0 | 0 | 0.012868 | 7.2463e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012941 | 0% | CZ 1B | 29.9833 | 12.2272 | 1.4065 | 1.9937 | 0 | 55.3191 | 0 | 7.3297 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 154.3732 | 0%
CZ 2A | 0.30444 | 0.12411 | 0.013131 | 0.024346 | 0 | 0.49074 | 0 | 0.060385 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.4854 | 15.52% | CZ 2A | 9.772 | 3.9836 | 1.3399 | 0.87256 | 0 | 15.7516 | 0 | 1.9382 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 48.687 | 15.52% | CZ 2A | 2.864 | 1.1675 | 0 | 0.21678 | 0 | 4.6165 | 0 | 0.56807 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.8377 | 15.52% | CZ 2A | 0 | 0 | 0.013399 | 0.0013291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014728 | 15.52% | CZ 2A | 29.9833 | 12.2229 | 1.4645 | 2.4147 | 0 | 48.3306 | 0 | 5.9471 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 146.4767 | 15.52%
CZ 2B | 0.30444 | 0.1242 | 0.01317 | 0.027663 | 0 | 0.34622 | 0 | 0.070382 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3543 | 3.865% | CZ 2B | 9.772 | 3.9866 | 1.3439 | 0.90317 | 0 | 11.1131 | 0 | 2.2591 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 44.407 | 3.865% | CZ 2B | 2.864 | 1.1684 | 0 | 0.25818 | 0 | 3.257 | 0 | 0.6621 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.6145 | 3.865% | CZ 2B | 0 | 0 | 0.013439 | 0.00022269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013662 | 3.865% | CZ 2B | 29.9833 | 12.2321 | 1.4689 | 2.7272 | 0 | 34.098 | 0 | 6.9316 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 133.5548 | 3.865%
CZ 3A | 0.30444 | 0.12417 | 0.014194 | 0.10274 | 0 | 0.27976 | 0 | 0.050279 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3438 | 14.49% | CZ 3A | 9.772 | 3.9857 | 1.4484 | 4.4404 | 0 | 8.9798 | 0 | 1.6138 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 45.2692 | 14.49% | CZ 3A | 2.864 | 1.1682 | 0 | 0.81277 | 0 | 2.6318 | 0 | 0.47299 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.3545 | 14.49% | CZ 3A | 0 | 0 | 0.014484 | 0.016672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031156 | 14.49% | CZ 3A | 29.9833 | 12.2294 | 1.5831 | 10.3311 | 0 | 27.5527 | 0 | 4.9517 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 132.745 | 14.49%
CZ 3B | 0.30444 | 0.12417 | 0.013914 | 0.047591 | 0 | 0.23759 | 0 | 0.060661 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.2566 | 8.895% | CZ 3B | 9.772 | 3.9857 | 1.4197 | 1.6824 | 0 | 7.626 | 0 | 1.9471 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 41.4621 | 8.895% | CZ 3B | 2.864 | 1.1682 | 0 | 0.42688 | 0 | 2.2351 | 0 | 0.57066 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 11.6695 | 8.895% | CZ 3B | 0 | 0 | 0.014197 | 0.0022587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016456 | 8.895% | CZ 3B | 29.9833 | 12.2294 | 1.5518 | 4.7159 | 0 | 23.3988 | 0 | 5.9742 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 123.967 | 8.895%
CZ 3C | 0.30444 | 0.12415 | 0.0143 | 0.019672 | 0 | 0.18898 | 0 | 0.044997 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.1648 | 3.286% | CZ 3C | 9.772 | 3.985 | 1.4592 | 0.64755 | 0 | 6.0657 | 0 | 1.4443 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 38.4029 | 3.286% | CZ 3C | 2.864 | 1.1679 | 0 | 0.1829 | 0 | 1.7778 | 0 | 0.4233 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 10.8207 | 3.286% | CZ 3C | 0 | 0 | 0.014592 | 0.00023506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014827 | 3.286% | CZ 3C | 29.9833 | 12.2272 | 1.5949 | 1.9404 | 0 | 18.6115 | 0 | 4.4316 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 114.9025 | 3.286%
CZ 4A | 0.30444 | 0.12399 | 0.015076 | 0.18212 | 0 | 0.20385 | 0 | 0.047745 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3454 | 18.98% | CZ 4A | 9.772 | 3.9797 | 1.5383 | 7.7132 | 0 | 6.5431 | 0 | 1.5325 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 46.108 | 18.98% | CZ 4A | 2.864 | 1.1664 | 0 | 1.4621 | 0 | 1.9177 | 0 | 0.44916 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.2641 | 18.98% | CZ 4A | 0 | 0 | 0.015383 | 0.027246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04263 | 18.98% | CZ 4A | 29.9833 | 12.2109 | 1.6814 | 18.2845 | 0 | 20.076 | 0 | 4.7022 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 133.052 | 18.98%
CZ 4B | 0.30444 | 0.12408 | 0.014828 | 0.080583 | 0 | 0.18732 | 0 | 0.061768 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.2413 | 0.5078% | CZ 4B | 9.772 | 3.9827 | 1.5131 | 2.9491 | 0 | 6.0125 | 0 | 1.9826 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 41.2412 | 0.5078% | CZ 4B | 2.864 | 1.1673 | 0 | 0.7093 | 0 | 1.7622 | 0 | 0.58107 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 11.4886 | 0.5078% | CZ 4B | 0 | 0 | 0.015131 | 0.0052898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02042 | 0.5078% | CZ 4B | 29.9833 | 12.2201 | 1.6538 | 8.0039 | 0 | 18.4482 | 0 | 6.0832 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 122.5062 | 0.5078%
CZ 4C | 0.30444 | 0.12384 | 0.01533 | 0.1451 | 0 | 0.09532 | 0 | 0.044463 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.1967 | 3.396% | CZ 4C | 9.772 | 3.9751 | 1.5643 | 5.2887 | 0 | 3.0596 | 0 | 1.4272 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 40.116 | 3.396% | CZ 4C | 2.864 | 1.165 | 0 | 1.2801 | 0 | 0.89671 | 0 | 0.41828 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 11.0289 | 3.396% | CZ 4C | 0 | 0 | 0.015643 | 0.0092099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024853 | 3.396% | CZ 4C | 29.9833 | 12.1968 | 1.7098 | 14.4082 | 0 | 9.3876 | 0 | 4.3789 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 118.1783 | 3.396%
CZ 5A | 0.30444 | 0.12403 | 0.015829 | 0.2812 | 0 | 0.1218 | 0 | 0.045537 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3611 | 17.55% | CZ 5A | 9.772 | 3.981 | 1.6152 | 12.6496 | 0 | 3.9095 | 0 | 1.4616 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 48.4181 | 17.55% | CZ 5A | 2.864 | 1.1668 | 0 | 2.1579 | 0 | 1.1458 | 0 | 0.42838 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.1677 | 17.55% | CZ 5A | 0 | 0 | 0.016152 | 0.052868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06902 | 17.55% | CZ 5A | 29.9833 | 12.2147 | 1.7654 | 28.3697 | 0 | 11.9956 | 0 | 4.4847 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 134.9271 | 17.55%
CZ 5B | 0.30444 | 0.12403 | 0.015618 | 0.16233 | 0 | 0.14296 | 0 | 0.057945 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.2756 | 6.239% | CZ 5B | 9.772 | 3.9811 | 1.5937 | 6.5265 | 0 | 4.5886 | 0 | 1.8599 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 43.3509 | 6.239% | CZ 5B | 2.864 | 1.1668 | 0 | 1.3501 | 0 | 1.3448 | 0 | 0.54511 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 11.6756 | 6.239% | CZ 5B | 0 | 0 | 0.015937 | 0.019201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035138 | 6.239% | CZ 5B | 29.9833 | 12.2153 | 1.7419 | 16.2325 | 0 | 14.079 | 0 | 5.7068 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 126.0724 | 6.239%
CZ 5C | 0.30444 | 0.12384 | 0.01577 | 0.14084 | 0 | 0.063877 | 0 | 0.042221 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.1592 | 0.04746% | CZ 5C | 9.772 | 3.9749 | 1.6092 | 5.4882 | 0 | 2.0503 | 0 | 1.3552 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 39.279 | 0.04746% | CZ 5C | 2.864 | 1.165 | 0 | 1.1948 | 0 | 0.60091 | 0 | 0.39719 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 10.6267 | 0.04746% | CZ 5C | 0 | 0 | 0.016092 | 0.014114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030207 | 0.04746% | CZ 5C | 29.9833 | 12.1963 | 1.7589 | 14.0514 | 0 | 6.291 | 0 | 4.1582 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 114.5527 | 0.04746%
CZ 6A | 0.30444 | 0.12397 | 0.016406 | 0.41617 | 0 | 0.13075 | 0 | 0.049491 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.5095 | 3.432% | CZ 6A | 9.772 | 3.9792 | 1.6741 | 19.0673 | 0 | 4.1968 | 0 | 1.5886 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 55.307 | 3.432% | CZ 6A | 2.864 | 1.1662 | 0 | 3.1472 | 0 | 1.23 | 0 | 0.46558 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.2778 | 3.432% | CZ 6A | 0 | 0 | 0.016741 | 0.083292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10003 | 3.432% | CZ 6A | 29.9833 | 12.2093 | 1.8298 | 42.0514 | 0 | 12.877 | 0 | 4.8742 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 149.9386 | 3.432%
CZ 6B | 0.30444 | 0.12388 | 0.016255 | 0.29336 | 0 | 0.098349 | 0 | 0.052361 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3569 | 0.5173% | CZ 6B | 9.772 | 3.9762 | 1.6587 | 12.5206 | 0 | 3.1568 | 0 | 1.6807 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 47.794 | 0.5173% | CZ 6B | 2.864 | 1.1654 | 0 | 2.3422 | 0 | 0.9252 | 0 | 0.49258 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.1941 | 0.5173% | CZ 6B | 0 | 0 | 0.016587 | 0.045289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061876 | 0.5173% | CZ 6B | 29.9833 | 12.2001 | 1.813 | 29.4707 | 0 | 9.686 | 0 | 5.1568 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 134.4234 | 0.5173%
CZ 7 | 0.30444 | 0.1238 | 0.0171 | 0.45389 | 0 | 0.10723 | 0 | 0.051369 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.5261 | 0.4099% | CZ 7 | 9.772 | 3.9737 | 1.7449 | 21.7758 | 0 | 3.4419 | 0 | 1.6488 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 57.3863 | 0.4099% | CZ 7 | 2.864 | 1.1646 | 0 | 3.3005 | 0 | 1.0088 | 0 | 0.48325 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.226 | 0.4099% | CZ 7 | 0 | 0 | 0.017449 | 0.10514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12259 | 0.4099% | CZ 7 | 29.9833 | 12.1925 | 1.9072 | 46.0454 | 0 | 10.5609 | 0 | 5.0591 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 151.8621 | 0.4099%
CZ 8 | 0.30444 | 0.12312 | 0.018022 | 0.65828 | 0 | 0.063481 | 0 | 0.053286 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.6889 | 0.04597% | CZ 8 | 9.772 | 3.952 | 1.839 | 32.0771 | 0 | 2.0376 | 0 | 1.7104 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 66.4171 | 0.04597% | CZ 8 | 2.864 | 1.1583 | 0 | 4.7202 | 0 | 0.59718 | 0 | 0.50128 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 14.2457 | 0.04597% | CZ 8 | 0 | 0 | 0.01839 | 0.15972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17811 | 0.04597% | CZ 8 | 29.9833 | 12.1258 | 2.01 | 66.8727 | 0 | 6.2519 | 0 | 5.2479 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 168.6053 | 0.04597%
US Weighted | 0.30444 | 0.12408 | 0.014607 | 0.14204 | 0 | 0.25174 | 0 | 0.053007 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3581 | 100% | US Weighted | 9.772 | 3.9826 | 1.4905 | 6.0967 | 0 | 8.0804 | 0 | 1.7014 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 46.1526 | 100% | US Weighted | 2.864 | 1.1672 | 0 | 1.1295 | 0 | 2.3682 | 0 | 0.49865 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.4324 | 100% | US Weighted | 0 | 0 | 0.014905 | 0.022429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037334 | 100% | US Weighted | 29.9833 | 12.2196 | 1.6291 | 14.276 | 0 | 24.793 | 0 | 5.2204 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 134.2351 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 53628 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.30444 | 0.12427 | 0.012043 | 2.7538e-05 | 0 | 0.93474 | 0 | 0.09228 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.936 | 0% | CZ 0A | 9.772 | 3.9889 | 1.2289 | 0.00088391 | 0 | 30.0031 | 0 | 2.962 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 62.9849 | 0% | CZ 0A | 2.864 | 1.1691 | 0 | 0.00025906 | 0 | 8.7934 | 0 | 0.86811 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 18.0996 | 0% | CZ 0A | 0 | 0 | 0.012289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012289 | 0% | CZ 0A | 29.9833 | 12.2391 | 1.3432 | 0.0027121 | 0 | 92.0582 | 0 | 9.0882 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 190.8283 | 0%
CZ 0B | 0.30444 | 0.1243 | 0.012164 | 0.0041527 | 0 | 0.74229 | 0 | 0.090192 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.7458 | 0% | CZ 0B | 9.772 | 3.9896 | 1.2412 | 0.13329 | 0 | 23.8258 | 0 | 2.895 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 56.8861 | 0% | CZ 0B | 2.864 | 1.1693 | 0 | 0.039066 | 0 | 6.9829 | 0 | 0.84847 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 16.3086 | 0% | CZ 0B | 0 | 0 | 0.012412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012412 | 0% | CZ 0B | 29.9833 | 12.2413 | 1.3567 | 0.40898 | 0 | 73.1044 | 0 | 8.8826 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 172.091 | 0%
CZ 1A | 0.30444 | 0.12431 | 0.012531 | 0.00095282 | 0 | 0.59016 | 0 | 0.081441 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.5821 | 2.823% | CZ 1A | 9.772 | 3.9901 | 1.2787 | 0.030583 | 0 | 18.9427 | 0 | 2.6141 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 51.6574 | 2.823% | CZ 1A | 2.864 | 1.1694 | 0 | 0.0089635 | 0 | 5.5518 | 0 | 0.76614 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 14.7651 | 2.823% | CZ 1A | 0 | 0 | 0.012787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012787 | 2.823% | CZ 1A | 29.9833 | 12.2429 | 1.3976 | 0.093838 | 0 | 58.1218 | 0 | 8.0207 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 155.9739 | 2.823%
CZ 1B | 0.30444 | 0.12415 | 0.012611 | 0.021458 | 0 | 0.59745 | 0 | 0.084762 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.6131 | 0% | CZ 1B | 9.772 | 3.985 | 1.2868 | 0.705 | 0 | 19.1768 | 0 | 2.7207 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 52.6754 | 0% | CZ 1B | 2.864 | 1.1679 | 0 | 0.19968 | 0 | 5.6204 | 0 | 0.79738 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 15.0542 | 0% | CZ 1B | 0 | 0 | 0.012868 | 0.00023683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013105 | 0% | CZ 1B | 29.9833 | 12.2272 | 1.4065 | 2.1164 | 0 | 58.8399 | 0 | 8.3478 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 159.0348 | 0%
CZ 2A | 0.30444 | 0.12411 | 0.013131 | 0.041374 | 0 | 0.53699 | 0 | 0.071373 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.5596 | 15.52% | CZ 2A | 9.772 | 3.9836 | 1.3399 | 1.4879 | 0 | 17.2363 | 0 | 2.2909 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 51.1397 | 15.52% | CZ 2A | 2.864 | 1.1675 | 0 | 0.36771 | 0 | 5.0517 | 0 | 0.67143 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 14.5271 | 15.52% | CZ 2A | 0 | 0 | 0.013399 | 0.002333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015732 | 15.52% | CZ 2A | 29.9833 | 12.2229 | 1.4645 | 4.1045 | 0 | 52.8858 | 0 | 7.0292 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 153.8038 | 15.52%
CZ 2B | 0.30444 | 0.1242 | 0.013169 | 0.049258 | 0 | 0.37371 | 0 | 0.08338 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.4164 | 3.865% | CZ 2B | 9.772 | 3.9866 | 1.3437 | 1.6117 | 0 | 11.9952 | 0 | 2.6763 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 46.4147 | 3.865% | CZ 2B | 2.864 | 1.1684 | 0 | 0.45926 | 0 | 3.5156 | 0 | 0.78438 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.1964 | 3.865% | CZ 2B | 0 | 0 | 0.013437 | 0.00044715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013885 | 3.865% | CZ 2B | 29.9833 | 12.2321 | 1.4687 | 4.8569 | 0 | 36.8047 | 0 | 8.2117 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 139.671 | 3.865%
CZ 3A | 0.30444 | 0.12417 | 0.014198 | 0.1282 | 0 | 0.296 | 0 | 0.058359 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3936 | 14.49% | CZ 3A | 9.772 | 3.9857 | 1.4487 | 5.8668 | 0 | 9.501 | 0 | 1.8732 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 47.4765 | 14.49% | CZ 3A | 2.864 | 1.1682 | 0 | 0.97033 | 0 | 2.7846 | 0 | 0.549 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.7408 | 14.49% | CZ 3A | 0 | 0 | 0.014487 | 0.02556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040047 | 14.49% | CZ 3A | 29.9833 | 12.2294 | 1.5835 | 12.9521 | 0 | 29.1517 | 0 | 5.7475 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 137.7611 | 14.49%
CZ 3B | 0.30444 | 0.12417 | 0.013915 | 0.060835 | 0 | 0.24755 | 0 | 0.070139 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.2893 | 8.895% | CZ 3B | 9.772 | 3.9857 | 1.4199 | 2.2745 | 0 | 7.9458 | 0 | 2.2513 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 42.6784 | 8.895% | CZ 3B | 2.864 | 1.1682 | 0 | 0.529 | 0 | 2.3288 | 0 | 0.65982 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 11.9546 | 8.895% | CZ 3B | 0 | 0 | 0.014199 | 0.004696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018895 | 8.895% | CZ 3B | 29.9833 | 12.2294 | 1.552 | 6.0514 | 0 | 24.3801 | 0 | 6.9077 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 127.2174 | 8.895%
CZ 3C | 0.30444 | 0.12415 | 0.0143 | 0.054572 | 0 | 0.21957 | 0 | 0.060226 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.2455 | 3.286% | CZ 3C | 9.772 | 3.985 | 1.4592 | 1.7653 | 0 | 7.0478 | 0 | 1.9331 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 40.9915 | 3.286% | CZ 3C | 2.864 | 1.1679 | 0 | 0.51154 | 0 | 2.0656 | 0 | 0.56656 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 11.5804 | 3.286% | CZ 3C | 0 | 0 | 0.014592 | 0.00019972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014791 | 3.286% | CZ 3C | 29.9833 | 12.2272 | 1.5949 | 5.3771 | 0 | 21.6246 | 0 | 5.9313 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 122.8521 | 3.286%
CZ 4A | 0.30444 | 0.12399 | 0.015077 | 0.2627 | 0 | 0.20973 | 0 | 0.056194 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.4404 | 18.98% | CZ 4A | 9.772 | 3.9797 | 1.5385 | 11.219 | 0 | 6.732 | 0 | 1.8037 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 50.0741 | 18.98% | CZ 4A | 2.864 | 1.1664 | 0 | 2.0965 | 0 | 1.973 | 0 | 0.52864 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.0333 | 18.98% | CZ 4A | 0 | 0 | 0.015385 | 0.040659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056044 | 18.98% | CZ 4A | 29.9833 | 12.2109 | 1.6816 | 26.3919 | 0 | 20.6558 | 0 | 5.5343 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 142.5715 | 18.98%
CZ 4B | 0.30444 | 0.12408 | 0.014828 | 0.13058 | 0 | 0.19202 | 0 | 0.070398 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3046 | 0.5078% | CZ 4B | 9.772 | 3.9827 | 1.5131 | 5.0426 | 0 | 6.1635 | 0 | 2.2596 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 43.7626 | 0.5078% | CZ 4B | 2.864 | 1.1673 | 0 | 1.1139 | 0 | 1.8064 | 0 | 0.66226 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.0186 | 0.5078% | CZ 4B | 0 | 0 | 0.015131 | 0.012421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027552 | 0.5078% | CZ 4B | 29.9833 | 12.2201 | 1.6538 | 13.0186 | 0 | 18.9114 | 0 | 6.9332 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 128.834 | 0.5078%
CZ 4C | 0.30444 | 0.12384 | 0.015336 | 0.2164 | 0 | 0.092704 | 0 | 0.051821 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.2728 | 3.396% | CZ 4C | 9.772 | 3.9751 | 1.5648 | 8.1259 | 0 | 2.9756 | 0 | 1.6633 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 43.1059 | 3.396% | CZ 4C | 2.864 | 1.165 | 0 | 1.877 | 0 | 0.8721 | 0 | 0.4875 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 11.6705 | 3.396% | CZ 4C | 0 | 0 | 0.015648 | 0.017214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032863 | 3.396% | CZ 4C | 29.9833 | 12.1968 | 1.7104 | 21.5323 | 0 | 9.13 | 0 | 5.1036 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 125.77 | 3.396%
CZ 5A | 0.30444 | 0.12403 | 0.015834 | 0.37194 | 0 | 0.12294 | 0 | 0.053727 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.4611 | 17.55% | CZ 5A | 9.772 | 3.981 | 1.6158 | 16.92 | 0 | 3.9461 | 0 | 1.7245 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 52.9885 | 17.55% | CZ 5A | 2.864 | 1.1668 | 0 | 2.8289 | 0 | 1.1565 | 0 | 0.50542 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.9264 | 17.55% | CZ 5A | 0 | 0 | 0.016158 | 0.072677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088834 | 17.55% | CZ 5A | 29.9833 | 12.2147 | 1.766 | 37.5596 | 0 | 12.1079 | 0 | 5.2913 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 145.0365 | 17.55%
CZ 5B | 0.30444 | 0.12403 | 0.01562 | 0.23386 | 0 | 0.14302 | 0 | 0.065948 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.3552 | 6.239% | CZ 5B | 9.772 | 3.9811 | 1.5938 | 10.0202 | 0 | 4.5905 | 0 | 2.1168 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 47.1035 | 6.239% | CZ 5B | 2.864 | 1.1668 | 0 | 1.862 | 0 | 1.3454 | 0 | 0.6204 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 12.2634 | 6.239% | CZ 5B | 0 | 0 | 0.015938 | 0.036672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05261 | 6.239% | CZ 5B | 29.9833 | 12.2153 | 1.7421 | 23.5011 | 0 | 14.085 | 0 | 6.4949 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 134.1353 | 6.239%
CZ 5C | 0.30444 | 0.12384 | 0.015772 | 0.20815 | 0 | 0.060099 | 0 | 0.048748 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.2293 | 0.04746% | CZ 5C | 9.772 | 3.9749 | 1.6094 | 8.4536 | 0 | 1.929 | 0 | 1.5647 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 42.3328 | 0.04746% | CZ 5C | 2.864 | 1.165 | 0 | 1.7197 | 0 | 0.56537 | 0 | 0.45859 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 11.1774 | 0.04746% | CZ 5C | 0 | 0 | 0.016094 | 0.02586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041954 | 0.04746% | CZ 5C | 29.9833 | 12.1963 | 1.7591 | 20.83 | 0 | 5.9189 | 0 | 4.8009 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 121.6021 | 0.04746%
CZ 6A | 0.30444 | 0.12397 | 0.016413 | 0.53607 | 0 | 0.13216 | 0 | 0.058348 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.6396 | 3.432% | CZ 6A | 9.772 | 3.9792 | 1.6748 | 24.7009 | 0 | 4.2421 | 0 | 1.8728 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 61.2708 | 3.432% | CZ 6A | 2.864 | 1.1662 | 0 | 4.0351 | 0 | 1.2433 | 0 | 0.54889 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 14.2623 | 3.432% | CZ 6A | 0 | 0 | 0.016748 | 0.10933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12608 | 3.432% | CZ 6A | 29.9833 | 12.2093 | 1.8305 | 54.1931 | 0 | 13.0159 | 0 | 5.7464 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 163.0921 | 3.432%
CZ 6B | 0.30444 | 0.12388 | 0.016259 | 0.39855 | 0 | 0.096802 | 0 | 0.060556 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.4687 | 0.5173% | CZ 6B | 9.772 | 3.9762 | 1.6591 | 17.5257 | 0 | 3.1071 | 0 | 1.9437 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 53.0129 | 0.5173% | CZ 6B | 2.864 | 1.1654 | 0 | 3.1126 | 0 | 0.91065 | 0 | 0.56967 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.0271 | 0.5173% | CZ 6B | 0 | 0 | 0.016591 | 0.069054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085644 | 0.5173% | CZ 6B | 29.9833 | 12.2001 | 1.8133 | 40.1339 | 0 | 9.5335 | 0 | 5.9639 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 145.7417 | 0.5173%
CZ 7 | 0.30444 | 0.1238 | 0.017106 | 0.60654 | 0 | 0.11158 | 0 | 0.063519 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.6952 | 0.4099% | CZ 7 | 9.772 | 3.9737 | 1.7455 | 28.7411 | 0 | 3.5814 | 0 | 2.0388 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 64.8817 | 0.4099% | CZ 7 | 2.864 | 1.1646 | 0 | 4.4588 | 0 | 1.0497 | 0 | 0.59755 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 14.5394 | 0.4099% | CZ 7 | 0 | 0 | 0.017455 | 0.13528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15273 | 0.4099% | CZ 7 | 29.9833 | 12.1925 | 1.9078 | 61.4651 | 0 | 10.9889 | 0 | 6.2557 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 168.9069 | 0.4099%
CZ 8 | 0.30444 | 0.12312 | 0.018027 | 0.7567 | 0 | 0.061608 | 0 | 0.06347 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.7956 | 0.04597% | CZ 8 | 9.772 | 3.952 | 1.8395 | 38.2164 | 0 | 1.9775 | 0 | 2.0372 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 72.8237 | 0.04597% | CZ 8 | 2.864 | 1.1583 | 0 | 5.2452 | 0 | 0.57957 | 0 | 0.59708 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 14.8489 | 0.04597% | CZ 8 | 0 | 0 | 0.018395 | 0.2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22159 | 0.04597% | CZ 8 | 29.9833 | 12.1258 | 2.0106 | 77.1217 | 0 | 6.0675 | 0 | 6.2508 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 179.6733 | 0.04597%
US Weighted | 0.30444 | 0.12408 | 0.014609 | 0.19525 | 0 | 0.26654 | 0 | 0.062225 | 0 | 8.2614e-05 | 0 | 0.096361 | 0.018594 | 0 | 0 | 0.35319 | 1.4354 | 100% | US Weighted | 9.772 | 3.9826 | 1.4908 | 8.5074 | 0 | 8.5552 | 0 | 1.9973 | 0 | 0.0026517 | 0 | 3.093 | 0.59682 | 0 | 0 | 11.3367 | 49.3343 | 100% | US Weighted | 2.864 | 1.1672 | 0 | 1.5355 | 0 | 2.5074 | 0 | 0.58537 | 0 | 0.00077718 | 0 | 0.9065 | 0.17492 | 0 | 0 | 3.3226 | 13.0643 | 100% | US Weighted | 0 | 0 | 0.014908 | 0.032682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04759 | 100% | US Weighted | 29.9833 | 12.2196 | 1.6294 | 19.6474 | 0 | 26.2499 | 0 | 6.1283 | 0 | 0.0081363 | 0 | 9.4902 | 1.8312 | 0 | 0 | 34.7842 | 141.9715 | 100%
Building Type: | Medium Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Medium Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 53628 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 53628 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 53628 | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.16913 | 0.099164 | 0.00083658 | 2.7538e-05 | 0 | 0.41419 | 0 | 0.027841 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.75979 | 0% | CZ 0A | 5.4288 | 3.183 | 0.085365 | 0.00088391 | 0 | 13.2947 | 0 | 0.89363 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 24.4461 | 0% | CZ 0A | 1.5911 | 0.93287 | 0 | 0.00025906 | 0 | 3.8965 | 0 | 0.26191 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 7.1397 | 0% | CZ 0A | 0 | 0 | 0.00085365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00085365 | 0% | CZ 0A | 16.6571 | 9.7662 | 0.093304 | 0.0027121 | 0 | 40.792 | 0 | 2.7419 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 74.8391 | 0%
CZ 0B | 0.16897 | 0.098652 | 0.00092664 | 0.0039379 | 0 | 0.26245 | 0 | 0.032142 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.61567 | 0% | CZ 0B | 5.4235 | 3.1665 | 0.094555 | 0.1264 | 0 | 8.424 | 0 | 1.0317 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 19.8264 | 0% | CZ 0B | 1.5895 | 0.92805 | 0 | 0.037045 | 0 | 2.4689 | 0 | 0.30237 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 5.7831 | 0% | CZ 0B | 0 | 0 | 0.00094555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00094555 | 0% | CZ 0B | 16.6409 | 9.7158 | 0.10335 | 0.38783 | 0 | 25.8473 | 0 | 3.1656 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 60.6465 | 0%
CZ 1A | 0.16867 | 0.098531 | 0.0008054 | 0.00094731 | 0 | 0.23824 | 0 | 0.027345 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.58314 | 2.823% | CZ 1A | 5.414 | 3.1626 | 0.082184 | 0.030407 | 0 | 7.6471 | 0 | 0.87772 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 18.7737 | 2.823% | CZ 1A | 1.5867 | 0.92691 | 0 | 0.0089116 | 0 | 2.2412 | 0 | 0.25725 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 5.4782 | 2.823% | CZ 1A | 0 | 0 | 0.00082184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00082184 | 2.823% | CZ 1A | 16.6116 | 9.7039 | 0.089827 | 0.093296 | 0 | 23.4634 | 0 | 2.6931 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 57.4408 | 2.823%
CZ 1B | 0.16862 | 0.098465 | 0.00082792 | 0.019181 | 0 | 0.21108 | 0 | 0.031068 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.57784 | 0% | CZ 1B | 5.4124 | 3.1605 | 0.084481 | 0.60318 | 0 | 6.7754 | 0 | 0.99723 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 18.5929 | 0% | CZ 1B | 1.5863 | 0.92629 | 0 | 0.18212 | 0 | 1.9857 | 0 | 0.29227 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 5.4298 | 0% | CZ 1B | 0 | 0 | 0.00084481 | -0.00018204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00066277 | 0% | CZ 1B | 16.6067 | 9.6974 | 0.092338 | 1.8867 | 0 | 20.7887 | 0 | 3.0598 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 56.9173 | 0%
CZ 2A | 0.1689 | 0.098311 | 0.00074824 | 0.037472 | 0 | 0.23503 | 0 | 0.026255 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.6153 | 15.52% | CZ 2A | 5.4212 | 3.1556 | 0.076351 | 1.3202 | 0 | 7.5438 | 0 | 0.84272 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 19.9196 | 15.52% | CZ 2A | 1.5889 | 0.92484 | 0 | 0.33673 | 0 | 2.211 | 0 | 0.24699 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 5.7655 | 15.52% | CZ 2A | 0 | 0 | 0.00076351 | 0.0017126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0024761 | 15.52% | CZ 2A | 16.6338 | 9.6822 | 0.083452 | 3.7124 | 0 | 23.1466 | 0 | 2.5857 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 60.6299 | 15.52%
CZ 2B | 0.16875 | 0.098399 | 0.00074305 | 0.045483 | 0 | 0.13515 | 0 | 0.030198 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.52731 | 3.865% | CZ 2B | 5.4166 | 3.1584 | 0.075821 | 1.3644 | 0 | 4.3379 | 0 | 0.9693 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 16.8822 | 3.865% | CZ 2B | 1.5875 | 0.92567 | 0 | 0.44071 | 0 | 1.2714 | 0 | 0.28408 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 4.9665 | 3.865% | CZ 2B | 0 | 0 | 0.00075821 | -0.0013927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00063449 | 3.865% | CZ 2B | 16.6197 | 9.6908 | 0.082872 | 4.4616 | 0 | 13.3099 | 0 | 2.9741 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 51.9247 | 3.865%
CZ 3A | 0.16836 | 0.098129 | 0.00066511 | 0.08492 | 0 | 0.12084 | 0 | 0.021683 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.54319 | 14.49% | CZ 3A | 5.4041 | 3.1497 | 0.067868 | 3.9233 | 0 | 3.8788 | 0 | 0.69599 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 18.6794 | 14.49% | CZ 3A | 1.5838 | 0.92313 | 0 | 0.6378 | 0 | 1.1368 | 0 | 0.20398 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 4.9427 | 14.49% | CZ 3A | 0 | 0 | 0.00067868 | 0.017471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018149 | 14.49% | CZ 3A | 16.5812 | 9.6643 | 0.07418 | 8.5867 | 0 | 11.9012 | 0 | 2.1355 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 53.7288 | 14.49%
CZ 3B | 0.16868 | 0.09863 | 0.00068243 | 0.048563 | 0 | 0.07942 | 0 | 0.022278 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.46684 | 8.895% | CZ 3B | 5.4141 | 3.1658 | 0.069635 | 1.4034 | 0 | 2.5492 | 0 | 0.71508 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 14.877 | 8.895% | CZ 3B | 1.5868 | 0.92785 | 0 | 0.47776 | 0 | 0.74713 | 0 | 0.20958 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 4.4062 | 8.895% | CZ 3B | 0 | 0 | 0.00069635 | -0.0022676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0015712 | 8.895% | CZ 3B | 16.6121 | 9.7136 | 0.076111 | 4.7538 | 0 | 7.8217 | 0 | 2.1941 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 45.9572 | 8.895%
CZ 3C | 0.16841 | 0.098707 | 0.00064778 | 0.051777 | 0 | 0.11298 | 0 | 0.026145 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.50726 | 3.286% | CZ 3C | 5.4055 | 3.1683 | 0.0661 | 1.593 | 0 | 3.6265 | 0 | 0.83918 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 16.2583 | 3.286% | CZ 3C | 1.5843 | 0.92857 | 0 | 0.49636 | 0 | 1.0629 | 0 | 0.24595 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 4.7751 | 3.286% | CZ 3C | 0 | 0 | 0.000661 | -0.0010056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00034464 | 3.286% | CZ 3C | 16.5855 | 9.7212 | 0.072248 | 5.0865 | 0 | 11.1272 | 0 | 2.5749 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 49.9532 | 3.286%
CZ 4A | 0.16825 | 0.098206 | 0.00062354 | 0.18897 | 0 | 0.089741 | 0 | 0.02067 | 0 | 0 | 0 | 0.0052708 | 0.012144 | 0 | 0 | 0.031173 | 0.61504 | 18.98% | CZ 4A | 5.4003 | 3.1522 | 0.063626 | 6.9455 | 0 | 2.8805 | 0 | 0.66346 | 0 | 0 | 0 | 0.16918 | 0.3898 | 0 | 0 | 1.0006 | 20.6651 | 18.98% | CZ 4A | 1.5827 | 0.92386 | 0 | 1.6593 | 0 | 0.84422 | 0 | 0.19445 | 0 | 0 | 0 | 0.049584 | 0.11425 | 0 | 0 | 0.29326 | 5.6617 | 18.98% | CZ 4A | 0 | 0 | 0.00063626 | 0.012838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013475 | 18.98% | CZ 4A | 16.5698 | 9.6719 | 0.069543 | 18.7747 | 0 | 8.8382 | 0 | 2.0357 | 0 | 0 | 0 | 0.51909 | 1.196 | 0 | 0 | 3.0701 | 60.745 | 18.98%
CZ 4B | 0.16897 | 0.09847 | 0.00064259 | 0.10943 | 0 | 0.071648 | 0 | 0.020857 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.51862 | 0.5078% | CZ 4B | 5.4237 | 3.1607 | 0.06557 | 3.4985 | 0 | 2.2998 | 0 | 0.66947 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 16.6774 | 0.5078% | CZ 4B | 1.5896 | 0.92634 | 0 | 1.0313 | 0 | 0.67402 | 0 | 0.19621 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 4.8746 | 0.5078% | CZ 4B | 0 | 0 | 0.0006557 | -0.00020325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00045245 | 0.5078% | CZ 4B | 16.6414 | 9.6979 | 0.071668 | 10.7746 | 0 | 7.0563 | 0 | 2.0541 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 51.0818 | 0.5078%
CZ 4C | 0.16757 | 0.097655 | 0.00059756 | 0.17213 | 0 | 0.047564 | 0 | 0.020488 | 0 | 0 | 0 | 0.0052708 | 0.012144 | 0 | 0 | 0.031173 | 0.5546 | 3.396% | CZ 4C | 5.3788 | 3.1345 | 0.060975 | 5.5925 | 0 | 1.5267 | 0 | 0.65763 | 0 | 0 | 0 | 0.16918 | 0.3898 | 0 | 0 | 1.0006 | 17.9106 | 3.396% | CZ 4C | 1.5764 | 0.91868 | 0 | 1.6103 | 0 | 0.44745 | 0 | 0.19274 | 0 | 0 | 0 | 0.049584 | 0.11425 | 0 | 0 | 0.29326 | 5.2026 | 3.396% | CZ 4C | 0 | 0 | 0.00060975 | 0.00098267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015924 | 3.396% | CZ 4C | 16.5036 | 9.6176 | 0.066646 | 16.9652 | 0 | 4.6843 | 0 | 2.0178 | 0 | 0 | 0 | 0.51909 | 1.196 | 0 | 0 | 3.0701 | 54.6405 | 3.396%
CZ 5A | 0.16848 | 0.09803 | 0.00059236 | 0.24452 | 0 | 0.044937 | 0 | 0.019822 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.62498 | 17.55% | CZ 5A | 5.4078 | 3.1465 | 0.060445 | 9.6806 | 0 | 1.4424 | 0 | 0.63624 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 21.9338 | 17.55% | CZ 5A | 1.5849 | 0.9222 | 0 | 2.0539 | 0 | 0.42273 | 0 | 0.18647 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 5.6274 | 17.55% | CZ 5A | 0 | 0 | 0.00060445 | 0.026727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027331 | 17.55% | CZ 5A | 16.5926 | 9.6545 | 0.066066 | 24.4238 | 0 | 4.4256 | 0 | 1.9522 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 61.9004 | 17.55%
CZ 5B | 0.16854 | 0.098272 | 0.00060622 | 0.1757 | 0 | 0.052107 | 0 | 0.02062 | 0 | 0 | 0 | 0.0052708 | 0.01215 | 0 | 0 | 0.031173 | 0.56444 | 6.239% | CZ 5B | 5.4097 | 3.1543 | 0.061859 | 6.298 | 0 | 1.6725 | 0 | 0.66187 | 0 | 0 | 0 | 0.16918 | 0.38998 | 0 | 0 | 1.0006 | 18.818 | 6.239% | CZ 5B | 1.5855 | 0.92448 | 0 | 1.5644 | 0 | 0.49019 | 0 | 0.19398 | 0 | 0 | 0 | 0.049584 | 0.1143 | 0 | 0 | 0.29326 | 5.2156 | 6.239% | CZ 5B | 0 | 0 | 0.00061859 | 0.009604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010223 | 6.239% | CZ 5B | 16.5985 | 9.6784 | 0.067612 | 17.427 | 0 | 5.1318 | 0 | 2.0308 | 0 | 0 | 0 | 0.51909 | 1.1966 | 0 | 0 | 3.0701 | 55.7199 | 6.239%
CZ 5C | 0.16745 | 0.097589 | 0.0005889 | 0.16334 | 0 | 0.034197 | 0 | 0.016842 | 0 | 0 | 0 | 0.0052708 | 0.012144 | 0 | 0 | 0.031173 | 0.52859 | 0.04746% | CZ 5C | 5.3749 | 3.1324 | 0.060091 | 5.5719 | 0 | 1.0976 | 0 | 0.5406 | 0 | 0 | 0 | 0.16918 | 0.3898 | 0 | 0 | 1.0006 | 17.3371 | 0.04746% | CZ 5C | 1.5753 | 0.91805 | 0 | 1.4923 | 0 | 0.3217 | 0 | 0.15844 | 0 | 0 | 0 | 0.049584 | 0.11425 | 0 | 0 | 0.29326 | 4.9229 | 0.04746% | CZ 5C | 0 | 0 | 0.00060091 | 0.004802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054029 | 0.04746% | CZ 5C | 16.4917 | 9.6111 | 0.06568 | 16.1476 | 0 | 3.3679 | 0 | 1.6587 | 0 | 0 | 0 | 0.51909 | 1.196 | 0 | 0 | 3.0701 | 52.1279 | 0.04746%
CZ 6A | 0.16831 | 0.097969 | 0.00056465 | 0.34638 | 0 | 0.04638 | 0 | 0.022785 | 0 | 0 | 0 | 0.0052708 | 0.012144 | 0 | 0 | 0.031173 | 0.73098 | 3.432% | CZ 6A | 5.4025 | 3.1446 | 0.057617 | 13.9989 | 0 | 1.4887 | 0 | 0.73135 | 0 | 0 | 0 | 0.16918 | 0.3898 | 0 | 0 | 1.0006 | 26.3832 | 3.432% | CZ 6A | 1.5834 | 0.92163 | 0 | 2.871 | 0 | 0.43631 | 0 | 0.21435 | 0 | 0 | 0 | 0.049584 | 0.11425 | 0 | 0 | 0.29326 | 6.4837 | 3.432% | CZ 6A | 0 | 0 | 0.00057617 | 0.04203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042607 | 3.432% | CZ 6A | 16.5763 | 9.6485 | 0.062975 | 34.6504 | 0 | 4.5677 | 0 | 2.244 | 0 | 0 | 0 | 0.51909 | 1.196 | 0 | 0 | 3.0701 | 72.5351 | 3.432%
CZ 6B | 0.16819 | 0.0976 | 0.00057504 | 0.28233 | 0 | 0.038195 | 0 | 0.021342 | 0 | 0 | 0 | 0.0052708 | 0.012144 | 0 | 0 | 0.031173 | 0.65682 | 0.5173% | CZ 6B | 5.3986 | 3.1328 | 0.058677 | 10.6161 | 0 | 1.226 | 0 | 0.68503 | 0 | 0 | 0 | 0.16918 | 0.3898 | 0 | 0 | 1.0006 | 22.6767 | 0.5173% | CZ 6B | 1.5822 | 0.91816 | 0 | 2.447 | 0 | 0.35932 | 0 | 0.20077 | 0 | 0 | 0 | 0.049584 | 0.11425 | 0 | 0 | 0.29326 | 5.9645 | 0.5173% | CZ 6B | 0 | 0 | 0.00058677 | 0.02267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023257 | 0.5173% | CZ 6B | 16.5644 | 9.6122 | 0.064134 | 28.0952 | 0 | 3.7617 | 0 | 2.1019 | 0 | 0 | 0 | 0.51909 | 1.196 | 0 | 0 | 3.0701 | 64.9847 | 0.5173%
CZ 7 | 0.16813 | 0.097529 | 0.00054559 | 0.46383 | 0 | 0.047371 | 0 | 0.027241 | -0.011423 | 0 | 0 | 0.0052708 | 0.012144 | 0 | 0 | 0.031173 | 0.84181 | 0.4099% | CZ 7 | 5.3966 | 3.1305 | 0.055673 | 22.9698 | 0 | 1.5205 | 0 | 0.87436 | -0.36665 | 0 | 0 | 0.16918 | 0.3898 | 0 | 0 | 1.0006 | 35.1403 | 0.4099% | CZ 7 | 1.5817 | 0.91748 | 0 | 3.2764 | 0 | 0.44563 | 0 | 0.25626 | -0.10746 | 0 | 0 | 0.049584 | 0.11425 | 0 | 0 | 0.29326 | 6.827 | 0.4099% | CZ 7 | 0 | 0 | 0.00055673 | 0.11791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11846 | 0.4099% | CZ 7 | 16.5584 | 9.6051 | 0.06085 | 47.1877 | 0 | 4.6653 | 0 | 2.6828 | -1.125 | 0 | 0 | 0.51909 | 1.196 | 0 | 0 | 3.0701 | 84.4205 | 0.4099%
CZ 8 | 0.16321 | 0.094709 | 0.0004971 | 0.54945 | 0 | 0.032842 | 0 | 0.025913 | -0.011665 | 0 | 0 | 0.0052708 | 0.012139 | 0 | 0 | 0.031173 | 0.90354 | 0.04597% | CZ 8 | 5.2386 | 3.0399 | 0.050724 | 29.0545 | 0 | 1.0542 | 0 | 0.83176 | -0.37442 | 0 | 0 | 0.16918 | 0.38963 | 0 | 0 | 1.0006 | 40.4546 | 0.04597% | CZ 8 | 1.5353 | 0.89096 | 0 | 3.6331 | 0 | 0.30895 | 0 | 0.24377 | -0.10974 | 0 | 0 | 0.049584 | 0.11419 | 0 | 0 | 0.29326 | 6.9594 | 0.04597% | CZ 8 | 0 | 0 | 0.00050724 | 0.16658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16709 | 0.04597% | CZ 8 | 16.0735 | 9.3274 | 0.055442 | 56.2425 | 0 | 3.2344 | 0 | 2.5521 | -1.1488 | 0 | 0 | 0.51909 | 1.1955 | 0 | 0 | 3.0701 | 91.1212 | 0.04597%
US Weighted | 0.16848 | 0.098222 | 0.0006547 | 0.13764 | 0 | 0.10887 | 0 | 0.02251 | -5.2186e-05 | 0 | 0 | 0.0052708 | 0.012148 | 0 | 0 | 0.031173 | 0.58492 | 100% | US Weighted | 5.4078 | 3.1527 | 0.066806 | 5.2672 | 0 | 3.4945 | 0 | 0.72251 | -0.0016751 | 0 | 0 | 0.16918 | 0.38993 | 0 | 0 | 1.0006 | 19.6695 | 100% | US Weighted | 1.5849 | 0.92401 | 0 | 1.1807 | 0 | 1.0242 | 0 | 0.21176 | -0.00049093 | 0 | 0 | 0.049584 | 0.11428 | 0 | 0 | 0.29326 | 5.3821 | 100% | US Weighted | 0 | 0 | 0.00066806 | 0.012388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013056 | 100% | US Weighted | 16.5926 | 9.6734 | 0.073019 | 13.7143 | 0 | 10.7221 | 0 | 2.2169 | -0.0051396 | 0 | 0 | 0.51909 | 1.1964 | 0 | 0 | 3.0701 | 57.7727 | 100%
Building Type: | Medium Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Medium Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Medium Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Medium Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 53628 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 53628 | [17 empty] | Prototype Floor Area: | 53628 | Building Type: | Medium Office | [15 empty] | Prototype Floor Area: | 53628 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 55.55% | 79.8% | 6.947% | 100% |  | 44.31% |  | 30.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.24% | 0% | CZ 0A | 55.55% | 79.8% | 6.947% | 100% |  | 44.31% |  | 30.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 38.81% | 0% | CZ 0A | 55.55% | 79.8% |  | 100% |  | 44.31% |  | 30.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.45% | 0% | CZ 0A |  |  | 6.947% | [13 empty] | 6.947% | 0% | CZ 0A | 55.55% | 79.8% | 6.947% | 100% |  | 44.31% |  | 30.17% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.22% | 0%
CZ 0B | 55.5% | 79.37% | 7.618% | 94.83% |  | 35.36% |  | 35.64% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 35.27% | 0% | CZ 0B | 55.5% | 79.37% | 7.618% | 94.83% |  | 35.36% |  | 35.64% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 34.85% | 0% | CZ 0B | 55.5% | 79.37% |  | 94.83% |  | 35.36% |  | 35.64% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 35.46% | 0% | CZ 0B |  |  | 7.618% | [13 empty] | 7.618% | 0% | CZ 0B | 55.5% | 79.37% | 7.618% | 94.83% |  | 35.36% |  | 35.64% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 35.24% | 0%
CZ 1A | 55.4% | 79.26% | 6.427% | 99.42% |  | 40.37% |  | 33.58% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 36.86% | 2.823% | CZ 1A | 55.4% | 79.26% | 6.427% | 99.42% |  | 40.37% |  | 33.58% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 36.34% | 2.823% | CZ 1A | 55.4% | 79.26% |  | 99.42% |  | 40.37% |  | 33.58% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 37.1% | 2.823% | CZ 1A |  |  | 6.427% | [13 empty] | 6.427% | 2.823% | CZ 1A | 55.4% | 79.26% | 6.427% | 99.42% |  | 40.37% |  | 33.58% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 36.83% | 2.823%
CZ 1B | 55.39% | 79.31% | 6.565% | 89.39% |  | 35.33% |  | 36.65% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 35.82% | 0% | CZ 1B | 55.39% | 79.31% | 6.565% | 85.56% |  | 35.33% |  | 36.65% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 35.3% | 0% | CZ 1B | 55.39% | 79.31% |  | 91.2% |  | 35.33% |  | 36.65% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 36.07% | 0% | CZ 1B |  |  | 6.565% | -76.87% | [12 empty] | 5.057% | 0% | CZ 1B | 55.39% | 79.31% | 6.565% | 89.15% |  | 35.33% |  | 36.65% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 35.79% | 0%
CZ 2A | 55.48% | 79.21% | 5.698% | 90.57% |  | 43.77% |  | 36.79% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.45% | 15.52% | CZ 2A | 55.48% | 79.21% | 5.698% | 88.73% |  | 43.77% |  | 36.79% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 38.95% | 15.52% | CZ 2A | 55.48% | 79.21% |  | 91.57% |  | 43.77% |  | 36.79% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.69% | 15.52% | CZ 2A |  |  | 5.698% | 73.41% | [12 empty] | 15.74% | 15.52% | CZ 2A | 55.48% | 79.21% | 5.698% | 90.45% |  | 43.77% |  | 36.79% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.42% | 15.52%
CZ 2B | 55.43% | 79.22% | 5.643% | 92.34% |  | 36.16% |  | 36.22% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 37.23% | 3.865% | CZ 2B | 55.43% | 79.22% | 5.643% | 84.66% |  | 36.16% |  | 36.22% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 36.37% | 3.865% | CZ 2B | 55.43% | 79.22% |  | 95.96% |  | 36.16% |  | 36.22% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 37.64% | 3.865% | CZ 2B |  |  | 5.643% | -311.5% | [12 empty] | -4.57% | 3.865% | CZ 2B | 55.43% | 79.22% | 5.643% | 91.86% |  | 36.16% |  | 36.22% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 37.18% | 3.865%
CZ 3A | 55.3% | 79.03% | 4.685% | 66.24% |  | 40.83% |  | 37.16% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 38.98% | 14.49% | CZ 3A | 55.3% | 79.03% | 4.685% | 66.87% |  | 40.83% |  | 37.16% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.34% | 14.49% | CZ 3A | 55.3% | 79.03% |  | 65.73% |  | 40.83% |  | 37.16% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 38.79% | 14.49% | CZ 3A |  |  | 4.685% | 68.35% | [12 empty] | 45.32% | 14.49% | CZ 3A | 55.3% | 79.03% | 4.685% | 66.3% |  | 40.83% |  | 37.16% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39% | 14.49%
CZ 3B | 55.4% | 79.43% | 4.904% | 79.83% |  | 32.08% |  | 31.76% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 36.21% | 8.895% | CZ 3B | 55.4% | 79.43% | 4.904% | 61.7% |  | 32.08% |  | 31.76% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 34.86% | 8.895% | CZ 3B | 55.4% | 79.43% |  | 90.31% |  | 32.08% |  | 31.76% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 36.86% | 8.895% | CZ 3B |  |  | 4.904% | -48.29% | [12 empty] | -8.315% | 8.895% | CZ 3B | 55.4% | 79.43% | 4.904% | 78.56% |  | 32.08% |  | 31.76% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 36.12% | 8.895%
CZ 3C | 55.32% | 79.5% | 4.53% | 94.88% |  | 51.46% |  | 43.41% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 40.73% | 3.286% | CZ 3C | 55.32% | 79.5% | 4.53% | 90.24% |  | 51.46% |  | 43.41% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.66% | 3.286% | CZ 3C | 55.32% | 79.5% |  | 97.03% |  | 51.46% |  | 43.41% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 41.23% | 3.286% | CZ 3C |  |  | 4.53% | -503.5% | [12 empty] | -2.33% | 3.286% | CZ 3C | 55.32% | 79.5% | 4.53% | 94.59% |  | 51.46% |  | 43.41% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 40.66% | 3.286%
CZ 4A | 55.26% | 79.21% | 4.136% | 71.93% |  | 42.79% |  | 36.78% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 42.7% | 18.98% | CZ 4A | 55.26% | 79.21% | 4.136% | 61.91% |  | 42.79% |  | 36.78% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 41.27% | 18.98% | CZ 4A | 55.26% | 79.21% |  | 79.15% |  | 42.79% |  | 36.78% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 43.44% | 18.98% | CZ 4A |  |  | 4.136% | 31.58% | [12 empty] | 24.04% | 18.98% | CZ 4A | 55.26% | 79.21% | 4.136% | 71.14% |  | 42.79% |  | 36.78% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 42.61% | 18.98%
CZ 4B | 55.5% | 79.36% | 4.334% | 83.81% |  | 37.31% |  | 29.63% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.75% | 0.5078% | CZ 4B | 55.5% | 79.36% | 4.334% | 69.38% |  | 37.31% |  | 29.63% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 38.11% | 0.5078% | CZ 4B | 55.5% | 79.36% |  | 92.59% |  | 37.31% |  | 29.63% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 40.56% | 0.5078% | CZ 4B |  |  | 4.334% | -1.636% | [12 empty] | 1.642% | 0.5078% | CZ 4B | 55.5% | 79.36% | 4.334% | 82.76% |  | 37.31% |  | 29.63% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.65% | 0.5078%
CZ 4C | 55.04% | 78.85% | 3.897% | 79.54% |  | 51.31% |  | 39.54% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 43.57% | 3.396% | CZ 4C | 55.04% | 78.85% | 3.897% | 68.82% |  | 51.31% |  | 39.54% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 41.55% | 3.396% | CZ 4C | 55.04% | 78.85% |  | 85.79% |  | 51.31% |  | 39.54% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 44.58% | 3.396% | CZ 4C |  |  | 3.897% | 5.708% | [12 empty] | 4.846% | 3.396% | CZ 4C | 55.04% | 78.85% | 3.897% | 78.79% |  | 51.31% |  | 39.54% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 43.44% | 3.396%
CZ 5A | 55.34% | 79.04% | 3.741% | 65.74% |  | 36.55% |  | 36.89% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 42.77% | 17.55% | CZ 5A | 55.34% | 79.04% | 3.741% | 57.21% |  | 36.55% |  | 36.89% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 41.39% | 17.55% | CZ 5A | 55.34% | 79.04% |  | 72.6% |  | 36.55% |  | 36.89% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 43.53% | 17.55% | CZ 5A |  |  | 3.741% | 36.77% | [12 empty] | 30.77% | 17.55% | CZ 5A | 55.34% | 79.04% | 3.741% | 65.03% |  | 36.55% |  | 36.89% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 42.68% | 17.55%
CZ 5B | 55.36% | 79.23% | 3.881% | 75.13% |  | 36.43% |  | 31.27% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 41.65% | 6.239% | CZ 5B | 55.36% | 79.23% | 3.881% | 62.85% |  | 36.43% |  | 31.27% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 39.95% | 6.239% | CZ 5B | 55.36% | 79.23% |  | 84.02% |  | 36.43% |  | 31.27% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 42.53% | 6.239% | CZ 5B |  |  | 3.881% | 26.19% | [12 empty] | 19.43% | 6.239% | CZ 5B | 55.36% | 79.23% | 3.881% | 74.15% |  | 36.43% |  | 31.27% |  | 0% |  | 5.47% | 65.34% |  |  | 8.826% | 41.54% | 6.239%
CZ 5C | 55% | 78.8% | 3.734% | 78.47% |  | 56.9% |  | 34.55% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 43% | 0.04746% | CZ 5C | 55% | 78.8% | 3.734% | 65.91% |  | 56.9% |  | 34.55% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 40.95% | 0.04746% | CZ 5C | 55% | 78.8% |  | 86.78% |  | 56.9% |  | 34.55% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 44.04% | 0.04746% | CZ 5C |  |  | 3.734% | 18.57% | [12 empty] | 12.88% | 0.04746% | CZ 5C | 55% | 78.8% | 3.734% | 77.52% |  | 56.9% |  | 34.55% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 42.87% | 0.04746%
CZ 6A | 55.29% | 79.03% | 3.44% | 64.61% |  | 35.09% |  | 39.05% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 44.58% | 3.432% | CZ 6A | 55.29% | 79.03% | 3.44% | 56.67% |  | 35.09% |  | 39.05% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 43.06% | 3.432% | CZ 6A | 55.29% | 79.03% |  | 71.15% |  | 35.09% |  | 39.05% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 45.46% | 3.432% | CZ 6A |  |  | 3.44% | 38.44% | [12 empty] | 33.79% | 3.432% | CZ 6A | 55.29% | 79.03% | 3.44% | 63.94% |  | 35.09% |  | 39.05% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 44.47% | 3.432%
CZ 6B | 55.25% | 78.79% | 3.537% | 70.84% |  | 39.46% |  | 35.24% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 44.72% | 0.5173% | CZ 6B | 55.25% | 78.79% | 3.537% | 60.57% |  | 39.46% |  | 35.24% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 42.78% | 0.5173% | CZ 6B | 55.25% | 78.79% |  | 78.61% |  | 39.46% |  | 35.24% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 45.79% | 0.5173% | CZ 6B |  |  | 3.537% | 32.83% | [12 empty] | 27.16% | 0.5173% | CZ 6B | 55.25% | 78.79% | 3.537% | 70% |  | 39.46% |  | 35.24% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 44.59% | 0.5173%
CZ 7 | 55.23% | 78.78% | 3.19% | 76.47% |  | 42.46% |  | 42.89% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 49.66% | 0.4099% | CZ 7 | 55.23% | 78.78% | 3.19% | 79.92% |  | 42.46% |  | 42.89% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 54.16% | 0.4099% | CZ 7 | 55.23% | 78.78% |  | 73.48% |  | 42.46% |  | 42.89% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 46.96% | 0.4099% | CZ 7 |  |  | 3.19% | 87.16% | [12 empty] | 77.56% | 0.4099% | CZ 7 | 55.23% | 78.78% | 3.19% | 76.77% |  | 42.46% |  | 42.89% |  | 0% |  | 5.47% | 65.31% |  |  | 8.826% | 49.98% | 0.4099%
CZ 8 | 53.61% | 76.92% | 2.757% | 72.61% |  | 53.31% |  | 40.83% |  | 0% |  | 5.47% | 65.28% |  |  | 8.826% | 50.32% | 0.04597% | CZ 8 | 53.61% | 76.92% | 2.757% | 76.03% |  | 53.31% |  | 40.83% |  | 0% |  | 5.47% | 65.28% |  |  | 8.826% | 55.55% | 0.04597% | CZ 8 | 53.61% | 76.92% |  | 69.26% |  | 53.31% |  | 40.83% |  | 0% |  | 5.47% | 65.28% |  |  | 8.826% | 46.87% | 0.04597% | CZ 8 |  |  | 2.757% | 81.98% | [12 empty] | 75.4% | 0.04597% | CZ 8 | 53.61% | 76.92% | 2.757% | 72.93% |  | 53.31% |  | 40.83% |  | 0% |  | 5.47% | 65.28% |  |  | 8.826% | 50.71% | 0.04597%
US Weighted | 55.34% | 79.16% | 4.538% | 76.22% | 0% | 40.16% | 0% | 36.32% | 0% | 0% | 0% | 5.47% | 65.34% | 0% | 0% | 8.826% | 40.71% | 100% | US Weighted | 55.34% | 79.16% | 4.538% | 69.04% | 0% | 40.16% | 0% | 36.32% | 0% | 0% | 0% | 5.47% | 65.34% | 0% | 0% | 8.826% | 39.74% | 100% | US Weighted | 55.34% | 79.16% | 0% | 81.08% | 0% | 40.16% | 0% | 36.32% | 0% | 0% | 0% | 5.47% | 65.34% | 0% | 0% | 8.826% | 41.21% | 100% | US Weighted | 0% | 0% | 4.538% | 4.571% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 21.2% | 100% | US Weighted | 55.34% | 79.16% | 4.538% | 75.67% | 0% | 40.16% | 0% | 36.32% | 0% | 0% | 0% | 5.47% | 65.34% | 0% | 0% | 8.826% | 40.64% | 100%

## OffL
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Large Office |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 498588 |  | Building Type: | Large Office |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 |  | Building Type: | Large Office |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Large Office |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Large Office | [14 empty] | Prototype Floor Area: | 498588 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.15298 | 0.020384 | 0.010275 | 0.012214 | 0.055024 | 0.16797 | 0.056842 | 0.12304 | 0.0020252 | 0.021646 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.6077 |  | STD2019 | 4.9103 | 0.65429 | 1.0485 | 1.2463 | 1.7661 | 5.3915 | 1.8245 | 3.9495 | 0.065004 | 0.6948 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 53.1759 |  | STD2019 | 1.4391 | 0.19176 | 0 | 0 | 0.51763 | 1.5802 | 0.53473 | 1.1575 | 0.019052 | 0.20363 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.9124 |  | STD2019 | 0 | 0 | 0.010485 | 0.012463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022948 |  | STD2019 | 15.0663 | 2.0076 | 1.146 | 1.3623 | 5.4191 | 16.5426 | 5.5981 | 12.1181 | 0.19945 | 2.1318 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 158.626
STD2016 | 0.18798 | 0.020384 | 0.010276 | 0.014679 | 0.050754 | 0.18466 | 0.064517 | 0.12745 | 0.0022936 | 0.022668 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6709 |  | STD2016 | 6.0336 | 0.65429 | 1.0485 | 1.4978 | 1.6291 | 5.9273 | 2.0708 | 4.0907 | 0.07362 | 0.72758 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 55.379 |  | STD2016 | 1.7684 | 0.19176 | 0 | 0 | 0.47746 | 1.7372 | 0.60693 | 1.1989 | 0.021577 | 0.21324 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 15.4844 |  | STD2016 | 0 | 0 | 0.010485 | 0.014978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025463 |  | STD2016 | 18.5129 | 2.0076 | 1.146 | 1.6371 | 4.9986 | 18.1868 | 6.3539 | 12.5515 | 0.22589 | 2.2324 | 0 | 11.0904 | 0.32083 | 0 | 54.5001 | 31.125 | 164.889
STD2013 | 0.20214 | 0.040368 | 0.010554 | 0.017787 | 0.030376 | 0.21094 | 0.071731 | 0.12856 | 0.0026257 | 0.024938 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.7268 |  | STD2013 | 6.4882 | 1.2957 | 1.0769 | 1.815 | 0.97499 | 6.7709 | 2.3024 | 4.1263 | 0.084279 | 0.80045 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 57.4079 |  | STD2013 | 1.9016 | 0.37975 | 0 | 0 | 0.28575 | 1.9844 | 0.67479 | 1.2094 | 0.024701 | 0.2346 | 0 | 1.0594 | 0.0445 | 0 | 5.2059 | 2.9731 | 15.9777 |  | STD2013 | 0 | 0 | 0.010769 | 0.01815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028919 |  | STD2013 | 19.9075 | 3.9756 | 1.177 | 1.9838 | 2.9916 | 20.7749 | 7.0644 | 12.6608 | 0.25859 | 2.456 | 0 | 11.0904 | 0.46587 | 0 | 54.5001 | 31.125 | 170.4316
STD2010 | 0.22363 | 0.040368 | 0.010554 | 0.032647 | 0.031008 | 0.21323 | 0.073473 | 0.1343 | 0 | 0.03299 | 0 | 0.11285 | 0.0047592 | 0 | 0.55338 | 0.31716 | 1.7803 |  | STD2010 | 7.1781 | 1.2957 | 1.0769 | 3.3313 | 0.9953 | 6.8441 | 2.3583 | 4.3106 | 0 | 1.0589 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 60.1668 |  | STD2010 | 2.1038 | 0.37975 | 0 | 0 | 0.2917 | 2.0059 | 0.69119 | 1.2634 | 0 | 0.31035 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 16.3419 |  | STD2010 | 0 | 0 | 0.010769 | 0.033313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044083 |  | STD2010 | 22.0245 | 3.9756 | 1.1771 | 3.6411 | 3.0539 | 20.9996 | 7.236 | 13.2262 | 0 | 3.2491 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 175.9016
STD2007 | 0.30444 | 0.058431 | 0.010631 | 0.059194 | 0.0074914 | 0.28998 | 0.1029 | 0.14364 | 0 | 0.06472 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0671 |  | STD2007 | 9.772 | 1.8755 | 1.0848 | 6.0402 | 0.24046 | 9.3077 | 3.3029 | 4.6104 | 0 | 2.0774 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 71.2322 |  | STD2007 | 2.864 | 0.54968 | 0 | 0 | 0.070474 | 2.7279 | 0.96804 | 1.3512 | 0 | 0.60884 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.7888 |  | STD2007 | 0 | 0 | 0.010848 | 0.060402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071249 |  | STD2007 | 29.9834 | 5.7546 | 1.1856 | 6.6019 | 0.73779 | 28.5587 | 10.1344 | 14.146 | 0 | 6.374 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 204.4872
STD2004 | 0.30444 | 0.058431 | 0.010631 | 0.079344 | 0.0077692 | 0.2978 | 0.10497 | 0.14836 | 0 | 0.064471 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.1019 |  | STD2004 | 9.772 | 1.8755 | 1.0848 | 8.0963 | 0.24937 | 9.5588 | 3.3693 | 4.762 | 0 | 2.0694 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 73.7584 |  | STD2004 | 2.864 | 0.54968 | 0 | 0 | 0.073087 | 2.8015 | 0.9875 | 1.3957 | 0 | 0.6065 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.9265 |  | STD2004 | 0 | 0 | 0.010848 | 0.080963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091811 |  | STD2004 | 29.9834 | 5.7546 | 1.1857 | 8.8493 | 0.76515 | 29.3291 | 10.3381 | 14.6112 | 0 | 6.3494 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 208.1767
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 1.3381e-07 | 0.020151 | 0.00027778 | 0.007823 | 0.0020683 | 0.004723 | 0 | -0.00024953 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034793 |  | 2004-2007 | 0 | 0 | 1.3654e-05 | 2.0562 | 0.0089161 | 0.2511 | 0.066388 | 0.1516 | 0 | -0.0080094 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5262 |  | 2004-2007 | 0 | 0 | 0 | 0 | 0.0026132 | 0.073594 | 0.019457 | 0.044431 | 0 | -0.0023474 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13775 |  | 2004-2007 | 0 | 0 | 1.3654e-07 | 0.020562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020562 |  | 2004-2007 | 0 | 0 | 1.4923e-05 | 2.2474 | 0.027357 | 0.77045 | 0.2037 | 0.46515 | 0 | -0.024575 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6895
2007-2010 | 0.080813 | 0.018063 | 7.6635e-05 | 0.026546 | -0.023517 | 0.076753 | 0.029429 | 0.0093397 | 0 | 0.03173 | 0 | 0.0030461 | 0.0037612 | 0 | 0 | 0.030684 | 0.28673 |  | 2007-2010 | 2.5939 | 0.57978 | 0.0078198 | 2.7088 | -0.75484 | 2.4636 | 0.94462 | 0.29978 | 0 | 1.0185 | 0 | 0.097773 | 0.12073 | 0 | 0 | 0.9849 | 11.0654 |  | 2007-2010 | 0.76024 | 0.16992 | 0 | 0 | -0.22123 | 0.72205 | 0.27685 | 0.087862 | 0 | 0.29849 | 0 | 0.028656 | 0.035383 | 0 | 0 | 0.28866 | 2.4469 |  | 2007-2010 | 0 | 0 | 7.8198e-05 | 0.027088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027166 |  | 2007-2010 | 7.9589 | 1.7789 | 0.0085471 | 2.9607 | -2.3161 | 7.5591 | 2.8984 | 0.91983 | 0 | 3.1249 | 0 | 0.3 | 0.37042 | 0 | 0 | 3.022 | 28.5856
2010-2013 | 0.021495 | 0 | 3.9422e-07 | 0.01486 | 0.00063255 | 0.0022808 | 0.0017424 | 0.0057412 | -0.0026257 | 0.0080524 | 0 | 0.00023814 | 2.8944e-05 | 0 | 0 | 0.0011261 | 0.053573 |  | 2010-2013 | 0.68994 | 0 | 4.0226e-05 | 1.5164 | 0.020304 | 0.073209 | 0.055927 | 0.18428 | -0.084279 | 0.25846 | 0 | 0.0076439 | 0.00092903 | 0 | 0 | 0.036147 | 2.759 |  | 2010-2013 | 0.20221 | 0 | 0 | 0 | 0.0059506 | 0.021456 | 0.016391 | 0.054009 | -0.024701 | 0.075752 | 0 | 0.0022403 | 0.00027228 | 0 | 0 | 0.010594 | 0.36417 |  | 2010-2013 | 0 | 0 | 4.0226e-07 | 0.015164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015164 |  | 2010-2013 | 2.1169 | 0 | 4.3967e-05 | 1.6574 | 0.062297 | 0.22463 | 0.1716 | 0.56542 | -0.25859 | 0.79304 | 0 | 0.023454 | 0.0028505 | 0 | 0 | 0.11091 | 5.47
2013-2016 | 0.014161 | 0.019983 | 0.00027796 | 0.0031082 | -0.020379 | 0.02628 | 0.0072141 | 0.0011094 | 0.00033209 | 0.0022703 | 0 | 0 | 0.0014727 | 0 | 0 | 0 | 0.05583 |  | 2013-2016 | 0.45453 | 0.64143 | 0.028363 | 0.31716 | -0.65411 | 0.84353 | 0.23156 | 0.035609 | 0.010659 | 0.072871 | 0 | 0 | 0.04727 | 0 | 0 | 0 | 2.0289 |  | 2013-2016 | 0.13321 | 0.18799 | 0 | 0 | -0.19171 | 0.24722 | 0.067865 | 0.010436 | 0.0031241 | 0.021357 | 0 | 0 | 0.013854 | 0 | 0 | 0 | 0.49336 |  | 2013-2016 | 0 | 0 | 0.00028363 | 0.0031716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034552 |  | 2013-2016 | 1.3946 | 1.9681 | 0.031001 | 0.34666 | -2.007 | 2.5882 | 0.71048 | 0.10926 | 0.032706 | 0.22359 | 0 | 0 | 0.14504 | 0 | 0 | 0 | 5.5426
2016-2019 | 0.034996 | 0 | 3.3051e-07 | 0.0024644 | -0.0042695 | 0.016694 | 0.0076747 | 0.0044011 | 0.00026842 | 0.0010214 | 0 | 0 | 1.5422e-05 | 0 | 0 | 0 | 0.063266 |  | 2016-2019 | 1.1233 | 0 | 3.3726e-05 | 0.25147 | -0.13704 | 0.53585 | 0.24634 | 0.14127 | 0.0086158 | 0.032784 | 0 | 0 | 0.00049501 | 0 | 0 | 0 | 2.2031 |  | 2016-2019 | 0.32922 | 0 | 0 | 0 | -0.040165 | 0.15705 | 0.072198 | 0.041403 | 0.0025251 | 0.0096084 | 0 | 0 | 0.00014508 | 0 | 0 | 0 | 0.57198 |  | 2016-2019 | 0 | 0 | 3.3726e-07 | 0.0025147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002515 |  | 2016-2019 | 3.4466 | 0 | 3.6862e-05 | 0.27485 | -0.42048 | 1.6441 | 0.75584 | 0.43344 | 0.026436 | 0.10059 | 0 | 0 | 0.0015188 | 0 | 0 | 0 | 6.263
2004-2019 | 0.15146 | 0.038046 | 0.00035546 | 0.06713 | -0.047255 | 0.12983 | 0.048129 | 0.025314 | -0.0020252 | 0.042824 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.49419 |  | 2004-2019 | 4.8617 | 1.2212 | 0.036271 | 6.85 | -1.5168 | 4.1673 | 1.5448 | 0.81254 | -0.065004 | 1.3746 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 20.5825 |  | 2004-2019 | 1.4249 | 0.35791 | 0 | 0 | -0.44454 | 1.2214 | 0.45276 | 0.23814 | -0.019052 | 0.40286 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 4.0141 |  | 2004-2019 | 0 | 0 | 0.00036271 | 0.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068863 |  | 2004-2019 | 14.9171 | 3.747 | 0.039644 | 7.4871 | -4.6539 | 12.7865 | 4.74 | 2.4931 | -0.19945 | 4.2176 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 49.5507
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.001259% | 25.4% | 3.575% | 2.627% | 1.97% | 3.184% |  | -0.387% |  | 0% | 0% |  | 0% | 0% | 1.655% |  | 2004-2007 | 0% | 0% | 0.001259% | 25.4% | 3.575% | 2.627% | 1.97% | 3.184% |  | -0.387% |  | 0% | 0% |  | 0% | 0% | 3.425% |  | 2004-2007 | 0% | 0% |  |  | 3.575% | 2.627% | 1.97% | 3.184% |  | -0.387% |  | 0% | 0% |  | 0% | 0% | 0.7278% |  | 2004-2007 |  |  | 0.001259% | 25.4% | [12 empty] | 22.4% |  | 2004-2007 | 0% | 0% | 0.001259% | 25.4% | 3.575% | 2.627% | 1.97% | 3.184% |  | -0.387% |  | 0% | 0% |  | 0% | 0% | 1.772%
2007-2010 | 26.54% | 30.91% | 0.7209% | 44.85% | -313.9% | 26.47% | 28.6% | 6.502% |  | 49.03% |  | 2.628% | 44.14% |  | 0% | 8.821% | 13.87% |  | 2007-2010 | 26.54% | 30.91% | 0.7209% | 44.85% | -313.9% | 26.47% | 28.6% | 6.502% |  | 49.03% |  | 2.628% | 44.14% |  | 0% | 8.821% | 15.53% |  | 2007-2010 | 26.54% | 30.91% |  |  | -313.9% | 26.47% | 28.6% | 6.502% |  | 49.03% |  | 2.628% | 44.14% |  | 0% | 8.821% | 13.02% |  | 2007-2010 |  |  | 0.7209% | 44.85% | [12 empty] | 38.13% |  | 2007-2010 | 26.54% | 30.91% | 0.7209% | 44.85% | -313.9% | 26.47% | 28.6% | 6.502% |  | 49.03% |  | 2.628% | 44.14% |  | 0% | 8.821% | 13.98%
2010-2013 | 9.612% | 0% | 0.003735% | 45.52% | 2.04% | 1.07% | 2.371% | 4.275% |  | 24.41% |  | 0.211% | 0.6082% |  | 0% | 0.3551% | 3.009% |  | 2010-2013 | 9.612% | 0% | 0.003735% | 45.52% | 2.04% | 1.07% | 2.371% | 4.275% |  | 24.41% |  | 0.211% | 0.6082% |  | 0% | 0.3551% | 4.586% |  | 2010-2013 | 9.612% | 0% |  |  | 2.04% | 1.07% | 2.371% | 4.275% |  | 24.41% |  | 0.211% | 0.6082% |  | 0% | 0.3551% | 2.228% |  | 2010-2013 |  |  | 0.003735% | 45.52% | [12 empty] | 34.4% |  | 2010-2013 | 9.612% | 0% | 0.003735% | 45.52% | 2.04% | 1.07% | 2.371% | 4.275% |  | 24.41% |  | 0.211% | 0.6082% |  | 0% | 0.3551% | 3.11%
2013-2016 | 7.006% | 49.5% | 2.634% | 17.47% | -67.09% | 12.46% | 10.06% | 0.863% | 12.65% | 9.104% |  | 0% | 31.13% |  | 0% | 0% | 3.233% |  | 2013-2016 | 7.006% | 49.5% | 2.634% | 17.47% | -67.09% | 12.46% | 10.06% | 0.863% | 12.65% | 9.104% |  | 0% | 31.13% |  | 0% | 0% | 3.534% |  | 2013-2016 | 7.006% | 49.5% |  |  | -67.09% | 12.46% | 10.06% | 0.863% | 12.65% | 9.104% |  | 0% | 31.13% |  | 0% | 0% | 3.088% |  | 2013-2016 |  |  | 2.634% | 17.47% | [12 empty] | 11.95% |  | 2013-2016 | 7.006% | 49.5% | 2.634% | 17.47% | -67.09% | 12.46% | 10.06% | 0.863% | 12.65% | 9.104% |  | 0% | 31.13% |  | 0% | 0% | 3.252%
2016-2019 | 18.62% | 0% | 0.003216% | 16.79% | -8.412% | 9.04% | 11.9% | 3.453% | 11.7% | 4.506% |  | 0% | 0.4734% |  | 0% | 0% | 3.786% |  | 2016-2019 | 18.62% | 0% | 0.003216% | 16.79% | -8.412% | 9.04% | 11.9% | 3.453% | 11.7% | 4.506% |  | 0% | 0.4734% |  | 0% | 0% | 3.978% |  | 2016-2019 | 18.62% | 0% |  |  | -8.412% | 9.04% | 11.9% | 3.453% | 11.7% | 4.506% |  | 0% | 0.4734% |  | 0% | 0% | 3.694% |  | 2016-2019 |  |  | 0.003216% | 16.79% | [12 empty] | 9.877% |  | 2016-2019 | 18.62% | 0% | 0.003216% | 16.79% | -8.412% | 9.04% | 11.9% | 3.453% | 11.7% | 4.506% |  | 0% | 0.4734% |  | 0% | 0% | 3.798%
2004-2019 | 49.75% | 65.11% | 3.344% | 84.61% | -608.2% | 43.6% | 45.85% | 17.06% |  | 66.42% |  | 2.834% | 61.95% |  | 0% | 9.145% | 23.51% |  | 2004-2019 | 49.75% | 65.11% | 3.344% | 84.61% | -608.2% | 43.6% | 45.85% | 17.06% |  | 66.42% |  | 2.834% | 61.95% |  | 0% | 9.145% | 27.91% |  | 2004-2019 | 49.75% | 65.11% |  |  | -608.2% | 43.6% | 45.85% | 17.06% |  | 66.42% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.21% |  | 2004-2019 |  |  | 3.344% | 84.61% | [12 empty] | 75% |  | 2004-2019 | 49.75% | 65.11% | 3.344% | 84.61% | -608.2% | 43.6% | 45.85% | 17.06% |  | 66.42% |  | 2.834% | 61.95% |  | 0% | 9.145% | 23.8%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.15252 | 0.019893 | 0.0074912 | 0.00027684 | 0 | 0.43791 | 0.14547 | 0.13844 | 0.0063066 | 0.046659 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.9402 | 0% | CZ 0A | 4.8957 | 0.63853 | 0.76441 | 0.028249 | 0 | 14.0559 | 4.6693 | 4.4437 | 0.20243 | 1.4976 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 62.8209 | 0% | CZ 0A | 1.4348 | 0.18714 | 0 | 0 | 0 | 4.1195 | 1.3685 | 1.3024 | 0.059329 | 0.43894 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 18.1794 | 0% | CZ 0A | 0 | 0 | 0.0076441 | 0.00028249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0079266 | 0% | CZ 0A | 15.0214 | 1.9592 | 0.8355 | 0.030876 | 0 | 43.1275 | 14.3266 | 13.6347 | 0.62111 | 4.5952 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 191.1868 | 0%
CZ 0B | 0.15262 | 0.020228 | 0.0074713 | 0.00033925 | 0.0010865 | 0.45825 | 0.12581 | 0.13579 | 0 | 0.047404 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.9343 | 0% | CZ 0B | 4.8987 | 0.64927 | 0.76238 | 0.034617 | 0.034873 | 14.7087 | 4.0381 | 4.3587 | 0 | 1.5216 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 62.6319 | 0% | CZ 0B | 1.4357 | 0.19029 | 0 | 0 | 0.010221 | 4.3109 | 1.1835 | 1.2775 | 0 | 0.44594 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 18.1228 | 0% | CZ 0B | 0 | 0 | 0.0076238 | 0.00034617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00797 | 0% | CZ 0B | 15.0306 | 1.9922 | 0.83328 | 0.037837 | 0.107 | 45.1306 | 12.3901 | 13.3737 | 0 | 4.6686 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 190.5985 | 0%
CZ 1A | 0.1528 | 0.020319 | 0.0080578 | 0.00039048 | 0 | 0.34896 | 0.12318 | 0.13146 | 0.0057628 | 0.037177 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.8134 | 2.832% | CZ 1A | 4.9046 | 0.6522 | 0.82222 | 0.039845 | 0 | 11.201 | 3.9539 | 4.2195 | 0.18497 | 1.1933 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 58.7966 | 2.832% | CZ 1A | 1.4375 | 0.19115 | 0 | 0 | 0 | 3.2828 | 1.1588 | 1.2367 | 0.054213 | 0.34974 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 16.9796 | 2.832% | CZ 1A | 0 | 0 | 0.0082222 | 0.00039845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086207 | 2.832% | CZ 1A | 15.0488 | 2.0011 | 0.89869 | 0.043551 | 0 | 34.3678 | 12.1318 | 12.9466 | 0.56755 | 3.6614 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 178.7021 | 2.832%
CZ 1B | 0.15284 | 0.020247 | 0.0080788 | 0.0016316 | 0.0063309 | 0.39598 | 0.11008 | 0.13314 | 0 | 0.041142 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.8547 | 0% | CZ 1B | 4.9058 | 0.64988 | 0.82437 | 0.16649 | 0.20321 | 12.7101 | 3.5333 | 4.2737 | 0 | 1.3206 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 60.2125 | 0% | CZ 1B | 1.4378 | 0.19047 | 0 | 0 | 0.059557 | 3.7251 | 1.0356 | 1.2525 | 0 | 0.38704 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 17.3569 | 0% | CZ 1B | 0 | 0 | 0.0082437 | 0.0016649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099086 | 0% | CZ 1B | 15.0525 | 1.994 | 0.90104 | 0.18197 | 0.62351 | 38.9984 | 10.8412 | 13.1128 | 0 | 4.0519 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 182.792 | 0%
CZ 2A | 0.15265 | 0.020315 | 0.0087104 | 0.0014919 | 0.016404 | 0.27223 | 0.098417 | 0.12283 | 0.0029774 | 0.032488 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.7138 | 14.12% | CZ 2A | 4.8996 | 0.65207 | 0.88881 | 0.15223 | 0.52653 | 8.7381 | 3.159 | 3.9425 | 0.095568 | 1.0428 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 55.7222 | 14.12% | CZ 2A | 1.436 | 0.19111 | 0 | 0 | 0.15432 | 2.561 | 0.92584 | 1.1555 | 0.028009 | 0.30562 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 16.0261 | 14.12% | CZ 2A | 0 | 0 | 0.0088881 | 0.0015223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01041 | 14.12% | CZ 2A | 15.0333 | 2.0007 | 0.97147 | 0.16639 | 1.6156 | 26.8111 | 9.6926 | 12.0968 | 0.29323 | 3.1996 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 168.9155 | 14.12%
CZ 2B | 0.15272 | 0.020327 | 0.0087501 | 0.0017249 | 0.079061 | 0.23787 | 0.072804 | 0.13755 | 0 | 0.027241 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.7233 | 1.729% | CZ 2B | 4.902 | 0.65247 | 0.89286 | 0.17601 | 2.5377 | 7.6351 | 2.3368 | 4.4151 | 0 | 0.87439 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 56.0475 | 1.729% | CZ 2B | 1.4367 | 0.19123 | 0 | 0 | 0.74376 | 2.2377 | 0.68489 | 1.294 | 0 | 0.25627 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 16.1133 | 1.729% | CZ 2B | 0 | 0 | 0.0089286 | 0.0017601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010689 | 1.729% | CZ 2B | 15.0408 | 2.002 | 0.9759 | 0.19238 | 7.7864 | 23.4266 | 7.1701 | 13.5467 | 0 | 2.6829 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 169.8584 | 1.729%
CZ 3A | 0.15298 | 0.020481 | 0.0098477 | 0.0066181 | 0.046613 | 0.1848 | 0.065415 | 0.12131 | 0.0024205 | 0.0235 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.6193 | 14.09% | CZ 3A | 4.9102 | 0.65739 | 1.0049 | 0.67531 | 1.4962 | 5.9316 | 2.0997 | 3.8939 | 0.077694 | 0.75429 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 53.1261 | 14.09% | CZ 3A | 1.4391 | 0.19267 | 0 | 0 | 0.4385 | 1.7384 | 0.61538 | 1.1412 | 0.022771 | 0.22107 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 15.0779 | 14.09% | CZ 3A | 0 | 0 | 0.010049 | 0.0067531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016802 | 14.09% | CZ 3A | 15.066 | 2.0171 | 1.0983 | 0.73812 | 4.5907 | 18.1997 | 6.4424 | 11.9476 | 0.23839 | 2.3144 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 159.6874 | 14.09%
CZ 3B | 0.1528 | 0.020159 | 0.0095577 | 0.0065711 | 0.085355 | 0.20708 | 0.064635 | 0.1473 | 0 | 0.024864 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.7036 | 6.659% | CZ 3B | 4.9045 | 0.64705 | 0.97527 | 0.67052 | 2.7397 | 6.6467 | 2.0746 | 4.7281 | 0 | 0.79808 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 55.8097 | 6.659% | CZ 3B | 1.4374 | 0.18964 | 0 | 0 | 0.80296 | 1.948 | 0.60804 | 1.3857 | 0 | 0.2339 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 15.8745 | 6.659% | CZ 3B | 0 | 0 | 0.0097527 | 0.0067052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016458 | 6.659% | CZ 3B | 15.0485 | 1.9853 | 1.066 | 0.73288 | 8.4062 | 20.394 | 6.3656 | 14.5072 | 0 | 2.4487 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 167.9892 | 6.659%
CZ 3C | 0.153 | 0.020133 | 0.0099752 | 0.00098757 | 0.022853 | 0.13322 | 0.051113 | 0.11856 | 0 | 0.019503 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.5146 | 5.951% | CZ 3C | 4.911 | 0.64623 | 1.0179 | 0.10077 | 0.73355 | 4.2761 | 1.6406 | 3.8055 | 0 | 0.626 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 49.3826 | 5.951% | CZ 3C | 1.4393 | 0.1894 | 0 | 0 | 0.21499 | 1.2532 | 0.48083 | 1.1153 | 0 | 0.18347 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.1454 | 5.951% | CZ 3C | 0 | 0 | 0.010179 | 0.0010077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011186 | 5.951% | CZ 3C | 15.0683 | 1.9828 | 1.1125 | 0.11014 | 2.2507 | 13.1203 | 5.0338 | 11.6762 | 0 | 1.9207 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 149.3104 | 5.951%
CZ 4A | 0.15311 | 0.020378 | 0.010756 | 0.013328 | 0.071111 | 0.13569 | 0.045514 | 0.11709 | 0.0026261 | 0.018796 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.5737 | 29.22% | CZ 4A | 4.9145 | 0.65408 | 1.0975 | 1.36 | 2.2825 | 4.3555 | 1.4609 | 3.7583 | 0.084292 | 0.60332 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 52.1959 | 29.22% | CZ 4A | 1.4403 | 0.1917 | 0 | 0 | 0.66896 | 1.2765 | 0.42816 | 1.1015 | 0.024705 | 0.17682 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.5775 | 29.22% | CZ 4A | 0 | 0 | 0.010975 | 0.0136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024575 | 29.22% | CZ 4A | 15.079 | 2.0069 | 1.1996 | 1.4864 | 7.0034 | 13.3638 | 4.4824 | 11.5317 | 0.25863 | 1.8511 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 155.2977 | 29.22%
CZ 4B | 0.15262 | 0.020206 | 0.010498 | 0.014344 | 0.12069 | 0.1523 | 0.04436 | 0.14917 | 0 | 0.019315 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.6688 | 0.02014% | CZ 4B | 4.8989 | 0.64857 | 1.0713 | 1.4637 | 3.8738 | 4.8884 | 1.4239 | 4.7881 | 0 | 0.61997 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 55.3015 | 0.02014% | CZ 4B | 1.4358 | 0.19009 | 0 | 0 | 1.1353 | 1.4327 | 0.41731 | 1.4033 | 0 | 0.1817 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 15.465 | 0.02014% | CZ 4B | 0 | 0 | 0.010713 | 0.014637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025349 | 0.02014% | CZ 4B | 15.0313 | 1.99 | 1.1709 | 1.5998 | 11.8859 | 14.9989 | 4.3689 | 14.6911 | 0 | 1.9023 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 164.6738 | 0.02014%
CZ 4C | 0.15353 | 0.02066 | 0.011034 | 0.020395 | 0.050608 | 0.075621 | 0.024384 | 0.11728 | 0 | 0.012623 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.4714 | 6.185% | CZ 4C | 4.9281 | 0.66314 | 1.1259 | 2.0811 | 1.6244 | 2.4273 | 0.78266 | 3.7645 | 0 | 0.40518 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 49.4274 | 6.185% | CZ 4C | 1.4444 | 0.19435 | 0 | 0 | 0.47609 | 0.71139 | 0.22938 | 1.1033 | 0 | 0.11875 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 13.5464 | 6.185% | CZ 4C | 0 | 0 | 0.011259 | 0.020811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03207 | 6.185% | CZ 4C | 15.1209 | 2.0347 | 1.2306 | 2.2746 | 4.9842 | 7.4476 | 2.4014 | 11.5507 | 0 | 1.2432 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 145.3227 | 6.185%
CZ 5A | 0.15295 | 0.020477 | 0.011529 | 0.022887 | 0.050598 | 0.12516 | 0.036659 | 0.11935 | 0.0021628 | 0.016037 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.5431 | 12.51% | CZ 5A | 4.9094 | 0.65728 | 1.1765 | 2.3354 | 1.6241 | 4.0173 | 1.1767 | 3.8309 | 0.069422 | 0.51476 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 51.9366 | 12.51% | CZ 5A | 1.4389 | 0.19264 | 0 | 0 | 0.47599 | 1.1774 | 0.34486 | 1.1228 | 0.020347 | 0.15087 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.1925 | 12.51% | CZ 5A | 0 | 0 | 0.011765 | 0.023354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035119 | 12.51% | CZ 5A | 15.0634 | 2.0167 | 1.2859 | 2.5526 | 4.9831 | 12.3261 | 3.6103 | 11.7543 | 0.21301 | 1.5794 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 152.4196 | 12.51%
CZ 5B | 0.15292 | 0.020345 | 0.011311 | 0.032675 | 0.1376 | 0.11583 | 0.033245 | 0.14724 | 0 | 0.017025 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.6535 | 3.999% | CZ 5B | 4.9083 | 0.65304 | 1.1542 | 3.3342 | 4.4166 | 3.7178 | 1.0671 | 4.7261 | 0 | 0.54646 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 56.1489 | 3.999% | CZ 5B | 1.4385 | 0.19139 | 0 | 0 | 1.2944 | 1.0896 | 0.31275 | 1.3852 | 0 | 0.16016 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 15.1408 | 3.999% | CZ 5B | 0 | 0 | 0.011542 | 0.033342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044884 | 3.999% | CZ 5B | 15.0601 | 2.0037 | 1.2615 | 3.6443 | 13.5515 | 11.4073 | 3.2742 | 14.5012 | 0 | 1.6767 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 163.4152 | 3.999%
CZ 5C | 0.15364 | 0.020689 | 0.011474 | 0.022556 | 0.057602 | 0.058729 | 0.017072 | 0.11875 | 0 | 0.010215 | 0 | 0.11261 | 0.0032428 | 0 | 0.55338 | 0.31604 | 1.456 | 0.02726% | CZ 5C | 4.9314 | 0.66407 | 1.1709 | 2.3016 | 1.8489 | 1.8851 | 0.54798 | 3.8116 | 0 | 0.32787 | 0 | 3.6145 | 0.10409 | 0 | 17.7624 | 10.1441 | 49.1145 | 0.02726% | CZ 5C | 1.4453 | 0.19463 | 0 | 0 | 0.54188 | 0.55248 | 0.1606 | 1.1171 | 0 | 0.096093 | 0 | 1.0594 | 0.030506 | 0 | 5.2059 | 2.9731 | 13.3769 | 0.02726% | CZ 5C | 0 | 0 | 0.011709 | 0.023016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034725 | 0.02726% | CZ 5C | 15.131 | 2.0375 | 1.2798 | 2.5157 | 5.673 | 5.7839 | 1.6814 | 11.695 | 0 | 1.006 | 0 | 11.0904 | 0.31937 | 0 | 54.5001 | 31.125 | 143.8381 | 0.02726%
CZ 6A | 0.15306 | 0.020502 | 0.012111 | 0.044718 | 0.070378 | 0.11923 | 0.034554 | 0.12326 | 0.0024111 | 0.016675 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.5822 | 2.349% | CZ 6A | 4.9129 | 0.65806 | 1.2358 | 4.563 | 2.259 | 3.827 | 1.1091 | 3.9563 | 0.07739 | 0.53524 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 54.7589 | 2.349% | CZ 6A | 1.4399 | 0.19287 | 0 | 0 | 0.66207 | 1.1216 | 0.32506 | 1.1595 | 0.022682 | 0.15687 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.3494 | 2.349% | CZ 6A | 0 | 0 | 0.012358 | 0.04563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057989 | 2.349% | CZ 6A | 15.0743 | 2.0191 | 1.3508 | 4.9874 | 6.9312 | 11.7423 | 3.4031 | 12.139 | 0.23745 | 1.6423 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 156.5616 | 2.349%
CZ 6B | 0.15314 | 0.020666 | 0.011962 | 0.059361 | 0.12702 | 0.10143 | 0.028087 | 0.13982 | 0 | 0.014668 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.6414 | 0.09127% | CZ 6B | 4.9156 | 0.66333 | 1.2206 | 6.0572 | 4.077 | 3.2556 | 0.90154 | 4.488 | 0 | 0.47082 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 57.6748 | 0.09127% | CZ 6B | 1.4407 | 0.19441 | 0 | 0 | 1.1949 | 0.95417 | 0.26423 | 1.3154 | 0 | 0.13799 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.7705 | 0.09127% | CZ 6B | 0 | 0 | 0.012206 | 0.060572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072778 | 0.09127% | CZ 6B | 15.0824 | 2.0353 | 1.3341 | 6.6205 | 12.5094 | 9.9892 | 2.7662 | 13.7706 | 0 | 1.4446 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 162.5871 | 0.09127%
CZ 7 | 0.15319 | 0.020709 | 0.012798 | 0.043798 | 0.083132 | 0.10135 | 0.027629 | 0.12446 | 0.0027428 | 0.016318 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.5714 | 0.2174% | CZ 7 | 4.917 | 0.66471 | 1.3059 | 4.4692 | 2.6684 | 3.253 | 0.88682 | 3.9948 | 0.088038 | 0.52376 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 54.3966 | 0.2174% | CZ 7 | 1.4411 | 0.19482 | 0 | 0 | 0.78205 | 0.9534 | 0.25991 | 1.1708 | 0.025802 | 0.1535 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.2501 | 0.2174% | CZ 7 | 0 | 0 | 0.013059 | 0.044692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057751 | 0.2174% | CZ 7 | 15.0868 | 2.0395 | 1.4274 | 4.8849 | 8.1873 | 9.9811 | 2.721 | 12.2572 | 0.27013 | 1.607 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 155.497 | 0.2174%
CZ 8 | 0.15654 | 0.022328 | 0.01373 | 0.061469 | 0.10058 | 0.072831 | 0.016919 | 0.12427 | 0.0028915 | 0.012975 | 0 | 0.11261 | 0.003244 | 0 | 0.55338 | 0.31604 | 1.5698 | 0% | CZ 8 | 5.0245 | 0.71668 | 1.401 | 6.2723 | 3.2283 | 2.3377 | 0.54306 | 3.9887 | 0.09281 | 0.41646 | 0 | 3.6145 | 0.10412 | 0 | 17.7624 | 10.1441 | 55.6467 | 0% | CZ 8 | 1.4726 | 0.21005 | 0 | 0 | 0.94616 | 0.68515 | 0.15916 | 1.169 | 0.027201 | 0.12206 | 0 | 1.0594 | 0.030517 | 0 | 5.2059 | 2.9731 | 14.0602 | 0% | CZ 8 | 0 | 0 | 0.01401 | 0.062723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076733 | 0% | CZ 8 | 15.4167 | 2.199 | 1.5313 | 6.8556 | 9.9053 | 7.1728 | 1.6663 | 12.2385 | 0.28477 | 1.2778 | 0 | 11.0904 | 0.31948 | 0 | 54.5001 | 31.125 | 155.583 | 0%
US Weighted | 0.15298 | 0.020384 | 0.010275 | 0.012214 | 0.055024 | 0.16797 | 0.056842 | 0.12304 | 0.0020252 | 0.021646 | 0 | 0.11261 | 0.0032422 | 0 | 0.55338 | 0.31604 | 1.6077 | 100% | US Weighted | 4.9103 | 0.65429 | 1.0485 | 1.2463 | 1.7661 | 5.3915 | 1.8245 | 3.9495 | 0.065004 | 0.6948 | 0 | 3.6145 | 0.10407 | 0 | 17.7624 | 10.1441 | 53.1759 | 100% | US Weighted | 1.4391 | 0.19176 | 0 | 0 | 0.51763 | 1.5802 | 0.53473 | 1.1575 | 0.019052 | 0.20363 | 0 | 1.0594 | 0.0305 | 0 | 5.2059 | 2.9731 | 14.9124 | 100% | US Weighted | 0 | 0 | 0.010485 | 0.012463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022948 | 100% | US Weighted | 15.0663 | 2.0076 | 1.146 | 1.3623 | 5.4191 | 16.5426 | 5.5981 | 12.1181 | 0.19945 | 2.1318 | 0 | 11.0904 | 0.31931 | 0 | 54.5001 | 31.125 | 158.626 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.18729 | 0.019893 | 0.0074909 | 0.00026175 | 0 | 0.46013 | 0.16071 | 0.14024 | 0.0075874 | 0.047959 | 0 | 0.11261 | 0.003257 | 0 | 0.55338 | 0.31604 | 2.0168 | 0% | CZ 0A | 6.0115 | 0.63853 | 0.76437 | 0.026709 | 0 | 14.7692 | 5.1586 | 4.5013 | 0.24354 | 1.5394 | 0 | 3.6145 | 0.10454 | 0 | 17.7624 | 10.1441 | 65.2786 | 0% | CZ 0A | 1.7619 | 0.18714 | 0 | 0 | 0 | 4.3286 | 1.5119 | 1.3193 | 0.071377 | 0.45117 | 0 | 1.0594 | 0.03064 | 0 | 5.2059 | 2.9731 | 18.9002 | 0% | CZ 0A | 0 | 0 | 0.0076437 | 0.00026709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0079108 | 0% | CZ 0A | 18.4449 | 1.9592 | 0.83546 | 0.029193 | 0 | 45.3162 | 15.828 | 13.8114 | 0.74725 | 4.7233 | 0 | 11.0904 | 0.32077 | 0 | 54.5001 | 31.125 | 198.7311 | 0%
CZ 0B | 0.18753 | 0.020228 | 0.0074707 | 0.00029566 | 0.0010592 | 0.47892 | 0.13886 | 0.13737 | 0 | 0.050049 | 0 | 0.11261 | 0.003257 | 0 | 0.55338 | 0.31604 | 2.0071 | 0% | CZ 0B | 6.0193 | 0.64927 | 0.76232 | 0.030169 | 0.033998 | 15.3722 | 4.4572 | 4.4094 | 0 | 1.6065 | 0 | 3.6145 | 0.10454 | 0 | 17.7624 | 10.1441 | 64.9658 | 0% | CZ 0B | 1.7642 | 0.19029 | 0 | 0 | 0.0099643 | 4.5053 | 1.3063 | 1.2923 | 0 | 0.47082 | 0 | 1.0594 | 0.03064 | 0 | 5.2059 | 2.9731 | 18.8081 | 0% | CZ 0B | 0 | 0 | 0.0076232 | 0.00030169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0079249 | 0% | CZ 0B | 18.469 | 1.9922 | 0.83322 | 0.032975 | 0.10432 | 47.1662 | 13.6761 | 13.5292 | 0 | 4.9291 | 0 | 11.0904 | 0.32077 | 0 | 54.5001 | 31.125 | 197.7684 | 0%
CZ 1A | 0.18758 | 0.020319 | 0.0080581 | 0.00029063 | 0 | 0.37369 | 0.13691 | 0.13505 | 0.0069814 | 0.038744 | 0 | 0.11261 | 0.003257 | 0 | 0.55338 | 0.31604 | 1.8929 | 2.832% | CZ 1A | 6.0209 | 0.6522 | 0.82226 | 0.029656 | 0 | 11.9947 | 4.3945 | 4.3348 | 0.22409 | 1.2436 | 0 | 3.6145 | 0.10454 | 0 | 17.7624 | 10.1441 | 61.3422 | 2.832% | CZ 1A | 1.7646 | 0.19115 | 0 | 0 | 0 | 3.5154 | 1.288 | 1.2704 | 0.065676 | 0.36448 | 0 | 1.0594 | 0.03064 | 0 | 5.2059 | 2.9731 | 17.7287 | 2.832% | CZ 1A | 0 | 0 | 0.0082226 | 0.00029656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0085192 | 2.832% | CZ 1A | 18.4738 | 2.0011 | 0.89873 | 0.032414 | 0 | 36.8031 | 13.4837 | 13.3003 | 0.68757 | 3.8158 | 0 | 11.0904 | 0.32077 | 0 | 54.5001 | 31.125 | 186.5327 | 2.832%
CZ 1B | 0.18766 | 0.020247 | 0.0080794 | 0.0019051 | 0.0062699 | 0.42087 | 0.12242 | 0.13678 | 0 | 0.043801 | 0 | 0.11261 | 0.003257 | 0 | 0.55338 | 0.31604 | 1.9333 | 0% | CZ 1B | 6.0236 | 0.64988 | 0.82443 | 0.1944 | 0.20125 | 13.5089 | 3.9293 | 4.3904 | 0 | 1.4059 | 0 | 3.6145 | 0.10454 | 0 | 17.7624 | 10.1441 | 62.7536 | 0% | CZ 1B | 1.7654 | 0.19047 | 0 | 0 | 0.058983 | 3.9592 | 1.1516 | 1.2868 | 0 | 0.41205 | 0 | 1.0594 | 0.03064 | 0 | 5.2059 | 2.9731 | 18.0934 | 0% | CZ 1B | 0 | 0 | 0.0082443 | 0.001944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010188 | 0% | CZ 1B | 18.482 | 1.994 | 0.9011 | 0.21248 | 0.6175 | 41.4492 | 12.0562 | 13.4711 | 0 | 4.3138 | 0 | 11.0904 | 0.32077 | 0 | 54.5001 | 31.125 | 190.5336 | 0%
CZ 2A | 0.18756 | 0.020315 | 0.0087111 | 0.0026751 | 0.01481 | 0.29358 | 0.11012 | 0.12565 | 0.0036361 | 0.033684 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.786 | 14.12% | CZ 2A | 6.0204 | 0.65207 | 0.88889 | 0.27296 | 0.47537 | 9.4232 | 3.5347 | 4.033 | 0.11671 | 1.0812 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 58.1239 | 14.12% | CZ 2A | 1.7645 | 0.19111 | 0 | 0 | 0.13932 | 2.7618 | 1.036 | 1.182 | 0.034206 | 0.31687 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 16.6946 | 14.12% | CZ 2A | 0 | 0 | 0.0088889 | 0.0027296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011619 | 14.12% | CZ 2A | 18.4722 | 2.0007 | 0.97156 | 0.29835 | 1.4586 | 28.9131 | 10.8455 | 12.3743 | 0.35811 | 3.3173 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 176.046 | 14.12%
CZ 2B | 0.18767 | 0.020327 | 0.0087497 | 0.0020483 | 0.083452 | 0.25213 | 0.080805 | 0.14042 | 0 | 0.02832 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.7892 | 1.729% | CZ 2B | 6.0237 | 0.65247 | 0.89282 | 0.20902 | 2.6786 | 8.0927 | 2.5937 | 4.5073 | 0 | 0.90901 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 58.1848 | 1.729% | CZ 2B | 1.7654 | 0.19123 | 0 | 0 | 0.78506 | 2.3718 | 0.76016 | 1.321 | 0 | 0.26642 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 16.7301 | 1.729% | CZ 2B | 0 | 0 | 0.0089282 | 0.0020902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011018 | 1.729% | CZ 2B | 18.4825 | 2.002 | 0.97586 | 0.22845 | 8.2188 | 24.8307 | 7.9581 | 13.8297 | 0 | 2.7891 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 176.3513 | 1.729%
CZ 3A | 0.18817 | 0.020481 | 0.009849 | 0.013218 | 0.042978 | 0.20541 | 0.074868 | 0.12445 | 0.0025041 | 0.025307 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6925 | 14.09% | CZ 3A | 6.0398 | 0.65739 | 1.005 | 1.3487 | 1.3795 | 6.5931 | 2.4031 | 3.9944 | 0.080375 | 0.81229 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 55.9392 | 14.09% | CZ 3A | 1.7702 | 0.19267 | 0 | 0 | 0.40431 | 1.9323 | 0.70431 | 1.1707 | 0.023557 | 0.23807 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 15.705 | 14.09% | CZ 3A | 0 | 0 | 0.01005 | 0.013487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023537 | 14.09% | CZ 3A | 18.5318 | 2.0171 | 1.0985 | 1.4742 | 4.2327 | 20.2294 | 7.3734 | 12.256 | 0.24661 | 2.4923 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 166.9883 | 14.09%
CZ 3B | 0.18771 | 0.020159 | 0.0095577 | 0.0054684 | 0.090484 | 0.21689 | 0.070976 | 0.1514 | 0 | 0.025724 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.7637 | 6.659% | CZ 3B | 6.025 | 0.64705 | 0.97527 | 0.558 | 2.9044 | 6.9618 | 2.2782 | 4.8596 | 0 | 0.82569 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 57.6604 | 6.659% | CZ 3B | 1.7658 | 0.18964 | 0 | 0 | 0.85122 | 2.0404 | 0.6677 | 1.4243 | 0 | 0.242 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 16.4499 | 6.659% | CZ 3B | 0 | 0 | 0.0097527 | 0.00558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015333 | 6.659% | CZ 3B | 18.4865 | 1.9853 | 1.066 | 0.6099 | 8.9114 | 21.3607 | 6.9901 | 14.9106 | 0 | 2.5335 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 173.8901 | 6.659%
CZ 3C | 0.18791 | 0.020133 | 0.009974 | 0.00076978 | 0.020638 | 0.14707 | 0.05831 | 0.1214 | 0 | 0.020306 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.5718 | 5.951% | CZ 3C | 6.0315 | 0.64623 | 1.0178 | 0.078549 | 0.66243 | 4.7205 | 1.8716 | 3.8967 | 0 | 0.65176 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 51.2026 | 5.951% | CZ 3C | 1.7677 | 0.1894 | 0 | 0 | 0.19415 | 1.3835 | 0.54854 | 1.1421 | 0 | 0.19102 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 14.6853 | 5.951% | CZ 3C | 0 | 0 | 0.010178 | 0.00078549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010963 | 5.951% | CZ 3C | 18.5064 | 1.9828 | 1.1124 | 0.085855 | 2.0325 | 14.4839 | 5.7426 | 11.9562 | 0 | 1.9998 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 154.9388 | 5.951%
CZ 4A | 0.18809 | 0.020378 | 0.010756 | 0.016823 | 0.046259 | 0.16588 | 0.054509 | 0.12273 | 0.0029472 | 0.019976 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6336 | 29.22% | CZ 4A | 6.0373 | 0.65408 | 1.0976 | 1.7166 | 1.4848 | 5.3244 | 1.7496 | 3.9394 | 0.094598 | 0.64119 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 54.3651 | 29.22% | CZ 4A | 1.7694 | 0.1917 | 0 | 0 | 0.43517 | 1.5605 | 0.51278 | 1.1546 | 0.027725 | 0.18792 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 15.1087 | 29.22% | CZ 4A | 0 | 0 | 0.010976 | 0.017166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028142 | 29.22% | CZ 4A | 18.5241 | 2.0069 | 1.1996 | 1.8762 | 4.5558 | 16.3369 | 5.3683 | 12.0873 | 0.29025 | 1.9674 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 161.249 | 29.22%
CZ 4B | 0.18737 | 0.020206 | 0.010498 | 0.011799 | 0.11792 | 0.16593 | 0.050586 | 0.15208 | 0 | 0.019613 | 0 | 0.11261 | 0.003257 | 0 | 0.55338 | 0.31604 | 1.7213 | 0.02014% | CZ 4B | 6.0141 | 0.64857 | 1.0712 | 1.204 | 3.785 | 5.3262 | 1.6237 | 4.8813 | 0 | 0.62954 | 0 | 3.6145 | 0.10454 | 0 | 17.7624 | 10.1441 | 56.809 | 0.02014% | CZ 4B | 1.7626 | 0.19009 | 0 | 0 | 1.1093 | 1.561 | 0.47588 | 1.4306 | 0 | 0.18451 | 0 | 1.0594 | 0.03064 | 0 | 5.2059 | 2.9731 | 15.983 | 0.02014% | CZ 4B | 0 | 0 | 0.010712 | 0.01204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022752 | 0.02014% | CZ 4B | 18.453 | 1.99 | 1.1708 | 1.316 | 11.6135 | 16.3422 | 4.982 | 14.9773 | 0 | 1.9316 | 0 | 11.0904 | 0.32077 | 0 | 54.5001 | 31.125 | 169.8124 | 0.02014%
CZ 4C | 0.18883 | 0.02066 | 0.011034 | 0.018064 | 0.052175 | 0.080198 | 0.02735 | 0.12301 | 0 | 0.012991 | 0 | 0.11261 | 0.0032582 | 0 | 0.55338 | 0.31604 | 1.5196 | 6.185% | CZ 4C | 6.0611 | 0.66314 | 1.1259 | 1.8433 | 1.6747 | 2.5742 | 0.87789 | 3.9485 | 0 | 0.41697 | 0 | 3.6145 | 0.10458 | 0 | 17.7624 | 10.1441 | 50.8112 | 6.185% | CZ 4C | 1.7764 | 0.19435 | 0 | 0 | 0.49083 | 0.75445 | 0.25729 | 1.1572 | 0 | 0.12221 | 0 | 1.0594 | 0.030651 | 0 | 5.2059 | 2.9731 | 14.0217 | 6.185% | CZ 4C | 0 | 0 | 0.011259 | 0.018433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029692 | 6.185% | CZ 4C | 18.5972 | 2.0347 | 1.2306 | 2.0147 | 5.1385 | 7.8983 | 2.6936 | 12.115 | 0 | 1.2794 | 0 | 11.0904 | 0.32088 | 0 | 54.5001 | 31.125 | 150.0383 | 6.185%
CZ 5A | 0.18792 | 0.020477 | 0.01153 | 0.027455 | 0.075083 | 0.11634 | 0.038694 | 0.12388 | 0.002382 | 0.016293 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6053 | 12.51% | CZ 5A | 6.0317 | 0.65728 | 1.1765 | 2.8015 | 2.41 | 3.7342 | 1.242 | 3.9763 | 0.076458 | 0.52296 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 54.2543 | 12.51% | CZ 5A | 1.7678 | 0.19264 | 0 | 0 | 0.70633 | 1.0944 | 0.36401 | 1.1654 | 0.022409 | 0.15327 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 14.7352 | 12.51% | CZ 5A | 0 | 0 | 0.011765 | 0.028015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03978 | 12.51% | CZ 5A | 18.5069 | 2.0167 | 1.2859 | 3.062 | 7.3945 | 11.4575 | 3.8108 | 12.2004 | 0.23459 | 1.6046 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 158.6102 | 12.51%
CZ 5B | 0.18776 | 0.020345 | 0.011311 | 0.029926 | 0.13745 | 0.12491 | 0.037403 | 0.15313 | 0 | 0.017409 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.7049 | 3.999% | CZ 5B | 6.0268 | 0.65304 | 1.1542 | 3.0537 | 4.4118 | 4.0095 | 1.2005 | 4.915 | 0 | 0.5588 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 57.6089 | 3.999% | CZ 5B | 1.7664 | 0.19139 | 0 | 0 | 1.293 | 1.1751 | 0.35186 | 1.4405 | 0 | 0.16378 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 15.6509 | 3.999% | CZ 5B | 0 | 0 | 0.011542 | 0.030537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042079 | 3.999% | CZ 5B | 18.492 | 2.0037 | 1.2616 | 3.3377 | 13.5367 | 12.3022 | 3.6836 | 15.0806 | 0 | 1.7146 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 168.4489 | 3.999%
CZ 5C | 0.18887 | 0.020689 | 0.011474 | 0.018605 | 0.043494 | 0.074289 | 0.021088 | 0.12451 | 0 | 0.010369 | 0 | 0.11261 | 0.0032582 | 0 | 0.55338 | 0.31604 | 1.4987 | 0.02726% | CZ 5C | 6.0623 | 0.66407 | 1.1709 | 1.8985 | 1.3961 | 2.3845 | 0.67688 | 3.9966 | 0 | 0.33283 | 0 | 3.6145 | 0.10458 | 0 | 17.7624 | 10.1441 | 50.2081 | 0.02726% | CZ 5C | 1.7767 | 0.19463 | 0 | 0 | 0.40917 | 0.69886 | 0.19838 | 1.1714 | 0 | 0.097548 | 0 | 1.0594 | 0.030651 | 0 | 5.2059 | 2.9731 | 13.8156 | 0.02726% | CZ 5C | 0 | 0 | 0.011709 | 0.018985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030693 | 0.02726% | CZ 5C | 18.6008 | 2.0375 | 1.2798 | 2.075 | 4.2836 | 7.3164 | 2.0769 | 12.2629 | 0 | 1.0212 | 0 | 11.0904 | 0.32088 | 0 | 54.5001 | 31.125 | 147.9903 | 0.02726%
CZ 6A | 0.18796 | 0.020502 | 0.01211 | 0.049031 | 0.082918 | 0.11731 | 0.037373 | 0.1292 | 0.0027215 | 0.017261 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6417 | 2.349% | CZ 6A | 6.033 | 0.65806 | 1.2357 | 5.0032 | 2.6615 | 3.7653 | 1.1996 | 4.1471 | 0.087353 | 0.55403 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 56.9703 | 2.349% | CZ 6A | 1.7682 | 0.19287 | 0 | 0 | 0.78004 | 1.1035 | 0.35158 | 1.2154 | 0.025602 | 0.16238 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 14.8685 | 2.349% | CZ 6A | 0 | 0 | 0.012357 | 0.050032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062389 | 2.349% | CZ 6A | 18.511 | 2.0191 | 1.3506 | 5.4685 | 8.1662 | 11.553 | 3.6807 | 12.7244 | 0.26802 | 1.6999 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 162.4777 | 2.349%
CZ 6B | 0.18805 | 0.020666 | 0.011963 | 0.056553 | 0.12732 | 0.10927 | 0.031626 | 0.14588 | 0 | 0.014991 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6916 | 0.09127% | CZ 6B | 6.0362 | 0.66333 | 1.2207 | 5.7707 | 4.0866 | 3.5072 | 1.0151 | 4.6824 | 0 | 0.48118 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 59.0889 | 0.09127% | CZ 6B | 1.7691 | 0.19441 | 0 | 0 | 1.1977 | 1.0279 | 0.29751 | 1.3723 | 0 | 0.14103 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 15.2689 | 0.09127% | CZ 6B | 0 | 0 | 0.012207 | 0.057707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069914 | 0.09127% | CZ 6B | 18.5207 | 2.0353 | 1.3342 | 6.3073 | 12.5389 | 10.7613 | 3.1147 | 14.367 | 0 | 1.4764 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 167.492 | 0.09127%
CZ 7 | 0.18801 | 0.020709 | 0.012798 | 0.050859 | 0.082713 | 0.11021 | 0.031068 | 0.13217 | 0.0030123 | 0.016699 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6335 | 0.2174% | CZ 7 | 6.0347 | 0.66471 | 1.3059 | 5.1897 | 2.6549 | 3.5374 | 0.9972 | 4.2422 | 0.096689 | 0.536 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 56.8849 | 0.2174% | CZ 7 | 1.7687 | 0.19482 | 0 | 0 | 0.77811 | 1.0367 | 0.29226 | 1.2433 | 0.028338 | 0.15709 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 14.7683 | 0.2174% | CZ 7 | 0 | 0 | 0.013059 | 0.051897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064956 | 0.2174% | CZ 7 | 18.5161 | 2.0395 | 1.4273 | 5.6723 | 8.146 | 10.8537 | 3.0597 | 13.0164 | 0.29667 | 1.6446 | 0 | 11.0904 | 0.32082 | 0 | 54.5001 | 31.125 | 161.7086 | 0.2174%
CZ 8 | 0.19234 | 0.022328 | 0.013728 | 0.071598 | 0.097241 | 0.080543 | 0.018719 | 0.13273 | 0.0032754 | 0.012999 | 0 | 0.11261 | 0.00326 | 0 | 0.55338 | 0.31604 | 1.6308 | 0% | CZ 8 | 6.1736 | 0.71668 | 1.4008 | 7.3059 | 3.1212 | 2.5852 | 0.60084 | 4.2602 | 0.10513 | 0.41724 | 0 | 3.6145 | 0.10464 | 0 | 17.7624 | 10.1441 | 58.3125 | 0% | CZ 8 | 1.8094 | 0.21005 | 0 | 0 | 0.91478 | 0.75769 | 0.1761 | 1.2486 | 0.030812 | 0.12229 | 0 | 1.0594 | 0.030668 | 0 | 5.2059 | 2.9731 | 14.5386 | 0% | CZ 8 | 0 | 0 | 0.014008 | 0.073059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087067 | 0% | CZ 8 | 18.9423 | 2.199 | 1.5311 | 7.9854 | 9.5768 | 7.9323 | 1.8436 | 13.0716 | 0.32258 | 1.2802 | 0 | 11.0904 | 0.32106 | 0 | 54.5001 | 31.125 | 161.7213 | 0%
US Weighted | 0.18798 | 0.020384 | 0.010276 | 0.014679 | 0.050754 | 0.18466 | 0.064517 | 0.12745 | 0.0022936 | 0.022668 | 0 | 0.11261 | 0.0032576 | 0 | 0.55338 | 0.31604 | 1.6709 | 100% | US Weighted | 6.0336 | 0.65429 | 1.0485 | 1.4978 | 1.6291 | 5.9273 | 2.0708 | 4.0907 | 0.07362 | 0.72758 | 0 | 3.6145 | 0.10456 | 0 | 17.7624 | 10.1441 | 55.379 | 100% | US Weighted | 1.7684 | 0.19176 | 0 | 0 | 0.47746 | 1.7372 | 0.60693 | 1.1989 | 0.021577 | 0.21324 | 0 | 1.0594 | 0.030645 | 0 | 5.2059 | 2.9731 | 15.4844 | 100% | US Weighted | 0 | 0 | 0.010485 | 0.014978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025463 | 100% | US Weighted | 18.5129 | 2.0076 | 1.146 | 1.6371 | 4.9986 | 18.1868 | 6.3539 | 12.5515 | 0.22589 | 2.2324 | 0 | 11.0904 | 0.32083 | 0 | 54.5001 | 31.125 | 164.889 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.20137 | 0.040365 | 0.0077809 | 0.00027796 | 0 | 0.49259 | 0.16235 | 0.14343 | 0.0076224 | 0.054826 | 0 | 0.11261 | 0.0047297 | 0 | 0.55338 | 0.31604 | 2.0974 | 0% | CZ 0A | 6.4635 | 1.2956 | 0.79397 | 0.028363 | 0 | 15.811 | 5.2111 | 4.6038 | 0.24466 | 1.7598 | 0 | 3.6145 | 0.15181 | 0 | 17.7624 | 10.1441 | 67.8846 | 0% | CZ 0A | 1.8943 | 0.37973 | 0 | 0 | 0 | 4.6339 | 1.5273 | 1.3493 | 0.071706 | 0.51576 | 0 | 1.0594 | 0.044494 | 0 | 5.2059 | 2.9731 | 19.6548 | 0% | CZ 0A | 0 | 0 | 0.0079397 | 0.00028363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082234 | 0% | CZ 0A | 19.8319 | 3.9754 | 0.86781 | 0.031001 | 0 | 48.5128 | 15.9891 | 14.1259 | 0.75069 | 5.3995 | 0 | 11.0904 | 0.46581 | 0 | 54.5001 | 31.125 | 206.6653 | 0%
CZ 0B | 0.20156 | 0.040348 | 0.007766 | 0.00027609 | 0.001061 | 0.48823 | 0.13996 | 0.14026 | 0 | 0.054344 | 0 | 0.11261 | 0.0047297 | 0 | 0.55338 | 0.31604 | 2.0606 | 0% | CZ 0B | 6.4695 | 1.2951 | 0.79245 | 0.028173 | 0.034055 | 15.671 | 4.4925 | 4.502 | 0 | 1.7443 | 0 | 3.6145 | 0.15181 | 0 | 17.7624 | 10.1441 | 66.7019 | 0% | CZ 0B | 1.8961 | 0.37957 | 0 | 0 | 0.009981 | 4.5929 | 1.3167 | 1.3194 | 0 | 0.51123 | 0 | 1.0594 | 0.044494 | 0 | 5.2059 | 2.9731 | 19.3087 | 0% | CZ 0B | 0 | 0 | 0.0079245 | 0.00028173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082062 | 0% | CZ 0B | 19.8504 | 3.9737 | 0.86615 | 0.030793 | 0.10449 | 48.0831 | 13.7844 | 13.8133 | 0 | 5.3521 | 0 | 11.0904 | 0.46581 | 0 | 54.5001 | 31.125 | 203.0396 | 0%
CZ 1A | 0.20183 | 0.040354 | 0.0083454 | 0.00029826 | 0 | 0.38572 | 0.13835 | 0.13622 | 0.0070045 | 0.042399 | 0 | 0.11261 | 0.0047297 | 0 | 0.55338 | 0.31604 | 1.9473 | 2.832% | CZ 1A | 6.4784 | 1.2953 | 0.85157 | 0.030435 | 0 | 12.3807 | 4.4406 | 4.3725 | 0.22483 | 1.3609 | 0 | 3.6145 | 0.15181 | 0 | 17.7624 | 10.1441 | 63.108 | 2.832% | CZ 1A | 1.8987 | 0.37962 | 0 | 0 | 0 | 3.6286 | 1.3015 | 1.2815 | 0.065894 | 0.39886 | 0 | 1.0594 | 0.044494 | 0 | 5.2059 | 2.9731 | 18.2374 | 2.832% | CZ 1A | 0 | 0 | 0.0085157 | 0.00030435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0088201 | 2.832% | CZ 1A | 19.8775 | 3.9743 | 0.93077 | 0.033266 | 0 | 37.9875 | 13.625 | 13.416 | 0.68984 | 4.1757 | 0 | 11.0904 | 0.46581 | 0 | 54.5001 | 31.125 | 191.8912 | 2.832%
CZ 1B | 0.20191 | 0.040288 | 0.0083708 | 0.0017674 | 0.0062942 | 0.42257 | 0.12239 | 0.13786 | 0 | 0.046691 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.9749 | 0% | CZ 1B | 6.4809 | 1.2932 | 0.85416 | 0.18035 | 0.20203 | 13.5637 | 3.9286 | 4.4252 | 0 | 1.4987 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 64.0996 | 0% | CZ 1B | 1.8995 | 0.37901 | 0 | 0 | 0.059212 | 3.9753 | 1.1514 | 1.2969 | 0 | 0.43924 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 18.4833 | 0% | CZ 1B | 0 | 0 | 0.0085416 | 0.0018035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010345 | 0% | CZ 1B | 19.8854 | 3.9678 | 0.9336 | 0.19712 | 0.61989 | 41.6172 | 12.0541 | 13.5777 | 0 | 4.5984 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 194.6325 | 0%
CZ 2A | 0.2018 | 0.040271 | 0.008995 | 0.0029655 | 0.00029916 | 0.32404 | 0.11878 | 0.12675 | 0.0038986 | 0.036994 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.8515 | 14.12% | CZ 2A | 6.4774 | 1.2926 | 0.91786 | 0.3026 | 0.0096024 | 10.4009 | 3.8126 | 4.0684 | 0.12514 | 1.1874 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 60.2672 | 14.12% | CZ 2A | 1.8984 | 0.37884 | 0 | 0 | 0.0028143 | 3.0483 | 1.1174 | 1.1924 | 0.036675 | 0.34801 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 17.3056 | 14.12% | CZ 2A | 0 | 0 | 0.0091786 | 0.003026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012205 | 14.12% | CZ 2A | 19.8744 | 3.9661 | 1.0032 | 0.33074 | 0.029463 | 31.9128 | 11.6981 | 12.4829 | 0.38395 | 3.6434 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 182.5063 | 14.12%
CZ 2B | 0.20191 | 0.040308 | 0.0090362 | 0.0021314 | 0.090361 | 0.24792 | 0.079348 | 0.14163 | 0 | 0.030057 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.8295 | 1.729% | CZ 2B | 6.4808 | 1.2938 | 0.92206 | 0.21749 | 2.9004 | 7.9576 | 2.5469 | 4.546 | 0 | 0.96476 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 59.5026 | 1.729% | CZ 2B | 1.8994 | 0.37919 | 0 | 0 | 0.85006 | 2.3322 | 0.74645 | 1.3324 | 0 | 0.28276 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 17.1052 | 1.729% | CZ 2B | 0 | 0 | 0.0092206 | 0.0021749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011396 | 1.729% | CZ 2B | 19.885 | 3.9698 | 1.0078 | 0.23772 | 8.8993 | 24.4161 | 7.8146 | 13.9484 | 0 | 2.9602 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 180.3201 | 1.729%
CZ 3A | 0.20242 | 0.040298 | 0.010128 | 0.015718 | 0.0010622 | 0.25103 | 0.087968 | 0.12533 | 0.0031332 | 0.027829 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.7517 | 14.09% | CZ 3A | 6.4973 | 1.2935 | 1.0335 | 1.6038 | 0.034093 | 8.0574 | 2.8236 | 4.0228 | 0.10057 | 0.89325 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 58.0326 | 14.09% | CZ 3A | 1.9043 | 0.3791 | 0 | 0 | 0.0099922 | 2.3615 | 0.82755 | 1.179 | 0.029475 | 0.2618 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 16.2354 | 14.09% | CZ 3A | 0 | 0 | 0.010335 | 0.016038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026373 | 14.09% | CZ 3A | 19.9357 | 3.9688 | 1.1296 | 1.753 | 0.10461 | 24.7224 | 8.6636 | 12.3431 | 0.30857 | 2.7408 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 172.8513 | 14.09%
CZ 3B | 0.20196 | 0.040296 | 0.0098362 | 0.0059895 | 0.090459 | 0.21837 | 0.071073 | 0.1432 | 0 | 0.025342 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.7933 | 6.659% | CZ 3B | 6.4825 | 1.2934 | 1.0037 | 0.61117 | 2.9035 | 7.0092 | 2.2813 | 4.5964 | 0 | 0.81343 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 58.6673 | 6.659% | CZ 3B | 1.8999 | 0.37908 | 0 | 0 | 0.85098 | 2.0543 | 0.66861 | 1.3471 | 0 | 0.2384 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 16.7211 | 6.659% | CZ 3B | 0 | 0 | 0.010037 | 0.0061117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016149 | 6.659% | CZ 3B | 19.89 | 3.9686 | 1.097 | 0.66801 | 8.9089 | 21.5062 | 6.9997 | 14.1029 | 0 | 2.4958 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 176.8185 | 6.659%
CZ 3C | 0.20217 | 0.040401 | 0.010258 | 0.00093857 | 0.020168 | 0.14595 | 0.058198 | 0.12197 | 0 | 0.021407 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.6082 | 5.951% | CZ 3C | 6.4892 | 1.2968 | 1.0468 | 0.095773 | 0.64735 | 4.6848 | 1.868 | 3.9148 | 0 | 0.68711 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 52.4035 | 5.951% | CZ 3C | 1.9019 | 0.38006 | 0 | 0 | 0.18973 | 1.373 | 0.54748 | 1.1474 | 0 | 0.20138 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 15.0237 | 5.951% | CZ 3C | 0 | 0 | 0.010468 | 0.00095773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011425 | 5.951% | CZ 3C | 19.9109 | 3.9789 | 1.1441 | 0.10468 | 1.9863 | 14.3743 | 5.7316 | 12.0118 | 0 | 2.1083 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 158.5321 | 5.951%
CZ 4A | 0.20215 | 0.040447 | 0.011031 | 0.021112 | 0.0015562 | 0.21811 | 0.068803 | 0.12568 | 0.0034069 | 0.02267 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.7017 | 29.22% | CZ 4A | 6.4886 | 1.2983 | 1.1256 | 2.1543 | 0.049951 | 7.0009 | 2.2084 | 4.0342 | 0.10935 | 0.72765 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 56.87 | 29.22% | CZ 4A | 1.9017 | 0.3805 | 0 | 0 | 0.01464 | 2.0519 | 0.64725 | 1.1823 | 0.03205 | 0.21326 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 15.7064 | 29.22% | CZ 4A | 0 | 0 | 0.011256 | 0.021543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032799 | 29.22% | CZ 4A | 19.9089 | 3.9834 | 1.2303 | 2.3546 | 0.15327 | 21.4809 | 6.7761 | 12.378 | 0.33553 | 2.2326 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 168.015 | 29.22%
CZ 4B | 0.20146 | 0.040289 | 0.010775 | 0.011869 | 0.11771 | 0.16825 | 0.050681 | 0.15568 | 0 | 0.021481 | 0 | 0.11261 | 0.0047297 | 0 | 0.55338 | 0.31604 | 1.765 | 0.02014% | CZ 4B | 6.4665 | 1.2932 | 1.0995 | 1.2111 | 3.7782 | 5.4004 | 1.6267 | 4.997 | 0 | 0.68951 | 0 | 3.6145 | 0.15181 | 0 | 17.7624 | 10.1441 | 58.235 | 0.02014% | CZ 4B | 1.8952 | 0.37902 | 0 | 0 | 1.1073 | 1.5828 | 0.47677 | 1.4645 | 0 | 0.20208 | 0 | 1.0594 | 0.044494 | 0 | 5.2059 | 2.9731 | 16.3905 | 0.02014% | CZ 4B | 0 | 0 | 0.010995 | 0.012111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023106 | 0.02014% | CZ 4B | 19.8412 | 3.9679 | 1.2018 | 1.3237 | 11.5926 | 16.57 | 4.9913 | 15.3321 | 0 | 2.1156 | 0 | 11.0904 | 0.46581 | 0 | 54.5001 | 31.125 | 174.1175 | 0.02014%
CZ 4C | 0.20284 | 0.04046 | 0.011304 | 0.018868 | 0.059578 | 0.076075 | 0.026331 | 0.12411 | 0 | 0.014148 | 0 | 0.11261 | 0.0047309 | 0 | 0.55338 | 0.31604 | 1.5605 | 6.185% | CZ 4C | 6.5106 | 1.2987 | 1.1534 | 1.9253 | 1.9123 | 2.4418 | 0.84518 | 3.9836 | 0 | 0.45411 | 0 | 3.6145 | 0.15185 | 0 | 17.7624 | 10.1441 | 52.1979 | 6.185% | CZ 4C | 1.9081 | 0.38062 | 0 | 0 | 0.56047 | 0.71566 | 0.24771 | 1.1675 | 0 | 0.13309 | 0 | 1.0594 | 0.044505 | 0 | 5.2059 | 2.9731 | 14.396 | 6.185% | CZ 4C | 0 | 0 | 0.011534 | 0.019253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030787 | 6.185% | CZ 4C | 19.9764 | 3.9847 | 1.2607 | 2.1043 | 5.8676 | 7.4923 | 2.5933 | 12.223 | 0 | 1.3933 | 0 | 11.0904 | 0.46592 | 0 | 54.5001 | 31.125 | 154.0768 | 6.185%
CZ 5A | 0.20206 | 0.040342 | 0.011806 | 0.034488 | 0.076012 | 0.11777 | 0.038825 | 0.12584 | 0.0028666 | 0.018426 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.6552 | 12.51% | CZ 5A | 6.4855 | 1.2949 | 1.2046 | 3.5192 | 2.4398 | 3.7803 | 1.2462 | 4.0391 | 0.092012 | 0.59145 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 56.3658 | 12.51% | CZ 5A | 1.9008 | 0.37951 | 0 | 0 | 0.71507 | 1.1079 | 0.36524 | 1.1838 | 0.026967 | 0.17334 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 15.1354 | 12.51% | CZ 5A | 0 | 0 | 0.012046 | 0.035192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047238 | 12.51% | CZ 5A | 19.8995 | 3.9731 | 1.3167 | 3.8465 | 7.486 | 11.5989 | 3.8237 | 12.393 | 0.28232 | 1.8147 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 163.6158 | 12.51%
CZ 5B | 0.20192 | 0.040407 | 0.011587 | 0.031047 | 0.13724 | 0.12567 | 0.037338 | 0.1552 | 0 | 0.019268 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.7464 | 3.999% | CZ 5B | 6.481 | 1.297 | 1.1823 | 3.1681 | 4.4049 | 4.0337 | 1.1985 | 4.9817 | 0 | 0.61845 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 59.0384 | 3.999% | CZ 5B | 1.8995 | 0.38012 | 0 | 0 | 1.291 | 1.1822 | 0.35125 | 1.46 | 0 | 0.18126 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 16.0282 | 3.999% | CZ 5B | 0 | 0 | 0.011823 | 0.031681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043504 | 3.999% | CZ 5B | 19.8857 | 3.9795 | 1.2923 | 3.4627 | 13.5157 | 12.3765 | 3.6773 | 15.2852 | 0 | 1.8976 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 172.5537 | 3.999%
CZ 5C | 0.20301 | 0.04043 | 0.011744 | 0.0191 | 0.04316 | 0.079073 | 0.02242 | 0.12604 | 0 | 0.011351 | 0 | 0.11261 | 0.0047309 | 0 | 0.55338 | 0.31604 | 1.5431 | 0.02726% | CZ 5C | 6.5162 | 1.2977 | 1.1984 | 1.949 | 1.3853 | 2.5381 | 0.71965 | 4.0458 | 0 | 0.36434 | 0 | 3.6145 | 0.15185 | 0 | 17.7624 | 10.1441 | 51.6873 | 0.02726% | CZ 5C | 1.9098 | 0.38034 | 0 | 0 | 0.40602 | 0.74387 | 0.21092 | 1.1857 | 0 | 0.10678 | 0 | 1.0594 | 0.044505 | 0 | 5.2059 | 2.9731 | 14.2262 | 0.02726% | CZ 5C | 0 | 0 | 0.011984 | 0.01949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031474 | 0.02726% | CZ 5C | 19.9936 | 3.9818 | 1.3098 | 2.1303 | 4.2506 | 7.7875 | 2.2081 | 12.4136 | 0 | 1.1179 | 0 | 11.0904 | 0.46592 | 0 | 54.5001 | 31.125 | 152.3745 | 0.02726%
CZ 6A | 0.20218 | 0.040387 | 0.012384 | 0.065702 | 0.082119 | 0.11871 | 0.037486 | 0.13042 | 0.003145 | 0.020047 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.6993 | 2.349% | CZ 6A | 6.4897 | 1.2963 | 1.2637 | 6.7043 | 2.6358 | 3.8104 | 1.2032 | 4.1862 | 0.10095 | 0.64347 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 60.0068 | 2.349% | CZ 6A | 1.902 | 0.37993 | 0 | 0 | 0.77252 | 1.1168 | 0.35264 | 1.2269 | 0.029586 | 0.18859 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 15.2517 | 2.349% | CZ 6A | 0 | 0 | 0.012637 | 0.067043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07968 | 2.349% | CZ 6A | 19.9122 | 3.9775 | 1.3812 | 7.3278 | 8.0875 | 11.6913 | 3.6918 | 12.8444 | 0.30974 | 1.9744 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 168.379 | 2.349%
CZ 6B | 0.20228 | 0.040327 | 0.012239 | 0.061252 | 0.12721 | 0.10926 | 0.03151 | 0.14271 | 0 | 0.016408 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.73 | 0.09127% | CZ 6B | 6.4929 | 1.2944 | 1.2489 | 6.2502 | 4.083 | 3.5071 | 1.0114 | 4.5806 | 0 | 0.52665 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 60.668 | 0.09127% | CZ 6B | 1.903 | 0.37937 | 0 | 0 | 1.1967 | 1.0279 | 0.29643 | 1.3425 | 0 | 0.15435 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 15.5829 | 0.09127% | CZ 6B | 0 | 0 | 0.012489 | 0.062502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074991 | 0.09127% | CZ 6B | 19.9221 | 3.9717 | 1.365 | 6.8315 | 12.5279 | 10.7608 | 3.1033 | 14.0547 | 0 | 1.6159 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 171.3341 | 0.09127%
CZ 7 | 0.20223 | 0.040439 | 0.013072 | 0.071567 | 0.083352 | 0.11012 | 0.031182 | 0.13337 | 0.0034021 | 0.019704 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.6952 | 0.2174% | CZ 7 | 6.491 | 1.298 | 1.3339 | 7.3027 | 2.6754 | 3.5346 | 1.0009 | 4.2809 | 0.1092 | 0.63245 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 60.3319 | 0.2174% | CZ 7 | 1.9024 | 0.38043 | 0 | 0 | 0.78412 | 1.0359 | 0.29334 | 1.2547 | 0.032005 | 0.18536 | 0 | 1.0594 | 0.044499 | 0 | 5.2059 | 2.9731 | 15.151 | 0.2174% | CZ 7 | 0 | 0 | 0.013339 | 0.073027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086366 | 0.2174% | CZ 7 | 19.9163 | 3.9827 | 1.4579 | 7.9819 | 8.2089 | 10.8453 | 3.071 | 13.1351 | 0.33506 | 1.9405 | 0 | 11.0904 | 0.46586 | 0 | 54.5001 | 31.125 | 168.0559 | 0.2174%
CZ 8 | 0.2066 | 0.040946 | 0.014011 | 0.11421 | 0.10035 | 0.077433 | 0.018589 | 0.13398 | 0.003597 | 0.016283 | 0 | 0.11261 | 0.0047338 | 0 | 0.55338 | 0.31604 | 1.7128 | 0% | CZ 8 | 6.6316 | 1.3143 | 1.4297 | 11.6536 | 3.221 | 2.4854 | 0.59668 | 4.3004 | 0.11546 | 0.52266 | 0 | 3.6145 | 0.15195 | 0 | 17.7624 | 10.1441 | 63.9437 | 0% | CZ 8 | 1.9436 | 0.38519 | 0 | 0 | 0.94402 | 0.72844 | 0.17488 | 1.2604 | 0.033838 | 0.15318 | 0 | 1.0594 | 0.044533 | 0 | 5.2059 | 2.9731 | 14.9063 | 0% | CZ 8 | 0 | 0 | 0.014297 | 0.11654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13083 | 0% | CZ 8 | 20.3475 | 4.0326 | 1.5627 | 12.7374 | 9.883 | 7.626 | 1.8308 | 13.1949 | 0.35425 | 1.6037 | 0 | 11.0904 | 0.46621 | 0 | 54.5001 | 31.125 | 170.3544 | 0%
US Weighted | 0.20214 | 0.040368 | 0.010554 | 0.017787 | 0.030376 | 0.21094 | 0.071731 | 0.12856 | 0.0026257 | 0.024938 | 0 | 0.11261 | 0.0047303 | 0 | 0.55338 | 0.31604 | 1.7268 | 100% | US Weighted | 6.4882 | 1.2957 | 1.0769 | 1.815 | 0.97499 | 6.7709 | 2.3024 | 4.1263 | 0.084279 | 0.80045 | 0 | 3.6145 | 0.15183 | 0 | 17.7624 | 10.1441 | 57.4079 | 100% | US Weighted | 1.9016 | 0.37975 | 0 | 0 | 0.28575 | 1.9844 | 0.67479 | 1.2094 | 0.024701 | 0.2346 | 0 | 1.0594 | 0.0445 | 0 | 5.2059 | 2.9731 | 15.9777 | 100% | US Weighted | 0 | 0 | 0.010769 | 0.01815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028919 | 100% | US Weighted | 19.9075 | 3.9756 | 1.177 | 1.9838 | 2.9916 | 20.7749 | 7.0644 | 12.6608 | 0.25859 | 2.456 | 0 | 11.0904 | 0.46587 | 0 | 54.5001 | 31.125 | 170.4316 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.22276 | 0.040365 | 0.0077809 | 0.00018555 | 0 | 0.56164 | 0.17432 | 0.15509 | 0 | 0.071329 | 0 | 0.11285 | 0.0047587 | 0 | 0.55338 | 0.31716 | 2.2216 | 0% | CZ 0A | 7.1501 | 1.2956 | 0.79397 | 0.018934 | 0 | 18.0273 | 5.5954 | 4.9781 | 0 | 2.2895 | 0 | 3.6222 | 0.15274 | 0 | 17.7624 | 10.1802 | 71.8665 | 0% | CZ 0A | 2.0956 | 0.37973 | 0 | 0 | 0 | 5.2835 | 1.6399 | 1.459 | 0 | 0.67101 | 0 | 1.0616 | 0.044767 | 0 | 5.2059 | 2.9837 | 20.8246 | 0% | CZ 0A | 0 | 0 | 0.0079397 | 0.00018934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081291 | 0% | CZ 0A | 21.9386 | 3.9754 | 0.86781 | 0.020695 | 0 | 55.3131 | 17.1684 | 15.2741 | 0 | 7.0248 | 0 | 11.1138 | 0.46866 | 0 | 54.5001 | 31.2359 | 218.9013 | 0%
CZ 0B | 0.22292 | 0.040348 | 0.0077651 | 0.00076382 | 0.0010527 | 0.49818 | 0.14554 | 0.14921 | 0 | 0.064566 | 0 | 0.11285 | 0.0047587 | 0 | 0.55338 | 0.31716 | 2.1185 | 0% | CZ 0B | 7.1554 | 1.2951 | 0.79236 | 0.077941 | 0.033789 | 15.9906 | 4.6716 | 4.7893 | 0 | 2.0724 | 0 | 3.6222 | 0.15274 | 0 | 17.7624 | 10.1802 | 68.5959 | 0% | CZ 0B | 2.0971 | 0.37957 | 0 | 0 | 0.009903 | 4.6866 | 1.3692 | 1.4037 | 0 | 0.6074 | 0 | 1.0616 | 0.044767 | 0 | 5.2059 | 2.9837 | 19.8493 | 0% | CZ 0B | 0 | 0 | 0.0079236 | 0.00077941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008703 | 0% | CZ 0B | 21.9548 | 3.9737 | 0.86605 | 0.08519 | 0.10367 | 49.0637 | 14.3338 | 14.6948 | 0 | 6.3589 | 0 | 11.1138 | 0.46866 | 0 | 54.5001 | 31.2359 | 208.7531 | 0%
CZ 1A | 0.22328 | 0.040354 | 0.0083452 | 0.00023753 | 0 | 0.40513 | 0.14549 | 0.14632 | 0 | 0.055899 | 0 | 0.11285 | 0.0047587 | 0 | 0.55338 | 0.31716 | 2.0132 | 2.832% | CZ 1A | 7.1668 | 1.2953 | 0.85155 | 0.024238 | 0 | 13.0039 | 4.6699 | 4.6967 | 0 | 1.7942 | 0 | 3.6222 | 0.15274 | 0 | 17.7624 | 10.1802 | 65.2202 | 2.832% | CZ 1A | 2.1005 | 0.37962 | 0 | 0 | 0 | 3.8112 | 1.3687 | 1.3765 | 0 | 0.52586 | 0 | 1.0616 | 0.044767 | 0 | 5.2059 | 2.9837 | 18.8583 | 2.832% | CZ 1A | 0 | 0 | 0.0085155 | 0.00024238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0087579 | 2.832% | CZ 1A | 21.9899 | 3.9743 | 0.93075 | 0.026492 | 0 | 39.8998 | 14.3287 | 14.4109 | 0 | 5.5052 | 0 | 11.1138 | 0.46866 | 0 | 54.5001 | 31.2359 | 198.3844 | 2.832%
CZ 1B | 0.22331 | 0.040288 | 0.0083702 | 0.0045243 | 0.0062693 | 0.43351 | 0.12707 | 0.14688 | 0 | 0.055312 | 0 | 0.11285 | 0.0047587 | 0 | 0.55338 | 0.31716 | 2.0337 | 0% | CZ 1B | 7.1676 | 1.2932 | 0.8541 | 0.46166 | 0.20123 | 13.9146 | 4.0788 | 4.7146 | 0 | 1.7754 | 0 | 3.6222 | 0.15274 | 0 | 17.7624 | 10.1802 | 66.1786 | 0% | CZ 1B | 2.1007 | 0.37901 | 0 | 0 | 0.058978 | 4.0781 | 1.1954 | 1.3818 | 0 | 0.52034 | 0 | 1.0616 | 0.044767 | 0 | 5.2059 | 2.9837 | 19.0102 | 0% | CZ 1B | 0 | 0 | 0.008541 | 0.0046166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013158 | 0% | CZ 1B | 21.9923 | 3.9678 | 0.93353 | 0.50459 | 0.61744 | 42.694 | 12.5149 | 14.4657 | 0 | 5.4474 | 0 | 11.1138 | 0.46866 | 0 | 54.5001 | 31.2359 | 200.4561 | 0%
CZ 2A | 0.22317 | 0.040271 | 0.0089952 | 0.0048873 | 0.00030212 | 0.33977 | 0.12519 | 0.13492 | 0 | 0.050695 | 0 | 0.11285 | 0.0047587 | 0 | 0.55338 | 0.31716 | 1.9163 | 14.12% | CZ 2A | 7.1632 | 1.2926 | 0.91788 | 0.49871 | 0.0096975 | 10.9057 | 4.0185 | 4.3305 | 0 | 1.6272 | 0 | 3.6222 | 0.15274 | 0 | 17.7624 | 10.1802 | 62.4815 | 14.12% | CZ 2A | 2.0994 | 0.37884 | 0 | 0 | 0.0028422 | 3.1963 | 1.1777 | 1.2692 | 0 | 0.4769 | 0 | 1.0616 | 0.044767 | 0 | 5.2059 | 2.9837 | 17.8971 | 14.12% | CZ 2A | 0 | 0 | 0.0091788 | 0.0049871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014166 | 14.12% | CZ 2A | 21.9787 | 3.9661 | 1.0032 | 0.54509 | 0.029755 | 33.462 | 12.3298 | 13.2874 | 0 | 4.9927 | 0 | 11.1138 | 0.46866 | 0 | 54.5001 | 31.2359 | 188.9132 | 14.12%
CZ 2B | 0.22336 | 0.040308 | 0.0090362 | 0.0038754 | 0.086772 | 0.25175 | 0.082451 | 0.14777 | 0 | 0.035304 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.8688 | 1.729% | CZ 2B | 7.1694 | 1.2938 | 0.92206 | 0.39545 | 2.7852 | 8.0806 | 2.6465 | 4.743 | 0 | 1.1332 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 60.8867 | 1.729% | CZ 2B | 2.1012 | 0.37919 | 0 | 0 | 0.8163 | 2.3683 | 0.77564 | 1.3901 | 0 | 0.33212 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 17.4587 | 1.729% | CZ 2B | 0 | 0 | 0.0092206 | 0.0039545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013175 | 1.729% | CZ 2B | 21.9978 | 3.9698 | 1.0078 | 0.43222 | 8.5458 | 24.7935 | 8.1202 | 14.5529 | 0 | 3.477 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 184.2155 | 1.729%
CZ 3A | 0.22392 | 0.040298 | 0.010129 | 0.023478 | 0.0010817 | 0.25585 | 0.090557 | 0.1312 | 0 | 0.03815 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.8028 | 14.09% | CZ 3A | 7.1875 | 1.2935 | 1.0335 | 2.3958 | 0.034721 | 8.2123 | 2.9067 | 4.2112 | 0 | 1.2245 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 60.2172 | 14.09% | CZ 3A | 2.1065 | 0.3791 | 0 | 0 | 0.010176 | 2.4069 | 0.8519 | 1.2342 | 0 | 0.35889 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 16.6436 | 14.09% | CZ 3A | 0 | 0 | 0.010335 | 0.023958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034293 | 14.09% | CZ 3A | 22.0532 | 3.9688 | 1.1297 | 2.6186 | 0.10653 | 25.1978 | 8.9185 | 12.9212 | 0 | 3.7572 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 177.99 | 14.09%
CZ 3B | 0.22347 | 0.040296 | 0.0098364 | 0.0090522 | 0.10025 | 0.20428 | 0.069339 | 0.14713 | 0 | 0.029686 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.8215 | 6.659% | CZ 3B | 7.1731 | 1.2934 | 1.0037 | 0.9237 | 3.2177 | 6.557 | 2.2256 | 4.7227 | 0 | 0.95284 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 59.7873 | 6.659% | CZ 3B | 2.1023 | 0.37908 | 0 | 0 | 0.94306 | 1.9217 | 0.65229 | 1.3841 | 0 | 0.27926 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 16.9578 | 6.659% | CZ 3B | 0 | 0 | 0.010037 | 0.009237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019274 | 6.659% | CZ 3B | 22.009 | 3.9686 | 1.0971 | 1.0096 | 9.8729 | 20.1187 | 6.8289 | 14.4906 | 0 | 2.9236 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 179.6374 | 6.659%
CZ 3C | 0.22372 | 0.040401 | 0.010258 | 0.0024837 | 0.024876 | 0.13382 | 0.05596 | 0.12979 | 0 | 0.027968 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.6374 | 5.951% | CZ 3C | 7.1808 | 1.2968 | 1.0467 | 0.25344 | 0.79846 | 4.2954 | 1.7962 | 4.1661 | 0 | 0.8977 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 53.4492 | 5.951% | CZ 3C | 2.1046 | 0.38006 | 0 | 0 | 0.23402 | 1.2589 | 0.52643 | 1.221 | 0 | 0.2631 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 15.284 | 5.951% | CZ 3C | 0 | 0 | 0.010467 | 0.0025344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013002 | 5.951% | CZ 3C | 22.0328 | 3.9789 | 1.1441 | 0.27701 | 2.4499 | 13.1795 | 5.5112 | 12.7829 | 0 | 2.7544 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 161.4292 | 5.951%
CZ 4A | 0.22367 | 0.040447 | 0.011031 | 0.043053 | 0.0015663 | 0.21841 | 0.070215 | 0.12959 | 0 | 0.029574 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.7557 | 29.22% | CZ 4A | 7.1795 | 1.2983 | 1.1256 | 4.3932 | 0.050275 | 7.0106 | 2.2537 | 4.1594 | 0 | 0.94925 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 60.1373 | 29.22% | CZ 4A | 2.1042 | 0.3805 | 0 | 0 | 0.014735 | 2.0547 | 0.66054 | 1.2191 | 0 | 0.27821 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 16.0078 | 29.22% | CZ 4A | 0 | 0 | 0.011256 | 0.043932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055188 | 29.22% | CZ 4A | 22.0286 | 3.9834 | 1.2303 | 4.8018 | 0.15426 | 21.5105 | 6.9151 | 12.7623 | 0 | 2.9126 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 173.6174 | 29.22%
CZ 4B | 0.22297 | 0.040289 | 0.010776 | 0.018077 | 0.12322 | 0.16057 | 0.050096 | 0.16253 | 0 | 0.027132 | 0 | 0.11285 | 0.0047587 | 0 | 0.55338 | 0.31716 | 1.8038 | 0.02014% | CZ 4B | 7.1567 | 1.2932 | 1.0996 | 1.8446 | 3.9551 | 5.1539 | 1.608 | 5.2167 | 0 | 0.87089 | 0 | 3.6222 | 0.15274 | 0 | 17.7624 | 10.1802 | 59.9162 | 0.02014% | CZ 4B | 2.0975 | 0.37902 | 0 | 0 | 1.1592 | 1.5105 | 0.47127 | 1.5289 | 0 | 0.25524 | 0 | 1.0616 | 0.044767 | 0 | 5.2059 | 2.9837 | 16.6975 | 0.02014% | CZ 4B | 0 | 0 | 0.010996 | 0.018446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029442 | 0.02014% | CZ 4B | 21.959 | 3.9679 | 1.2019 | 2.0162 | 12.1353 | 15.8138 | 4.9337 | 16.0064 | 0 | 2.6721 | 0 | 11.1138 | 0.46866 | 0 | 54.5001 | 31.2359 | 178.0247 | 0.02014%
CZ 4C | 0.2244 | 0.04046 | 0.011304 | 0.02637 | 0.053197 | 0.082586 | 0.027604 | 0.13086 | 0 | 0.01832 | 0 | 0.11285 | 0.0047599 | 0 | 0.55338 | 0.31716 | 1.6033 | 6.185% | CZ 4C | 7.2026 | 1.2987 | 1.1535 | 2.6909 | 1.7075 | 2.6508 | 0.88604 | 4.2004 | 0 | 0.58805 | 0 | 3.6222 | 0.15278 | 0 | 17.7624 | 10.1802 | 54.096 | 6.185% | CZ 4C | 2.111 | 0.38062 | 0 | 0 | 0.50044 | 0.77691 | 0.25968 | 1.2311 | 0 | 0.17235 | 0 | 1.0616 | 0.044778 | 0 | 5.2059 | 2.9837 | 14.7279 | 6.185% | CZ 4C | 0 | 0 | 0.011535 | 0.026909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038443 | 6.185% | CZ 4C | 22.0998 | 3.9847 | 1.2607 | 2.9411 | 5.2391 | 8.1335 | 2.7186 | 12.8881 | 0 | 1.8043 | 0 | 11.1138 | 0.46878 | 0 | 54.5001 | 31.2359 | 158.3885 | 6.185%
CZ 5A | 0.22355 | 0.040342 | 0.011808 | 0.07187 | 0.077347 | 0.11631 | 0.03849 | 0.13129 | 0 | 0.025177 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.7243 | 12.51% | CZ 5A | 7.1753 | 1.2949 | 1.2049 | 7.3337 | 2.4827 | 3.7332 | 1.2355 | 4.214 | 0 | 0.80814 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 61.1998 | 12.51% | CZ 5A | 2.103 | 0.37951 | 0 | 0 | 0.72763 | 1.0941 | 0.36209 | 1.2351 | 0 | 0.23685 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 15.4341 | 12.51% | CZ 5A | 0 | 0 | 0.012049 | 0.073337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085385 | 12.51% | CZ 5A | 22.016 | 3.9731 | 1.3169 | 8.0157 | 7.6176 | 11.4545 | 3.7907 | 12.9299 | 0 | 2.4796 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 170.9126 | 12.51%
CZ 5B | 0.22346 | 0.040407 | 0.011588 | 0.040232 | 0.13668 | 0.12712 | 0.037492 | 0.16165 | 0 | 0.024301 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.7911 | 3.999% | CZ 5B | 7.1725 | 1.297 | 1.1824 | 4.1053 | 4.387 | 4.0802 | 1.2034 | 5.1886 | 0 | 0.78 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 61.114 | 3.999% | CZ 5B | 2.1021 | 0.38012 | 0 | 0 | 1.2858 | 1.1958 | 0.3527 | 1.5207 | 0 | 0.2286 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 16.3617 | 3.999% | CZ 5B | 0 | 0 | 0.011824 | 0.041053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052878 | 3.999% | CZ 5B | 22.0074 | 3.9795 | 1.2924 | 4.4871 | 13.4605 | 12.5193 | 3.6924 | 15.9202 | 0 | 2.3933 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 177.0706 | 3.999%
CZ 5C | 0.22462 | 0.04043 | 0.011744 | 0.026119 | 0.059101 | 0.056782 | 0.017569 | 0.132 | 0 | 0.014373 | 0 | 0.11285 | 0.0047599 | 0 | 0.55338 | 0.31716 | 1.5709 | 0.02726% | CZ 5C | 7.2099 | 1.2977 | 1.1984 | 2.6652 | 1.897 | 1.8226 | 0.56392 | 4.237 | 0 | 0.46133 | 0 | 3.6222 | 0.15278 | 0 | 17.7624 | 10.1802 | 53.0705 | 0.02726% | CZ 5C | 2.1131 | 0.38034 | 0 | 0 | 0.55598 | 0.53417 | 0.16527 | 1.2418 | 0 | 0.13521 | 0 | 1.0616 | 0.044778 | 0 | 5.2059 | 2.9837 | 14.4217 | 0.02726% | CZ 5C | 0 | 0 | 0.011984 | 0.026652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038636 | 0.02726% | CZ 5C | 22.1219 | 3.9818 | 1.3098 | 2.913 | 5.8206 | 5.5922 | 1.7303 | 13.0003 | 0 | 1.4155 | 0 | 11.1138 | 0.46878 | 0 | 54.5001 | 31.2359 | 155.204 | 0.02726%
CZ 6A | 0.22371 | 0.040387 | 0.012387 | 0.11337 | 0.080866 | 0.12242 | 0.038077 | 0.13576 | 0 | 0.027472 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.7826 | 2.349% | CZ 6A | 7.1805 | 1.2963 | 1.264 | 11.5686 | 2.5956 | 3.9293 | 1.2222 | 4.3575 | 0 | 0.8818 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 66.0133 | 2.349% | CZ 6A | 2.1045 | 0.37993 | 0 | 0 | 0.76073 | 1.1516 | 0.3582 | 1.2771 | 0 | 0.25844 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 15.5864 | 2.349% | CZ 6A | 0 | 0 | 0.01264 | 0.11569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12833 | 2.349% | CZ 6A | 22.0318 | 3.9775 | 1.3815 | 12.6445 | 7.9641 | 12.0562 | 3.75 | 13.3699 | 0 | 2.7056 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 177.1996 | 2.349%
CZ 6B | 0.22388 | 0.040327 | 0.012241 | 0.074801 | 0.13863 | 0.096813 | 0.028399 | 0.14885 | 0 | 0.020675 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.7728 | 0.09127% | CZ 6B | 7.1861 | 1.2944 | 1.2491 | 7.6328 | 4.4497 | 3.1075 | 0.91154 | 4.7777 | 0 | 0.66363 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 62.9899 | 0.09127% | CZ 6B | 2.1061 | 0.37937 | 0 | 0 | 1.3041 | 0.91075 | 0.26716 | 1.4003 | 0 | 0.1945 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 15.8582 | 0.09127% | CZ 6B | 0 | 0 | 0.012491 | 0.076328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088819 | 0.09127% | CZ 6B | 22.049 | 3.9717 | 1.3652 | 8.3426 | 13.6529 | 9.5347 | 2.7969 | 14.6592 | 0 | 2.0362 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 175.7269 | 0.09127%
CZ 7 | 0.2238 | 0.040439 | 0.013077 | 0.12564 | 0.092522 | 0.10553 | 0.030828 | 0.13736 | 0 | 0.023968 | 0 | 0.11285 | 0.0047593 | 0 | 0.55338 | 0.31716 | 1.7813 | 0.2174% | CZ 7 | 7.1834 | 1.298 | 1.3344 | 12.8209 | 2.9698 | 3.3872 | 0.98952 | 4.4089 | 0 | 0.76933 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 66.879 | 0.2174% | CZ 7 | 2.1053 | 0.38043 | 0 | 0 | 0.87039 | 0.99272 | 0.29001 | 1.2922 | 0 | 0.22548 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 15.4524 | 0.2174% | CZ 7 | 0 | 0 | 0.013344 | 0.12821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14155 | 0.2174% | CZ 7 | 22.0408 | 3.9827 | 1.4585 | 14.0132 | 9.1121 | 10.3928 | 3.0361 | 13.5279 | 0 | 2.3605 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 177.2431 | 0.2174%
CZ 8 | 0.22907 | 0.040946 | 0.014018 | 0.18796 | 0.11538 | 0.066107 | 0.017377 | 0.13663 | 0 | 0.018637 | 0 | 0.11285 | 0.0047635 | 0 | 0.55338 | 0.31716 | 1.8143 | 0% | CZ 8 | 7.3528 | 1.3143 | 1.4304 | 19.18 | 3.7033 | 2.1219 | 0.55778 | 4.3857 | 0 | 0.59822 | 0 | 3.6222 | 0.1529 | 0 | 17.7624 | 10.1802 | 72.362 | 0% | CZ 8 | 2.155 | 0.38519 | 0 | 0 | 1.0854 | 0.62189 | 0.16347 | 1.2854 | 0 | 0.17533 | 0 | 1.0616 | 0.044811 | 0 | 5.2059 | 2.9837 | 15.1675 | 0% | CZ 8 | 0 | 0 | 0.014304 | 0.1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2061 | 0% | CZ 8 | 22.5604 | 4.0326 | 1.5635 | 20.9637 | 11.3629 | 6.5105 | 1.7114 | 13.4565 | 0 | 1.8355 | 0 | 11.1138 | 0.46913 | 0 | 54.5001 | 31.2359 | 181.3159 | 0%
US Weighted | 0.22363 | 0.040368 | 0.010554 | 0.032647 | 0.031008 | 0.21323 | 0.073473 | 0.1343 | 0 | 0.03299 | 0 | 0.11285 | 0.0047592 | 0 | 0.55338 | 0.31716 | 1.7803 | 100% | US Weighted | 7.1781 | 1.2957 | 1.0769 | 3.3313 | 0.9953 | 6.8441 | 2.3583 | 4.3106 | 0 | 1.0589 | 0 | 3.6222 | 0.15276 | 0 | 17.7624 | 10.1802 | 60.1668 | 100% | US Weighted | 2.1038 | 0.37975 | 0 | 0 | 0.2917 | 2.0059 | 0.69119 | 1.2634 | 0 | 0.31035 | 0 | 1.0616 | 0.044772 | 0 | 5.2059 | 2.9837 | 16.3419 | 100% | US Weighted | 0 | 0 | 0.010769 | 0.033313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044083 | 100% | US Weighted | 22.0245 | 3.9756 | 1.1771 | 3.6411 | 3.0539 | 20.9996 | 7.236 | 13.2262 | 0 | 3.2491 | 0 | 11.1138 | 0.46872 | 0 | 54.5001 | 31.2359 | 175.9016 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.30444 | 0.058529 | 0.0078612 | 0.00018555 | 0 | 0.70746 | 0.2592 | 0.16728 | 0 | 0.10736 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.638 | 0% | CZ 0A | 9.772 | 1.8786 | 0.80217 | 0.018934 | 0 | 22.708 | 8.3199 | 5.3693 | 0 | 3.4459 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 85.2358 | 0% | CZ 0A | 2.864 | 0.5506 | 0 | 0 | 0 | 6.6553 | 2.4384 | 1.5737 | 0 | 1.0099 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 24.7405 | 0% | CZ 0A | 0 | 0 | 0.0080217 | 0.00018934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008211 | 0% | CZ 0A | 29.9834 | 5.7642 | 0.87677 | 0.020695 | 0 | 69.6746 | 25.5278 | 16.4746 | 0 | 10.573 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 259.906 | 0%
CZ 0B | 0.30444 | 0.05854 | 0.0078473 | 0.0027118 | 0.0010349 | 0.57685 | 0.20183 | 0.16598 | 0 | 0.09027 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.4352 | 0% | CZ 0B | 9.772 | 1.879 | 0.80074 | 0.27671 | 0.033219 | 18.5157 | 6.4784 | 5.3276 | 0 | 2.8975 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 78.9018 | 0% | CZ 0B | 2.864 | 0.55071 | 0 | 0 | 0.0097358 | 5.4266 | 1.8987 | 1.5614 | 0 | 0.8492 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 22.809 | 0% | CZ 0B | 0 | 0 | 0.0080074 | 0.0027671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010775 | 0% | CZ 0B | 29.9834 | 5.7653 | 0.87521 | 0.30244 | 0.10192 | 56.8115 | 19.8777 | 16.3467 | 0 | 8.8903 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 239.9653 | 0%
CZ 1A | 0.30444 | 0.058547 | 0.0084183 | 0.00076289 | 0 | 0.48464 | 0.20882 | 0.15948 | 0 | 0.10099 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.3518 | 2.832% | CZ 1A | 9.772 | 1.8792 | 0.85901 | 0.077846 | 0 | 15.556 | 6.7028 | 5.1189 | 0 | 3.2416 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 76.1284 | 2.832% | CZ 1A | 2.864 | 0.55077 | 0 | 0 | 0 | 4.5592 | 1.9645 | 1.5003 | 0 | 0.95006 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 22.0374 | 2.832% | CZ 1A | 0 | 0 | 0.0085901 | 0.00077846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0093685 | 2.832% | CZ 1A | 29.9834 | 5.766 | 0.93889 | 0.085086 | 0 | 47.7304 | 20.5662 | 15.7063 | 0 | 9.9462 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 231.7332 | 2.832%
CZ 1B | 0.30444 | 0.058473 | 0.0084514 | 0.00957 | 0.0062841 | 0.49708 | 0.17013 | 0.15964 | 0 | 0.076018 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.3157 | 0% | CZ 1B | 9.772 | 1.8769 | 0.86239 | 0.97653 | 0.20171 | 15.9552 | 5.4608 | 5.1242 | 0 | 2.44 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 75.5906 | 0% | CZ 1B | 2.864 | 0.55008 | 0 | 0 | 0.059117 | 4.6762 | 1.6005 | 1.5018 | 0 | 0.71513 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 21.6154 | 0% | CZ 1B | 0 | 0 | 0.0086239 | 0.0097653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018389 | 0% | CZ 1B | 29.9834 | 5.7587 | 0.94259 | 1.0673 | 0.6189 | 48.9552 | 16.7552 | 15.7225 | 0 | 7.4867 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 228.3013 | 0%
CZ 2A | 0.30444 | 0.058453 | 0.0090727 | 0.010216 | 0.0006155 | 0.44337 | 0.17647 | 0.14666 | 0 | 0.099421 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.2744 | 14.12% | CZ 2A | 9.772 | 1.8762 | 0.92579 | 1.0424 | 0.019756 | 14.2312 | 5.6644 | 4.7075 | 0 | 3.1912 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 74.3515 | 14.12% | CZ 2A | 2.864 | 0.54989 | 0 | 0 | 0.0057902 | 4.1709 | 1.6601 | 1.3797 | 0 | 0.93528 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 21.2143 | 14.12% | CZ 2A | 0 | 0 | 0.0092579 | 0.010424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019682 | 14.12% | CZ 2A | 29.9834 | 5.7568 | 1.0119 | 1.1394 | 0.060618 | 43.6655 | 17.38 | 14.4441 | 0 | 9.7915 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 224.2439 | 14.12%
CZ 2B | 0.30444 | 0.058496 | 0.0091167 | 0.0096983 | 0.0025331 | 0.32891 | 0.11147 | 0.15915 | 0 | 0.05859 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0681 | 1.729% | CZ 2B | 9.772 | 1.8776 | 0.93027 | 0.98962 | 0.081307 | 10.5573 | 3.5779 | 5.1085 | 0 | 1.8806 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 67.6961 | 1.729% | CZ 2B | 2.864 | 0.55029 | 0 | 0 | 0.02383 | 3.0942 | 1.0486 | 1.4972 | 0 | 0.55118 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 19.2779 | 1.729% | CZ 2B | 0 | 0 | 0.0093027 | 0.0098962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019199 | 1.729% | CZ 2B | 29.9834 | 5.761 | 1.0168 | 1.0817 | 0.24947 | 32.3928 | 10.9782 | 15.6744 | 0 | 5.7703 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 203.9188 | 1.729%
CZ 3A | 0.30444 | 0.058484 | 0.010205 | 0.049763 | 0.0022256 | 0.31011 | 0.11774 | 0.14184 | 0 | 0.074578 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.095 | 14.09% | CZ 3A | 9.772 | 1.8772 | 1.0414 | 5.0779 | 0.071438 | 9.954 | 3.7791 | 4.5528 | 0 | 2.3938 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 71.4405 | 14.09% | CZ 3A | 2.864 | 0.55018 | 0 | 0 | 0.020937 | 2.9173 | 1.1076 | 1.3343 | 0 | 0.70158 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 19.1446 | 14.09% | CZ 3A | 0 | 0 | 0.010414 | 0.050779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061192 | 14.09% | CZ 3A | 29.9834 | 5.7599 | 1.1382 | 5.5501 | 0.21919 | 30.5417 | 11.5954 | 13.9693 | 0 | 7.3448 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 207.1127 | 14.09%
CZ 3B | 0.30444 | 0.058482 | 0.0099127 | 0.017816 | 0.045474 | 0.28508 | 0.09847 | 0.15656 | 0 | 0.045756 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0476 | 6.659% | CZ 3B | 9.772 | 1.8771 | 1.0115 | 1.818 | 1.4596 | 9.1506 | 3.1607 | 5.0251 | 0 | 1.4687 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 67.6643 | 6.659% | CZ 3B | 2.864 | 0.55016 | 0 | 0 | 0.42779 | 2.6819 | 0.92634 | 1.4728 | 0 | 0.43044 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 19.002 | 6.659% | CZ 3B | 0 | 0 | 0.010115 | 0.01818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028295 | 6.659% | CZ 3B | 29.9834 | 5.7596 | 1.1056 | 1.9871 | 4.4785 | 28.0767 | 9.6979 | 15.4185 | 0 | 4.5063 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 202.0244 | 6.659%
CZ 3C | 0.30444 | 0.058473 | 0.010334 | 0.007995 | 0.00039809 | 0.2225 | 0.092258 | 0.13732 | 0 | 0.047165 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 1.9065 | 5.951% | CZ 3C | 9.772 | 1.8769 | 1.0544 | 0.81582 | 0.012778 | 7.1417 | 2.9613 | 4.4078 | 0 | 1.5139 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 62.4776 | 5.951% | CZ 3C | 2.864 | 0.55008 | 0 | 0 | 0.003745 | 2.0931 | 0.8679 | 1.2919 | 0 | 0.4437 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.763 | 5.951% | CZ 3C | 0 | 0 | 0.010544 | 0.0081582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018703 | 5.951% | CZ 3C | 29.9834 | 5.7587 | 1.1525 | 0.89169 | 0.039206 | 21.9129 | 9.0861 | 13.5245 | 0 | 4.6451 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 188.0049 | 5.951%
CZ 4A | 0.30444 | 0.058395 | 0.01111 | 0.078584 | 0.0015355 | 0.27456 | 0.08838 | 0.13781 | 0 | 0.072482 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0529 | 29.22% | CZ 4A | 9.772 | 1.8743 | 1.1336 | 8.0188 | 0.049286 | 8.8127 | 2.8368 | 4.4235 | 0 | 2.3265 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 72.1686 | 29.22% | CZ 4A | 2.864 | 0.54934 | 0 | 0 | 0.014445 | 2.5829 | 0.83142 | 1.2965 | 0 | 0.68186 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.469 | 29.22% | CZ 4A | 0 | 0 | 0.011336 | 0.080188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091524 | 29.22% | CZ 4A | 29.9834 | 5.751 | 1.2391 | 8.7645 | 0.15122 | 27.0399 | 8.7041 | 13.5727 | 0 | 7.1384 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 203.3553 | 29.22%
CZ 4B | 0.30444 | 0.058439 | 0.01085 | 0.033021 | 0.070117 | 0.25566 | 0.076998 | 0.17154 | 0 | 0.041345 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0481 | 0.02014% | CZ 4B | 9.772 | 1.8758 | 1.1072 | 3.3695 | 2.2506 | 8.2062 | 2.4715 | 5.5059 | 0 | 1.3271 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 68.8067 | 0.02014% | CZ 4B | 2.864 | 0.54976 | 0 | 0 | 0.65962 | 2.4051 | 0.72435 | 1.6137 | 0 | 0.38895 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.854 | 0.02014% | CZ 4B | 0 | 0 | 0.011072 | 0.033695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044767 | 0.02014% | CZ 4B | 29.9834 | 5.7554 | 1.2101 | 3.6829 | 6.9055 | 25.1789 | 7.5832 | 16.8937 | 0 | 4.0719 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 202.276 | 0.02014%
CZ 4C | 0.30444 | 0.058328 | 0.01138 | 0.052708 | 0.0009117 | 0.17133 | 0.055677 | 0.1383 | 0 | 0.028648 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 1.8474 | 6.185% | CZ 4C | 9.772 | 1.8722 | 1.1612 | 5.3784 | 0.029264 | 5.4992 | 1.7871 | 4.4391 | 0 | 0.91953 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 63.7789 | 6.185% | CZ 4C | 2.864 | 0.54871 | 0 | 0 | 0.0085766 | 1.6117 | 0.52377 | 1.301 | 0 | 0.2695 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 16.7759 | 6.185% | CZ 4C | 0 | 0 | 0.011612 | 0.053784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065396 | 6.185% | CZ 4C | 29.9834 | 5.7444 | 1.2692 | 5.8786 | 0.089789 | 16.873 | 5.4834 | 13.6203 | 0 | 2.8214 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 182.7744 | 6.185%
CZ 5A | 0.30444 | 0.058413 | 0.01188 | 0.12169 | 0.0019336 | 0.20668 | 0.064901 | 0.13968 | 0 | 0.039282 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 1.9746 | 12.51% | CZ 5A | 9.772 | 1.8749 | 1.2123 | 12.4178 | 0.062064 | 6.634 | 2.0832 | 4.4834 | 0 | 1.2609 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 72.7215 | 12.51% | CZ 5A | 2.864 | 0.54951 | 0 | 0 | 0.01819 | 1.9443 | 0.61055 | 1.314 | 0 | 0.36954 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.3187 | 12.51% | CZ 5A | 0 | 0 | 0.012123 | 0.12418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1363 | 12.51% | CZ 5A | 29.9834 | 5.7528 | 1.325 | 13.5727 | 0.19043 | 20.3551 | 6.3918 | 13.7563 | 0 | 3.8687 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 196.2071 | 12.51%
CZ 5B | 0.30444 | 0.058415 | 0.011663 | 0.065376 | 0.078112 | 0.24228 | 0.061202 | 0.17095 | 0 | 0.03685 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0549 | 3.999% | CZ 5B | 9.772 | 1.875 | 1.1901 | 6.671 | 2.5072 | 7.7765 | 1.9644 | 5.4871 | 0 | 1.1828 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 71.3471 | 3.999% | CZ 5B | 2.864 | 0.54953 | 0 | 0 | 0.73483 | 2.2792 | 0.57574 | 1.6082 | 0 | 0.34666 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.6067 | 3.999% | CZ 5B | 0 | 0 | 0.011901 | 0.06671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078611 | 3.999% | CZ 5B | 29.9834 | 5.753 | 1.3008 | 7.2914 | 7.6929 | 23.8607 | 6.0275 | 16.8359 | 0 | 3.6292 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 203.3856 | 3.999%
CZ 5C | 0.30444 | 0.058324 | 0.01182 | 0.049647 | 0.0010083 | 0.15227 | 0.043506 | 0.13708 | 0 | 0.020984 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 1.8047 | 0.02726% | CZ 5C | 9.772 | 1.8721 | 1.2061 | 5.066 | 0.032363 | 4.8876 | 1.3964 | 4.4 | 0 | 0.67354 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 62.2271 | 0.02726% | CZ 5C | 2.864 | 0.54867 | 0 | 0 | 0.009485 | 1.4325 | 0.40927 | 1.2896 | 0 | 0.1974 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 16.3995 | 0.02726% | CZ 5C | 0 | 0 | 0.012061 | 0.05066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062721 | 0.02726% | CZ 5C | 29.9834 | 5.744 | 1.3183 | 5.5372 | 0.099299 | 14.9966 | 4.2847 | 13.5006 | 0 | 2.0666 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 178.5415 | 0.02726%
CZ 6A | 0.30444 | 0.058386 | 0.012459 | 0.1818 | 0.0023506 | 0.21112 | 0.06309 | 0.14512 | 0 | 0.042024 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0464 | 2.349% | CZ 6A | 9.772 | 1.8741 | 1.2714 | 18.5515 | 0.07545 | 6.7765 | 2.0251 | 4.6581 | 0 | 1.3489 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 79.2738 | 2.349% | CZ 6A | 2.864 | 0.54926 | 0 | 0 | 0.022113 | 1.9861 | 0.59351 | 1.3652 | 0 | 0.39533 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.4241 | 2.349% | CZ 6A | 0 | 0 | 0.012714 | 0.18551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19823 | 2.349% | CZ 6A | 29.9834 | 5.7502 | 1.3896 | 20.2768 | 0.2315 | 20.7922 | 6.2135 | 14.2925 | 0 | 4.1388 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 204.0792 | 2.349%
CZ 6B | 0.30444 | 0.058343 | 0.012311 | 0.12177 | 0.053557 | 0.20762 | 0.051498 | 0.1578 | 0 | 0.030067 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0231 | 0.09127% | CZ 6B | 9.772 | 1.8727 | 1.2562 | 12.4252 | 1.7191 | 6.6643 | 1.653 | 5.0652 | 0 | 0.96509 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 74.3136 | 0.09127% | CZ 6B | 2.864 | 0.54886 | 0 | 0 | 0.50383 | 1.9532 | 0.48446 | 1.4845 | 0 | 0.28285 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.7703 | 0.09127% | CZ 6B | 0 | 0 | 0.012562 | 0.12425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13681 | 0.09127% | CZ 6B | 29.9834 | 5.746 | 1.3731 | 13.5807 | 5.2746 | 20.448 | 5.0718 | 15.5414 | 0 | 2.9612 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 200.9909 | 0.09127%
CZ 7 | 0.30444 | 0.058308 | 0.013152 | 0.19706 | 0.002882 | 0.19726 | 0.051806 | 0.14649 | 0 | 0.036082 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0331 | 0.2174% | CZ 7 | 9.772 | 1.8716 | 1.342 | 20.1081 | 0.092506 | 6.3316 | 1.6629 | 4.7019 | 0 | 1.1581 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 79.9616 | 0.2174% | CZ 7 | 2.864 | 0.54852 | 0 | 0 | 0.027112 | 1.8557 | 0.48736 | 1.378 | 0 | 0.33943 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.1487 | 0.2174% | CZ 7 | 0 | 0 | 0.01342 | 0.20108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2145 | 0.2174% | CZ 7 | 29.9834 | 5.7425 | 1.4668 | 21.9782 | 0.28384 | 19.4271 | 5.1022 | 14.4267 | 0 | 3.5535 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 202.9751 | 0.2174%
CZ 8 | 0.30444 | 0.057987 | 0.014082 | 0.27735 | 0.017421 | 0.17082 | 0.034293 | 0.14505 | 0 | 0.026844 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0739 | 0% | CZ 8 | 9.772 | 1.8612 | 1.4369 | 28.3006 | 0.55916 | 5.4831 | 1.1007 | 4.6557 | 0 | 0.86165 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 86.952 | 0% | CZ 8 | 2.864 | 0.5455 | 0 | 0 | 0.16388 | 1.607 | 0.3226 | 1.3645 | 0 | 0.25253 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 16.7686 | 0% | CZ 8 | 0 | 0 | 0.014369 | 0.28301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29738 | 0% | CZ 8 | 29.9834 | 5.7108 | 1.5705 | 30.9326 | 1.7157 | 16.8236 | 3.3773 | 14.2851 | 0 | 2.6438 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 208.0537 | 0%
US Weighted | 0.30444 | 0.058431 | 0.010631 | 0.059194 | 0.0074914 | 0.28998 | 0.1029 | 0.14364 | 0 | 0.06472 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0671 | 100% | US Weighted | 9.772 | 1.8755 | 1.0848 | 6.0402 | 0.24046 | 9.3077 | 3.3029 | 4.6104 | 0 | 2.0774 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 71.2322 | 100% | US Weighted | 2.864 | 0.54968 | 0 | 0 | 0.070474 | 2.7279 | 0.96804 | 1.3512 | 0 | 0.60884 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.7888 | 100% | US Weighted | 0 | 0 | 0.010848 | 0.060402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071249 | 100% | US Weighted | 29.9834 | 5.7546 | 1.1856 | 6.6019 | 0.73779 | 28.5587 | 10.1344 | 14.146 | 0 | 6.374 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 204.4872 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 498588 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.30444 | 0.058529 | 0.0078616 | 0.00018406 | 0 | 0.75761 | 0.27035 | 0.16943 | 0 | 0.11535 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.7094 | 0% | CZ 0A | 9.772 | 1.8786 | 0.8022 | 0.018782 | 0 | 24.3178 | 8.6777 | 5.4382 | 0 | 3.7026 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 87.5289 | 0% | CZ 0A | 2.864 | 0.5506 | 0 | 0 | 0 | 7.1271 | 2.5433 | 1.5939 | 0 | 1.0852 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 25.4126 | 0% | CZ 0A | 0 | 0 | 0.008022 | 0.00018782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082099 | 0% | CZ 0A | 29.9834 | 5.7642 | 0.87681 | 0.020529 | 0 | 74.6139 | 26.6257 | 16.6861 | 0 | 11.3608 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 266.9423 | 0%
CZ 0B | 0.30444 | 0.05854 | 0.0078463 | 0.002804 | 0.0011344 | 0.60605 | 0.20722 | 0.16869 | 0 | 0.095781 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.4782 | 0% | CZ 0B | 9.772 | 1.879 | 0.80065 | 0.28612 | 0.036413 | 19.4528 | 6.6514 | 5.4145 | 0 | 3.0744 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 80.2883 | 0% | CZ 0B | 2.864 | 0.55071 | 0 | 0 | 0.010672 | 5.7013 | 1.9494 | 1.5869 | 0 | 0.90104 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 23.2126 | 0% | CZ 0B | 0 | 0 | 0.0080065 | 0.0028612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010868 | 0% | CZ 0B | 29.9834 | 5.7653 | 0.87511 | 0.31273 | 0.11173 | 59.6869 | 20.4085 | 16.6133 | 0 | 9.433 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 244.2009 | 0%
CZ 1A | 0.30444 | 0.058547 | 0.0084183 | 0.00074724 | 0 | 0.51079 | 0.2144 | 0.16821 | 0 | 0.10767 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.3989 | 2.832% | CZ 1A | 9.772 | 1.8792 | 0.85901 | 0.076249 | 0 | 16.3953 | 6.8817 | 5.3991 | 0 | 3.4559 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 77.6395 | 2.832% | CZ 1A | 2.864 | 0.55077 | 0 | 0 | 0 | 4.8052 | 2.0169 | 1.5824 | 0 | 1.0129 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 22.4807 | 2.832% | CZ 1A | 0 | 0 | 0.0085901 | 0.00076249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0093526 | 2.832% | CZ 1A | 29.9834 | 5.766 | 0.93889 | 0.08334 | 0 | 50.3055 | 21.1151 | 16.5661 | 0 | 10.6038 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 236.373 | 2.832%
CZ 1B | 0.30444 | 0.058473 | 0.0084512 | 0.01035 | 0.0065454 | 0.51842 | 0.17391 | 0.16226 | 0 | 0.0797 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.3482 | 0% | CZ 1B | 9.772 | 1.8769 | 0.86237 | 1.0561 | 0.21009 | 16.6401 | 5.5823 | 5.2081 | 0 | 2.5582 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 76.687 | 0% | CZ 1B | 2.864 | 0.55008 | 0 | 0 | 0.061575 | 4.8769 | 1.6361 | 1.5264 | 0 | 0.74977 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 21.9134 | 0% | CZ 1B | 0 | 0 | 0.0086237 | 0.010561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019185 | 0% | CZ 1B | 29.9834 | 5.7587 | 0.94257 | 1.1543 | 0.64463 | 51.0566 | 17.128 | 15.9799 | 0 | 7.8493 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 231.5084 | 0%
CZ 2A | 0.30444 | 0.058453 | 0.0090727 | 0.020178 | 0.00073102 | 0.47782 | 0.18376 | 0.15444 | 0 | 0.087814 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.3223 | 14.12% | CZ 2A | 9.772 | 1.8762 | 0.92579 | 2.059 | 0.023464 | 15.3369 | 5.8982 | 4.9571 | 0 | 2.8186 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 76.5883 | 14.12% | CZ 2A | 2.864 | 0.54989 | 0 | 0 | 0.0068769 | 4.495 | 1.7287 | 1.4529 | 0 | 0.82609 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 21.5719 | 14.12% | CZ 2A | 0 | 0 | 0.0092579 | 0.02059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029848 | 14.12% | CZ 2A | 29.9834 | 5.7568 | 1.0119 | 2.2505 | 0.071995 | 47.058 | 18.0974 | 15.2099 | 0 | 8.6484 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 229.0991 | 14.12%
CZ 2B | 0.30444 | 0.058496 | 0.0091167 | 0.023262 | 0.0029762 | 0.34717 | 0.11564 | 0.16633 | 0 | 0.064931 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.118 | 1.729% | CZ 2B | 9.772 | 1.8776 | 0.93027 | 2.3736 | 0.09553 | 11.1435 | 3.7118 | 5.3389 | 0 | 2.0842 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 70.2483 | 1.729% | CZ 2B | 2.864 | 0.55029 | 0 | 0 | 0.027998 | 3.266 | 1.0879 | 1.5648 | 0 | 0.61083 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 19.6203 | 1.729% | CZ 2B | 0 | 0 | 0.0093027 | 0.023736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033039 | 1.729% | CZ 2B | 29.9834 | 5.761 | 1.0168 | 2.5944 | 0.29311 | 34.1914 | 11.3887 | 16.3814 | 0 | 6.3948 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 209.0159 | 1.729%
CZ 3A | 0.30444 | 0.058484 | 0.010206 | 0.05953 | 0.0026113 | 0.31784 | 0.12062 | 0.1489 | 0 | 0.077263 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.1255 | 14.09% | CZ 3A | 9.772 | 1.8772 | 1.0415 | 6.0745 | 0.083817 | 10.2021 | 3.8717 | 4.7793 | 0 | 2.48 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 73.103 | 14.09% | CZ 3A | 2.864 | 0.55018 | 0 | 0 | 0.024565 | 2.9901 | 1.1347 | 1.4007 | 0 | 0.72684 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 19.3397 | 14.09% | CZ 3A | 0 | 0 | 0.010415 | 0.060745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071159 | 14.09% | CZ 3A | 29.9834 | 5.7599 | 1.1383 | 6.6394 | 0.25717 | 31.303 | 11.8796 | 14.6642 | 0 | 7.6093 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 210.245 | 14.09%
CZ 3B | 0.30444 | 0.058482 | 0.0099127 | 0.021461 | 0.045968 | 0.28804 | 0.099233 | 0.15806 | 0 | 0.047204 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0584 | 6.659% | CZ 3B | 9.772 | 1.8771 | 1.0115 | 2.1899 | 1.4755 | 9.2454 | 3.1852 | 5.0735 | 0 | 1.5151 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 68.2661 | 6.659% | CZ 3B | 2.864 | 0.55016 | 0 | 0 | 0.43243 | 2.7097 | 0.93352 | 1.487 | 0 | 0.44406 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 19.0694 | 6.659% | CZ 3B | 0 | 0 | 0.010115 | 0.021899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032014 | 6.659% | CZ 3B | 29.9834 | 5.7596 | 1.1056 | 2.3936 | 4.5271 | 28.3674 | 9.7731 | 15.567 | 0 | 4.6489 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 203.1365 | 6.659%
CZ 3C | 0.30444 | 0.058473 | 0.010333 | 0.02004 | 0.00047629 | 0.23332 | 0.094696 | 0.14758 | 0 | 0.050177 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 1.9452 | 5.951% | CZ 3C | 9.772 | 1.8769 | 1.0544 | 2.0449 | 0.015288 | 7.4892 | 3.0395 | 4.737 | 0 | 1.6106 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 64.5607 | 5.951% | CZ 3C | 2.864 | 0.55008 | 0 | 0 | 0.0044806 | 2.195 | 0.89084 | 1.3883 | 0 | 0.47203 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.0133 | 5.951% | CZ 3C | 0 | 0 | 0.010544 | 0.020449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030993 | 5.951% | CZ 3C | 29.9834 | 5.7587 | 1.1525 | 2.2351 | 0.046907 | 22.979 | 9.3262 | 14.5345 | 0 | 4.9417 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 191.9688 | 5.951%
CZ 4A | 0.30444 | 0.058395 | 0.011109 | 0.10477 | 0.001811 | 0.27567 | 0.089273 | 0.1406 | 0 | 0.073074 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0848 | 29.22% | CZ 4A | 9.772 | 1.8743 | 1.1336 | 10.6903 | 0.058128 | 8.8483 | 2.8655 | 4.5131 | 0 | 2.3455 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 75.0217 | 29.22% | CZ 4A | 2.864 | 0.54934 | 0 | 0 | 0.017036 | 2.5933 | 0.83982 | 1.3227 | 0 | 0.68744 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.5222 | 29.22% | CZ 4A | 0 | 0 | 0.011336 | 0.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11824 | 29.22% | CZ 4A | 29.9834 | 5.751 | 1.239 | 11.6845 | 0.17835 | 27.149 | 8.7921 | 13.8474 | 0 | 7.1968 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 206.8325 | 29.22%
CZ 4B | 0.30444 | 0.058439 | 0.010849 | 0.049131 | 0.070828 | 0.25659 | 0.077187 | 0.17315 | 0 | 0.042107 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0684 | 0.02014% | CZ 4B | 9.772 | 1.8758 | 1.1071 | 5.0133 | 2.2734 | 8.2359 | 2.4776 | 5.5579 | 0 | 1.3515 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 70.5854 | 0.02014% | CZ 4B | 2.864 | 0.54976 | 0 | 0 | 0.6663 | 2.4138 | 0.72613 | 1.6289 | 0 | 0.39611 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.8936 | 0.02014% | CZ 4B | 0 | 0 | 0.011071 | 0.050133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061204 | 0.02014% | CZ 4B | 29.9834 | 5.7554 | 1.21 | 5.4796 | 6.9755 | 25.2702 | 7.6018 | 17.0532 | 0 | 4.1469 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 204.4869 | 0.02014%
CZ 4C | 0.30444 | 0.058328 | 0.01138 | 0.072079 | 0.0010847 | 0.1706 | 0.055463 | 0.1455 | 0 | 0.029267 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 1.8738 | 6.185% | CZ 4C | 9.772 | 1.8722 | 1.1612 | 7.355 | 0.034816 | 5.4758 | 1.7802 | 4.6703 | 0 | 0.93942 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 65.982 | 6.185% | CZ 4C | 2.864 | 0.54871 | 0 | 0 | 0.010204 | 1.6049 | 0.52176 | 1.3688 | 0 | 0.27533 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 16.8423 | 6.185% | CZ 4C | 0 | 0 | 0.011612 | 0.07355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085162 | 6.185% | CZ 4C | 29.9834 | 5.7444 | 1.2692 | 8.039 | 0.10682 | 16.8014 | 5.4623 | 14.3299 | 0 | 2.8824 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 185.6297 | 6.185%
CZ 5A | 0.30444 | 0.058413 | 0.011881 | 0.15987 | 0.0022766 | 0.20523 | 0.064688 | 0.1414 | 0 | 0.040618 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0145 | 12.51% | CZ 5A | 9.772 | 1.8749 | 1.2124 | 16.3135 | 0.073073 | 6.5876 | 2.0764 | 4.5388 | 0 | 1.3037 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 76.6732 | 12.51% | CZ 5A | 2.864 | 0.54951 | 0 | 0 | 0.021417 | 1.9307 | 0.60855 | 1.3302 | 0 | 0.3821 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.3351 | 12.51% | CZ 5A | 0 | 0 | 0.012124 | 0.16313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17526 | 12.51% | CZ 5A | 29.9834 | 5.7528 | 1.3251 | 17.8306 | 0.22421 | 20.2125 | 6.3709 | 13.9263 | 0 | 4.0002 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 200.6369 | 12.51%
CZ 5B | 0.30444 | 0.058415 | 0.011662 | 0.096547 | 0.078514 | 0.23962 | 0.060805 | 0.17108 | 0 | 0.037032 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0838 | 3.999% | CZ 5B | 9.772 | 1.875 | 1.19 | 9.8517 | 2.5201 | 7.6914 | 1.9517 | 5.4912 | 0 | 1.1887 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 74.4528 | 3.999% | CZ 5B | 2.864 | 0.54953 | 0 | 0 | 0.73861 | 2.2542 | 0.57201 | 1.6094 | 0 | 0.34838 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.5847 | 3.999% | CZ 5B | 0 | 0 | 0.0119 | 0.098517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11042 | 3.999% | CZ 5B | 29.9834 | 5.753 | 1.3007 | 10.7679 | 7.7325 | 23.5996 | 5.9884 | 16.8486 | 0 | 3.6472 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 206.6321 | 3.999%
CZ 5C | 0.30444 | 0.058324 | 0.01182 | 0.073548 | 0.0011635 | 0.15043 | 0.042894 | 0.14236 | 0 | 0.02132 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 1.8319 | 0.02726% | CZ 5C | 9.772 | 1.8721 | 1.2061 | 7.5049 | 0.037345 | 4.8285 | 1.3768 | 4.5693 | 0 | 0.68432 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 64.7723 | 0.02726% | CZ 5C | 2.864 | 0.54867 | 0 | 0 | 0.010945 | 1.4151 | 0.40351 | 1.3392 | 0 | 0.20056 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 16.4306 | 0.02726% | CZ 5C | 0 | 0 | 0.012061 | 0.075049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08711 | 0.02726% | CZ 5C | 29.9834 | 5.744 | 1.3183 | 8.2029 | 0.11458 | 14.8152 | 4.2244 | 14.0199 | 0 | 2.0997 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 181.5332 | 0.02726%
CZ 6A | 0.30444 | 0.058386 | 0.01246 | 0.22951 | 0.002776 | 0.21028 | 0.063159 | 0.14714 | 0 | 0.043974 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0978 | 2.349% | CZ 6A | 9.772 | 1.8741 | 1.2714 | 23.4197 | 0.089103 | 6.7495 | 2.0273 | 4.723 | 0 | 1.4115 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 84.2585 | 2.349% | CZ 6A | 2.864 | 0.54926 | 0 | 0 | 0.026114 | 1.9782 | 0.59416 | 1.3842 | 0 | 0.41367 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.4582 | 2.349% | CZ 6A | 0 | 0 | 0.012714 | 0.2342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24691 | 2.349% | CZ 6A | 29.9834 | 5.7502 | 1.3897 | 25.5978 | 0.27339 | 20.7096 | 6.2202 | 14.4914 | 0 | 4.3308 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 209.7572 | 2.349%
CZ 6B | 0.30444 | 0.058343 | 0.012312 | 0.16138 | 0.05406 | 0.20447 | 0.051028 | 0.15914 | 0 | 0.030631 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.0614 | 0.09127% | CZ 6B | 9.772 | 1.8727 | 1.2563 | 16.4673 | 1.7352 | 6.563 | 1.6379 | 5.1081 | 0 | 0.98319 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 78.3166 | 0.09127% | CZ 6B | 2.864 | 0.54886 | 0 | 0 | 0.50856 | 1.9235 | 0.48004 | 1.4971 | 0 | 0.28816 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.7588 | 0.09127% | CZ 6B | 0 | 0 | 0.012563 | 0.16467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17724 | 0.09127% | CZ 6B | 29.9834 | 5.746 | 1.3731 | 17.9988 | 5.3241 | 20.1371 | 5.0256 | 15.673 | 0 | 3.0167 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 205.2886 | 0.09127%
CZ 7 | 0.30444 | 0.058308 | 0.013154 | 0.26038 | 0.0034075 | 0.19866 | 0.052123 | 0.15403 | 0 | 0.038275 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.1084 | 0.2174% | CZ 7 | 9.772 | 1.8716 | 1.3422 | 26.5689 | 0.10937 | 6.3765 | 1.673 | 4.9439 | 0 | 1.2285 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 86.807 | 0.2174% | CZ 7 | 2.864 | 0.54852 | 0 | 0 | 0.032055 | 1.8689 | 0.49034 | 1.449 | 0 | 0.36006 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 17.2614 | 0.2174% | CZ 7 | 0 | 0 | 0.013422 | 0.26569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27911 | 0.2174% | CZ 7 | 29.9834 | 5.7425 | 1.4671 | 29.0399 | 0.33559 | 19.5651 | 5.1334 | 15.1693 | 0 | 3.7695 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 211.2164 | 0.2174%
CZ 8 | 0.30444 | 0.057987 | 0.014083 | 0.3343 | 0.018182 | 0.16901 | 0.034054 | 0.14952 | 0 | 0.027824 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.1351 | 0% | CZ 8 | 9.772 | 1.8612 | 1.437 | 34.1127 | 0.58362 | 5.4249 | 1.0931 | 4.7992 | 0 | 0.89308 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 92.8978 | 0% | CZ 8 | 2.864 | 0.5455 | 0 | 0 | 0.17105 | 1.5899 | 0.32036 | 1.4066 | 0 | 0.26175 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 16.8078 | 0% | CZ 8 | 0 | 0 | 0.01437 | 0.34113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3555 | 0% | CZ 8 | 29.9834 | 5.7108 | 1.5707 | 37.2852 | 1.7907 | 16.6451 | 3.3539 | 14.7254 | 0 | 2.7402 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 214.8163 | 0%
US Weighted | 0.30444 | 0.058431 | 0.010631 | 0.079344 | 0.0077692 | 0.2978 | 0.10497 | 0.14836 | 0 | 0.064471 | 0 | 0.11589 | 0.0085204 | 0 | 0.55338 | 0.34785 | 2.1019 | 100% | US Weighted | 9.772 | 1.8755 | 1.0848 | 8.0963 | 0.24937 | 9.5588 | 3.3693 | 4.762 | 0 | 2.0694 | 0 | 3.7199 | 0.27349 | 0 | 17.7624 | 11.1651 | 73.7584 | 100% | US Weighted | 2.864 | 0.54968 | 0 | 0 | 0.073087 | 2.8015 | 0.9875 | 1.3957 | 0 | 0.6065 | 0 | 1.0902 | 0.080155 | 0 | 5.2059 | 3.2723 | 18.9265 | 100% | US Weighted | 0 | 0 | 0.010848 | 0.080963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091811 | 100% | US Weighted | 29.9834 | 5.7546 | 1.1857 | 8.8493 | 0.76515 | 29.3291 | 10.3381 | 14.6112 | 0 | 6.3494 | 0 | 11.4138 | 0.83914 | 0 | 54.5001 | 34.2578 | 208.1767 | 100%
Building Type: | Large Office |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Large Office |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 498588 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 498588 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 498588 | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.15192 | 0.038635 | 0.00037036 | -9.2777e-05 | 0 | 0.31971 | 0.12488 | 0.030984 | -0.0063066 | 0.068696 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.76917 | 0% | CZ 0A | 4.8763 | 1.2401 | 0.037792 | -0.009467 | 0 | 10.2619 | 4.0085 | 0.9945 | -0.20243 | 2.205 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 24.7081 | 0% | CZ 0A | 1.4292 | 0.36346 | 0 | 0 | 0 | 3.0076 | 1.1748 | 0.29147 | -0.059329 | 0.64625 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 7.2332 | 0% | CZ 0A | 0 | 0 | 0.00037792 | -9.467e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00028325 | 0% | CZ 0A | 14.962 | 3.805 | 0.041307 | -0.010347 | 0 | 31.4865 | 12.2991 | 3.0514 | -0.62111 | 6.7656 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 75.7555 | 0%
CZ 0B | 0.15183 | 0.038312 | 0.00037502 | 0.0024647 | 4.7984e-05 | 0.1478 | 0.081417 | 0.032895 | 0 | 0.048377 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.54389 | 0% | CZ 0B | 4.8733 | 1.2297 | 0.038267 | 0.2515 | 0.0015402 | 4.7441 | 2.6133 | 1.0559 | 0 | 1.5528 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 17.6564 | 0% | CZ 0B | 1.4283 | 0.36041 | 0 | 0 | 0.0004514 | 1.3904 | 0.76591 | 0.30946 | 0 | 0.4551 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 5.0899 | 0% | CZ 0B | 0 | 0 | 0.00038267 | 0.002515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028977 | 0% | CZ 0B | 14.9528 | 3.7732 | 0.041826 | 0.27489 | 0.0047257 | 14.5563 | 8.0183 | 3.2397 | 0 | 4.7645 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 53.6024 | 0%
CZ 1A | 0.15164 | 0.038227 | 0.00036049 | 0.00035676 | 0 | 0.16183 | 0.091214 | 0.036752 | -0.0057628 | 0.070492 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.58548 | 2.832% | CZ 1A | 4.8674 | 1.227 | 0.036784 | 0.036404 | 0 | 5.1943 | 2.9278 | 1.1796 | -0.18497 | 2.2626 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 18.8429 | 2.832% | CZ 1A | 1.4266 | 0.35962 | 0 | 0 | 0 | 1.5224 | 0.85808 | 0.34574 | -0.054213 | 0.66314 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 5.5011 | 2.832% | CZ 1A | 0 | 0 | 0.00036784 | 0.00036404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00073189 | 2.832% | CZ 1A | 14.9346 | 3.7648 | 0.040205 | 0.03979 | 0 | 15.9377 | 8.9833 | 3.6195 | -0.56755 | 6.9424 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 57.6709 | 2.832%
CZ 1B | 0.1516 | 0.038226 | 0.00037241 | 0.008718 | 0.00021445 | 0.12244 | 0.063835 | 0.029112 | 0 | 0.038558 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.49345 | 0% | CZ 1B | 4.8662 | 1.227 | 0.038001 | 0.88959 | 0.0068833 | 3.93 | 2.049 | 0.93444 | 0 | 1.2376 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 16.4745 | 0% | CZ 1B | 1.4262 | 0.35961 | 0 | 0 | 0.0020174 | 1.1518 | 0.60052 | 0.27387 | 0 | 0.36273 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 4.5565 | 0% | CZ 1B | 0 | 0 | 0.00038001 | 0.0088959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092759 | 0% | CZ 1B | 14.9309 | 3.7647 | 0.041535 | 0.97233 | 0.02112 | 12.0583 | 6.2868 | 2.8671 | 0 | 3.7974 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 48.7163 | 0%
CZ 2A | 0.1518 | 0.038138 | 0.00036235 | 0.018686 | -0.015673 | 0.20558 | 0.085341 | 0.03161 | -0.0029774 | 0.055326 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.60857 | 14.12% | CZ 2A | 4.8724 | 1.2241 | 0.036975 | 1.9067 | -0.50307 | 6.5988 | 2.7392 | 1.0146 | -0.095568 | 1.7759 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 20.866 | 14.12% | CZ 2A | 1.428 | 0.35878 | 0 | 0 | -0.14744 | 1.934 | 0.80283 | 0.29736 | -0.028009 | 0.52047 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 5.5458 | 14.12% | CZ 2A | 0 | 0 | 0.00036975 | 0.019067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019437 | 14.12% | CZ 2A | 14.9501 | 3.756 | 0.040413 | 2.0841 | -1.5436 | 20.2469 | 8.4048 | 3.1131 | -0.29323 | 5.4488 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 60.1836 | 14.12%
CZ 2B | 0.15172 | 0.038168 | 0.00036663 | 0.021537 | -0.076085 | 0.1093 | 0.042835 | 0.028783 | 0 | 0.03769 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.3947 | 1.729% | CZ 2B | 4.87 | 1.2251 | 0.037412 | 2.1976 | -2.4422 | 3.5084 | 1.3749 | 0.92388 | 0 | 1.2098 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 14.2009 | 1.729% | CZ 2B | 1.4273 | 0.35906 | 0 | 0 | -0.71576 | 1.0283 | 0.40296 | 0.27077 | 0 | 0.35456 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.507 | 1.729% | CZ 2B | 0 | 0 | 0.00037412 | 0.021976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02235 | 1.729% | CZ 2B | 14.9425 | 3.759 | 0.040891 | 2.402 | -7.4933 | 10.7649 | 4.2186 | 2.8347 | 0 | 3.7119 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 39.1575 | 1.729%
CZ 3A | 0.15147 | 0.038003 | 0.00035862 | 0.052912 | -0.044001 | 0.13305 | 0.055208 | 0.027583 | -0.0024205 | 0.053764 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.5063 | 14.09% | CZ 3A | 4.8618 | 1.2198 | 0.036594 | 5.3992 | -1.4124 | 4.2705 | 1.7721 | 0.88536 | -0.077694 | 1.7257 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 19.9769 | 14.09% | CZ 3A | 1.4249 | 0.35751 | 0 | 0 | -0.41394 | 1.2516 | 0.51936 | 0.25948 | -0.022771 | 0.50577 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 4.2618 | 14.09% | CZ 3A | 0 | 0 | 0.00036594 | 0.053992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054357 | 14.09% | CZ 3A | 14.9174 | 3.7428 | 0.039998 | 5.9013 | -4.3335 | 13.1032 | 5.4372 | 2.7165 | -0.23839 | 5.2949 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 50.5576 | 14.09%
CZ 3B | 0.15165 | 0.038323 | 0.00035508 | 0.01489 | -0.039387 | 0.08096 | 0.034598 | 0.01076 | 0 | 0.02234 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.35486 | 6.659% | CZ 3B | 4.8675 | 1.2301 | 0.036233 | 1.5194 | -1.2642 | 2.5986 | 1.1105 | 0.34538 | 0 | 0.71706 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 12.4565 | 6.659% | CZ 3B | 1.4266 | 0.36052 | 0 | 0 | -0.37053 | 0.76162 | 0.32548 | 0.10123 | 0 | 0.21016 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.1949 | 6.659% | CZ 3B | 0 | 0 | 0.00036233 | 0.015194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015556 | 6.659% | CZ 3B | 14.9349 | 3.7743 | 0.039603 | 1.6607 | -3.8791 | 7.9734 | 3.4074 | 1.0597 | 0 | 2.2001 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 35.1472 | 6.659%
CZ 3C | 0.15144 | 0.03834 | 0.00035807 | 0.019052 | -0.022377 | 0.1001 | 0.043584 | 0.029023 | 0 | 0.030674 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.43057 | 5.951% | CZ 3C | 4.861 | 1.2306 | 0.036537 | 1.9441 | -0.71826 | 3.2131 | 1.3989 | 0.93157 | 0 | 0.98456 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 15.1781 | 5.951% | CZ 3C | 1.4247 | 0.36068 | 0 | 0 | -0.21051 | 0.9417 | 0.41001 | 0.27303 | 0 | 0.28856 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.868 | 5.951% | CZ 3C | 0 | 0 | 0.00036537 | 0.019441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019807 | 5.951% | CZ 3C | 14.9151 | 3.7759 | 0.039935 | 2.1249 | -2.2038 | 9.8587 | 4.2924 | 2.8583 | 0 | 3.0209 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 42.6584 | 5.951%
CZ 4A | 0.15134 | 0.038017 | 0.00035359 | 0.091438 | -0.0693 | 0.13997 | 0.043759 | 0.023513 | -0.0026261 | 0.054278 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.51111 | 29.22% | CZ 4A | 4.8576 | 1.2203 | 0.036081 | 9.3304 | -2.2244 | 4.4928 | 1.4046 | 0.75473 | -0.084292 | 1.7422 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 22.8258 | 29.22% | CZ 4A | 1.4237 | 0.35764 | 0 | 0 | -0.65193 | 1.3168 | 0.41166 | 0.2212 | -0.024705 | 0.51061 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.9447 | 29.22% | CZ 4A | 0 | 0 | 0.00036081 | 0.093304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093665 | 29.22% | CZ 4A | 14.9044 | 3.7441 | 0.039437 | 10.1981 | -6.825 | 13.7853 | 4.3096 | 2.3157 | -0.25863 | 5.3456 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 51.5348 | 29.22%
CZ 4B | 0.15182 | 0.038233 | 0.00035099 | 0.034787 | -0.049859 | 0.10429 | 0.032827 | 0.023984 | 0 | 0.022792 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.3996 | 0.02014% | CZ 4B | 4.8731 | 1.2272 | 0.035815 | 3.5496 | -1.6004 | 3.3476 | 1.0537 | 0.76983 | 0 | 0.73157 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 15.2839 | 0.02014% | CZ 4B | 1.4282 | 0.35967 | 0 | 0 | -0.46904 | 0.98112 | 0.30882 | 0.22562 | 0 | 0.21441 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.4286 | 0.02014% | CZ 4B | 0 | 0 | 0.00035815 | 0.035496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035855 | 0.02014% | CZ 4B | 14.952 | 3.7654 | 0.039146 | 3.8798 | -4.9104 | 10.2713 | 3.233 | 2.362 | 0 | 2.2447 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 39.8131 | 0.02014%
CZ 4C | 0.15091 | 0.037668 | 0.00034596 | 0.051684 | -0.049524 | 0.094977 | 0.031079 | 0.02822 | 0 | 0.016644 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.40238 | 6.185% | CZ 4C | 4.8439 | 1.2091 | 0.035302 | 5.2739 | -1.5896 | 3.0485 | 0.99758 | 0.9058 | 0 | 0.53424 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 16.5546 | 6.185% | CZ 4C | 1.4197 | 0.35436 | 0 | 0 | -0.46589 | 0.89348 | 0.29238 | 0.26547 | 0 | 0.15658 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.2958 | 6.185% | CZ 4C | 0 | 0 | 0.00035302 | 0.052739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053092 | 6.185% | CZ 4C | 14.8624 | 3.7098 | 0.038585 | 5.7643 | -4.8774 | 9.3538 | 3.0609 | 2.7793 | 0 | 1.6392 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 40.307 | 6.185%
CZ 5A | 0.15149 | 0.037935 | 0.0003521 | 0.13698 | -0.048321 | 0.080077 | 0.02803 | 0.022054 | -0.0021628 | 0.02458 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.4714 | 12.51% | CZ 5A | 4.8627 | 1.2176 | 0.035929 | 13.9781 | -1.551 | 2.5703 | 0.8997 | 0.70788 | -0.069422 | 0.78897 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 24.7366 | 12.51% | CZ 5A | 1.4252 | 0.35687 | 0 | 0 | -0.45457 | 0.75331 | 0.26369 | 0.20747 | -0.020347 | 0.23124 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.1426 | 12.51% | CZ 5A | 0 | 0 | 0.00035929 | 0.13978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14014 | 12.51% | CZ 5A | 14.92 | 3.7361 | 0.03927 | 15.278 | -4.7589 | 7.8864 | 2.7605 | 2.172 | -0.21301 | 2.4208 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 48.2173 | 12.51%
CZ 5B | 0.15153 | 0.03807 | 0.00035117 | 0.063871 | -0.059085 | 0.1238 | 0.027559 | 0.023836 | 0 | 0.020008 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.43031 | 3.999% | CZ 5B | 4.8637 | 1.222 | 0.035834 | 6.5175 | -1.8965 | 3.9736 | 0.8846 | 0.76507 | 0 | 0.6422 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 18.3039 | 3.999% | CZ 5B | 1.4255 | 0.35813 | 0 | 0 | -0.55583 | 1.1646 | 0.25926 | 0.22423 | 0 | 0.18822 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.4439 | 3.999% | CZ 5B | 0 | 0 | 0.00035834 | 0.065175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065533 | 3.999% | CZ 5B | 14.9233 | 3.7493 | 0.039166 | 7.1236 | -5.819 | 12.1923 | 2.7142 | 2.3475 | 0 | 1.9705 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 43.2169 | 3.999%
CZ 5C | 0.15081 | 0.037635 | 0.00034558 | 0.050992 | -0.056439 | 0.091701 | 0.025821 | 0.023606 | 0 | 0.011105 | 0 | 0.0032842 | 0.0052777 | 0 | 0 | 0.03181 | 0.37595 | 0.02726% | CZ 5C | 4.8406 | 1.208 | 0.035264 | 5.2033 | -1.8116 | 2.9434 | 0.82881 | 0.75771 | 0 | 0.35645 | 0 | 0.10542 | 0.1694 | 0 | 0 | 1.021 | 15.6578 | 0.02726% | CZ 5C | 1.4187 | 0.35404 | 0 | 0 | -0.53094 | 0.86266 | 0.24291 | 0.22207 | 0 | 0.10447 | 0 | 0.030896 | 0.049649 | 0 | 0 | 0.29925 | 3.0537 | 0.02726% | CZ 5C | 0 | 0 | 0.00035264 | 0.052033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052385 | 0.02726% | CZ 5C | 14.8523 | 3.7065 | 0.038543 | 5.6872 | -5.5584 | 9.0312 | 2.543 | 2.3249 | 0 | 1.0937 | 0 | 0.32345 | 0.51977 | 0 | 0 | 3.1329 | 37.6951 | 0.02726%
CZ 6A | 0.15138 | 0.037884 | 0.00034875 | 0.1848 | -0.067602 | 0.091051 | 0.028605 | 0.023885 | -0.0024111 | 0.027298 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.51561 | 2.349% | CZ 6A | 4.8591 | 1.216 | 0.035587 | 18.8567 | -2.1699 | 2.9225 | 0.91816 | 0.76667 | -0.07739 | 0.87621 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 29.4996 | 2.349% | CZ 6A | 1.4241 | 0.35639 | 0 | 0 | -0.63595 | 0.85655 | 0.2691 | 0.2247 | -0.022682 | 0.2568 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.1088 | 2.349% | CZ 6A | 0 | 0 | 0.00035587 | 0.18857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18892 | 2.349% | CZ 6A | 14.9091 | 3.7311 | 0.038896 | 20.6104 | -6.6578 | 8.9672 | 2.8172 | 2.3524 | -0.23745 | 2.6885 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 53.1956 | 2.349%
CZ 6B | 0.1513 | 0.037678 | 0.00034987 | 0.10202 | -0.072958 | 0.10304 | 0.022941 | 0.019317 | 0 | 0.015963 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.42002 | 0.09127% | CZ 6B | 4.8564 | 1.2094 | 0.035701 | 10.4101 | -2.3418 | 3.3073 | 0.73636 | 0.62003 | 0 | 0.51237 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 20.6418 | 0.09127% | CZ 6B | 1.4233 | 0.35445 | 0 | 0 | -0.68634 | 0.96932 | 0.21582 | 0.18172 | 0 | 0.15017 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 2.9883 | 0.09127% | CZ 6B | 0 | 0 | 0.00035701 | 0.1041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10446 | 0.09127% | CZ 6B | 14.9009 | 3.7107 | 0.039021 | 11.3783 | -7.1853 | 10.1478 | 2.2594 | 1.9024 | 0 | 1.5721 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 42.7015 | 0.09127%
CZ 7 | 0.15126 | 0.037599 | 0.00035602 | 0.21658 | -0.079725 | 0.097314 | 0.024494 | 0.029569 | -0.0027428 | 0.021957 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.53703 | 0.2174% | CZ 7 | 4.855 | 1.2068 | 0.036328 | 22.0997 | -2.559 | 3.1236 | 0.78622 | 0.9491 | -0.088038 | 0.70478 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 32.4104 | 0.2174% | CZ 7 | 1.4229 | 0.3537 | 0 | 0 | -0.75 | 0.91546 | 0.23043 | 0.27816 | -0.025802 | 0.20656 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 3.0112 | 0.2174% | CZ 7 | 0 | 0 | 0.00036328 | 0.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22136 | 0.2174% | CZ 7 | 14.8966 | 3.7029 | 0.039707 | 24.155 | -7.8517 | 9.584 | 2.4123 | 2.9121 | -0.27013 | 2.1625 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 55.7194 | 0.2174%
CZ 8 | 0.14791 | 0.035659 | 0.00035285 | 0.27284 | -0.082394 | 0.09618 | 0.017136 | 0.025251 | -0.0028915 | 0.014849 | 0 | 0.0032842 | 0.0052765 | 0 | 0 | 0.03181 | 0.56526 | 0% | CZ 8 | 4.7475 | 1.1446 | 0.036005 | 27.8404 | -2.6447 | 3.0872 | 0.55002 | 0.8105 | -0.09281 | 0.47662 | 0 | 0.10542 | 0.16936 | 0 | 0 | 1.021 | 37.2511 | 0% | CZ 8 | 1.3914 | 0.33545 | 0 | 0 | -0.77511 | 0.9048 | 0.1612 | 0.23754 | -0.027201 | 0.13969 | 0 | 0.030896 | 0.049638 | 0 | 0 | 0.29925 | 2.7476 | 0% | CZ 8 | 0 | 0 | 0.00036005 | 0.2784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27876 | 0% | CZ 8 | 14.5666 | 3.5119 | 0.039353 | 30.4296 | -8.1146 | 9.4724 | 1.6876 | 2.4868 | -0.28477 | 1.4624 | 0 | 0.32345 | 0.51966 | 0 | 0 | 3.1329 | 59.2333 | 0%
US Weighted | 0.15146 | 0.038046 | 0.00035546 | 0.06713 | -0.047255 | 0.12983 | 0.048129 | 0.025314 | -0.0020252 | 0.042824 | 0 | 0.0032842 | 0.0052783 | 0 | 0 | 0.03181 | 0.49419 | 100% | US Weighted | 4.8617 | 1.2212 | 0.036271 | 6.85 | -1.5168 | 4.1673 | 1.5448 | 0.81254 | -0.065004 | 1.3746 | 0 | 0.10542 | 0.16942 | 0 | 0 | 1.021 | 20.5825 | 100% | US Weighted | 1.4249 | 0.35791 | 0 | 0 | -0.44454 | 1.2214 | 0.45276 | 0.23814 | -0.019052 | 0.40286 | 0 | 0.030896 | 0.049654 | 0 | 0 | 0.29925 | 4.0141 | 100% | US Weighted | 0 | 0 | 0.00036271 | 0.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068863 | 100% | US Weighted | 14.9171 | 3.747 | 0.039644 | 7.4871 | -4.6539 | 12.7865 | 4.74 | 2.4931 | -0.19945 | 4.2176 | 0 | 0.32345 | 0.51983 | 0 | 0 | 3.1329 | 49.5507 | 100%
Building Type: | Large Office |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Office |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Large Office |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Office |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 498588 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 498588 | [17 empty] | Prototype Floor Area: | 498588 | Building Type: | Large Office | [15 empty] | Prototype Floor Area: | 498588 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 49.9% | 66.01% | 4.711% | -50.4% |  | 42.2% | 46.19% | 18.29% |  | 59.55% |  | 2.834% | 61.95% |  | 0% | 9.145% | 28.39% | 0% | CZ 0A | 49.9% | 66.01% | 4.711% | -50.4% |  | 42.2% | 46.19% | 18.29% |  | 59.55% |  | 2.834% | 61.95% |  | 0% | 9.145% | 28.23% | 0% | CZ 0A | 49.9% | 66.01% |  |  |  | 42.2% | 46.19% | 18.29% |  | 59.55% |  | 2.834% | 61.95% |  | 0% | 9.145% | 28.46% | 0% | CZ 0A |  |  | 4.711% | -50.4% | [12 empty] | 3.45% | 0% | CZ 0A | 49.9% | 66.01% | 4.711% | -50.4% |  | 42.2% | 46.19% | 18.29% |  | 59.55% |  | 2.834% | 61.95% |  | 0% | 9.145% | 28.38% | 0%
CZ 0B | 49.87% | 65.45% | 4.78% | 87.9% | 4.23% | 24.39% | 39.29% | 19.5% |  | 50.51% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.95% | 0% | CZ 0B | 49.87% | 65.45% | 4.78% | 87.9% | 4.23% | 24.39% | 39.29% | 19.5% |  | 50.51% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.99% | 0% | CZ 0B | 49.87% | 65.45% |  |  | 4.23% | 24.39% | 39.29% | 19.5% |  | 50.51% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.93% | 0% | CZ 0B |  |  | 4.78% | 87.9% | [12 empty] | 26.66% | 0% | CZ 0B | 49.87% | 65.45% | 4.78% | 87.9% | 4.23% | 24.39% | 39.29% | 19.5% |  | 50.51% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.95% | 0%
CZ 1A | 49.81% | 65.29% | 4.282% | 47.74% |  | 31.68% | 42.54% | 21.85% |  | 65.47% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.41% | 2.832% | CZ 1A | 49.81% | 65.29% | 4.282% | 47.74% |  | 31.68% | 42.54% | 21.85% |  | 65.47% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.27% | 2.832% | CZ 1A | 49.81% | 65.29% |  |  |  | 31.68% | 42.54% | 21.85% |  | 65.47% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.47% | 2.832% | CZ 1A |  |  | 4.282% | 47.74% | [12 empty] | 7.826% | 2.832% | CZ 1A | 49.81% | 65.29% | 4.282% | 47.74% |  | 31.68% | 42.54% | 21.85% |  | 65.47% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.4% | 2.832%
CZ 1B | 49.8% | 65.37% | 4.407% | 84.24% | 3.276% | 23.62% | 36.7% | 17.94% |  | 48.38% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.01% | 0% | CZ 1B | 49.8% | 65.37% | 4.407% | 84.24% | 3.276% | 23.62% | 36.7% | 17.94% |  | 48.38% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.48% | 0% | CZ 1B | 49.8% | 65.37% |  |  | 3.276% | 23.62% | 36.7% | 17.94% |  | 48.38% |  | 2.834% | 61.95% |  | 0% | 9.145% | 20.79% | 0% | CZ 1B |  |  | 4.407% | 84.24% | [12 empty] | 48.35% | 0% | CZ 1B | 49.8% | 65.37% | 4.407% | 84.24% | 3.276% | 23.62% | 36.7% | 17.94% |  | 48.38% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.04% | 0%
CZ 2A | 49.86% | 65.25% | 3.994% | 92.61% | -2144% | 43.03% | 46.44% | 20.47% |  | 63% |  | 2.834% | 61.95% |  | 0% | 9.145% | 26.2% | 14.12% | CZ 2A | 49.86% | 65.25% | 3.994% | 92.61% | -2144% | 43.03% | 46.44% | 20.47% |  | 63% |  | 2.834% | 61.95% |  | 0% | 9.145% | 27.24% | 14.12% | CZ 2A | 49.86% | 65.25% |  |  | -2144% | 43.03% | 46.44% | 20.47% |  | 63% |  | 2.834% | 61.95% |  | 0% | 9.145% | 25.71% | 14.12% | CZ 2A |  |  | 3.994% | 92.61% | [12 empty] | 65.12% | 14.12% | CZ 2A | 49.86% | 65.25% | 3.994% | 92.61% | -2144% | 43.03% | 46.44% | 20.47% |  | 63% |  | 2.834% | 61.95% |  | 0% | 9.145% | 26.27% | 14.12%
CZ 2B | 49.84% | 65.25% | 4.022% | 92.58% | -2556% | 31.48% | 37.04% | 17.3% |  | 58.05% |  | 2.834% | 61.95% |  | 0% | 9.145% | 18.64% | 1.729% | CZ 2B | 49.84% | 65.25% | 4.022% | 92.58% | -2556% | 31.48% | 37.04% | 17.3% |  | 58.05% |  | 2.834% | 61.95% |  | 0% | 9.145% | 20.22% | 1.729% | CZ 2B | 49.84% | 65.25% |  |  | -2556% | 31.48% | 37.04% | 17.3% |  | 58.05% |  | 2.834% | 61.95% |  | 0% | 9.145% | 17.87% | 1.729% | CZ 2B |  |  | 4.022% | 92.58% | [12 empty] | 67.65% | 1.729% | CZ 2B | 49.84% | 65.25% | 4.022% | 92.58% | -2556% | 31.48% | 37.04% | 17.3% |  | 58.05% |  | 2.834% | 61.95% |  | 0% | 9.145% | 18.73% | 1.729%
CZ 3A | 49.75% | 64.98% | 3.514% | 88.88% | -1685% | 41.86% | 45.77% | 18.52% |  | 69.58% |  | 2.834% | 61.95% |  | 0% | 9.145% | 23.82% | 14.09% | CZ 3A | 49.75% | 64.98% | 3.514% | 88.88% | -1685% | 41.86% | 45.77% | 18.52% |  | 69.58% |  | 2.834% | 61.95% |  | 0% | 9.145% | 27.33% | 14.09% | CZ 3A | 49.75% | 64.98% |  |  | -1685% | 41.86% | 45.77% | 18.52% |  | 69.58% |  | 2.834% | 61.95% |  | 0% | 9.145% | 22.04% | 14.09% | CZ 3A |  |  | 3.514% | 88.88% | [12 empty] | 76.39% | 14.09% | CZ 3A | 49.75% | 64.98% | 3.514% | 88.88% | -1685% | 41.86% | 45.77% | 18.52% |  | 69.58% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.05% | 14.09%
CZ 3B | 49.81% | 65.53% | 3.582% | 69.38% | -85.68% | 28.11% | 34.87% | 6.808% |  | 47.33% |  | 2.834% | 61.95% |  | 0% | 9.145% | 17.24% | 6.659% | CZ 3B | 49.81% | 65.53% | 3.582% | 69.38% | -85.68% | 28.11% | 34.87% | 6.808% |  | 47.33% |  | 2.834% | 61.95% |  | 0% | 9.145% | 18.25% | 6.659% | CZ 3B | 49.81% | 65.53% |  |  | -85.68% | 28.11% | 34.87% | 6.808% |  | 47.33% |  | 2.834% | 61.95% |  | 0% | 9.145% | 16.75% | 6.659% | CZ 3B |  |  | 3.582% | 69.38% | [12 empty] | 48.59% | 6.659% | CZ 3B | 49.81% | 65.53% | 3.582% | 69.38% | -85.68% | 28.11% | 34.87% | 6.808% |  | 47.33% |  | 2.834% | 61.95% |  | 0% | 9.145% | 17.3% | 6.659%
CZ 3C | 49.74% | 65.57% | 3.465% | 95.07% | -4698% | 42.9% | 46.02% | 19.67% |  | 61.13% |  | 2.834% | 61.95% |  | 0% | 9.145% | 22.14% | 5.951% | CZ 3C | 49.74% | 65.57% | 3.465% | 95.07% | -4698% | 42.9% | 46.02% | 19.67% |  | 61.13% |  | 2.834% | 61.95% |  | 0% | 9.145% | 23.51% | 5.951% | CZ 3C | 49.74% | 65.57% |  |  | -4698% | 42.9% | 46.02% | 19.67% |  | 61.13% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.47% | 5.951% | CZ 3C |  |  | 3.465% | 95.07% | [12 empty] | 63.91% | 5.951% | CZ 3C | 49.74% | 65.57% | 3.465% | 95.07% | -4698% | 42.9% | 46.02% | 19.67% |  | 61.13% |  | 2.834% | 61.95% |  | 0% | 9.145% | 22.22% | 5.951%
CZ 4A | 49.71% | 65.1% | 3.183% | 87.28% | -3827% | 50.78% | 49.02% | 16.72% |  | 74.28% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.52% | 29.22% | CZ 4A | 49.71% | 65.1% | 3.183% | 87.28% | -3827% | 50.78% | 49.02% | 16.72% |  | 74.28% |  | 2.834% | 61.95% |  | 0% | 9.145% | 30.43% | 29.22% | CZ 4A | 49.71% | 65.1% |  |  | -3827% | 50.78% | 49.02% | 16.72% |  | 74.28% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.3% | 29.22% | CZ 4A |  |  | 3.183% | 87.28% | [12 empty] | 79.22% | 29.22% | CZ 4A | 49.71% | 65.1% | 3.183% | 87.28% | -3827% | 50.78% | 49.02% | 16.72% |  | 74.28% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.92% | 29.22%
CZ 4B | 49.87% | 65.42% | 3.235% | 70.8% | -70.39% | 40.65% | 42.53% | 13.85% |  | 54.13% |  | 2.834% | 61.95% |  | 0% | 9.145% | 19.32% | 0.02014% | CZ 4B | 49.87% | 65.42% | 3.235% | 70.8% | -70.39% | 40.65% | 42.53% | 13.85% |  | 54.13% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.65% | 0.02014% | CZ 4B | 49.87% | 65.42% |  |  | -70.39% | 40.65% | 42.53% | 13.85% |  | 54.13% |  | 2.834% | 61.95% |  | 0% | 9.145% | 18.15% | 0.02014% | CZ 4B |  |  | 3.235% | 70.8% | [12 empty] | 58.58% | 0.02014% | CZ 4B | 49.87% | 65.42% | 3.235% | 70.8% | -70.39% | 40.65% | 42.53% | 13.85% |  | 54.13% |  | 2.834% | 61.95% |  | 0% | 9.145% | 19.47% | 0.02014%
CZ 4C | 49.57% | 64.58% | 3.04% | 71.71% | -4566% | 55.67% | 56.04% | 19.39% |  | 56.87% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.47% | 6.185% | CZ 4C | 49.57% | 64.58% | 3.04% | 71.71% | -4566% | 55.67% | 56.04% | 19.39% |  | 56.87% |  | 2.834% | 61.95% |  | 0% | 9.145% | 25.09% | 6.185% | CZ 4C | 49.57% | 64.58% |  |  | -4566% | 55.67% | 56.04% | 19.39% |  | 56.87% |  | 2.834% | 61.95% |  | 0% | 9.145% | 19.57% | 6.185% | CZ 4C |  |  | 3.04% | 71.71% | [12 empty] | 62.34% | 6.185% | CZ 4C | 49.57% | 64.58% | 3.04% | 71.71% | -4566% | 55.67% | 56.04% | 19.39% |  | 56.87% |  | 2.834% | 61.95% |  | 0% | 9.145% | 21.71% | 6.185%
CZ 5A | 49.76% | 64.94% | 2.963% | 85.68% | -2123% | 39.02% | 43.33% | 15.6% |  | 60.52% |  | 2.834% | 61.95% |  | 0% | 9.145% | 23.4% | 12.51% | CZ 5A | 49.76% | 64.94% | 2.963% | 85.68% | -2123% | 39.02% | 43.33% | 15.6% |  | 60.52% |  | 2.834% | 61.95% |  | 0% | 9.145% | 32.26% | 12.51% | CZ 5A | 49.76% | 64.94% |  |  | -2123% | 39.02% | 43.33% | 15.6% |  | 60.52% |  | 2.834% | 61.95% |  | 0% | 9.145% | 18.13% | 12.51% | CZ 5A |  |  | 2.963% | 85.68% | [12 empty] | 79.96% | 12.51% | CZ 5A | 49.76% | 64.94% | 2.963% | 85.68% | -2123% | 39.02% | 43.33% | 15.6% |  | 60.52% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.03% | 12.51%
CZ 5B | 49.77% | 65.17% | 3.011% | 66.16% | -75.25% | 51.66% | 45.32% | 13.93% |  | 54.03% |  | 2.834% | 61.95% |  | 0% | 9.145% | 20.65% | 3.999% | CZ 5B | 49.77% | 65.17% | 3.011% | 66.16% | -75.25% | 51.66% | 45.32% | 13.93% |  | 54.03% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.58% | 3.999% | CZ 5B | 49.77% | 65.17% |  |  | -75.25% | 51.66% | 45.32% | 13.93% |  | 54.03% |  | 2.834% | 61.95% |  | 0% | 9.145% | 18.53% | 3.999% | CZ 5B |  |  | 3.011% | 66.16% | [12 empty] | 59.35% | 3.999% | CZ 5B | 49.77% | 65.17% | 3.011% | 66.16% | -75.25% | 51.66% | 45.32% | 13.93% |  | 54.03% |  | 2.834% | 61.95% |  | 0% | 9.145% | 20.91% | 3.999%
CZ 5C | 49.54% | 64.53% | 2.924% | 69.33% | -4851% | 60.96% | 60.2% | 16.58% |  | 52.09% |  | 2.834% | 61.94% |  | 0% | 9.145% | 20.52% | 0.02726% | CZ 5C | 49.54% | 64.53% | 2.924% | 69.33% | -4851% | 60.96% | 60.2% | 16.58% |  | 52.09% |  | 2.834% | 61.94% |  | 0% | 9.145% | 24.17% | 0.02726% | CZ 5C | 49.54% | 64.53% |  |  | -4851% | 60.96% | 60.2% | 16.58% |  | 52.09% |  | 2.834% | 61.94% |  | 0% | 9.145% | 18.59% | 0.02726% | CZ 5C |  |  | 2.924% | 69.33% | [12 empty] | 60.14% | 0.02726% | CZ 5C | 49.54% | 64.53% | 2.924% | 69.33% | -4851% | 60.96% | 60.2% | 16.58% |  | 52.09% |  | 2.834% | 61.94% |  | 0% | 9.145% | 20.76% | 0.02726%
CZ 6A | 49.72% | 64.89% | 2.799% | 80.52% | -2435% | 43.3% | 45.29% | 16.23% |  | 62.08% |  | 2.834% | 61.95% |  | 0% | 9.145% | 24.58% | 2.349% | CZ 6A | 49.72% | 64.89% | 2.799% | 80.52% | -2435% | 43.3% | 45.29% | 16.23% |  | 62.08% |  | 2.834% | 61.95% |  | 0% | 9.145% | 35.01% | 2.349% | CZ 6A | 49.72% | 64.89% |  |  | -2435% | 43.3% | 45.29% | 16.23% |  | 62.08% |  | 2.834% | 61.95% |  | 0% | 9.145% | 17.81% | 2.349% | CZ 6A |  |  | 2.799% | 80.52% | [12 empty] | 76.51% | 2.349% | CZ 6A | 49.72% | 64.89% | 2.799% | 80.52% | -2435% | 43.3% | 45.29% | 16.23% |  | 62.08% |  | 2.834% | 61.95% |  | 0% | 9.145% | 25.36% | 2.349%
CZ 6B | 49.7% | 64.58% | 2.842% | 63.22% | -135% | 50.39% | 44.96% | 12.14% |  | 52.11% |  | 2.834% | 61.95% |  | 0% | 9.145% | 20.38% | 0.09127% | CZ 6B | 49.7% | 64.58% | 2.842% | 63.22% | -135% | 50.39% | 44.96% | 12.14% |  | 52.11% |  | 2.834% | 61.95% |  | 0% | 9.145% | 26.36% | 0.09127% | CZ 6B | 49.7% | 64.58% |  |  | -135% | 50.39% | 44.96% | 12.14% |  | 52.11% |  | 2.834% | 61.95% |  | 0% | 9.145% | 16.83% | 0.09127% | CZ 6B |  |  | 2.842% | 63.22% | [12 empty] | 58.94% | 0.09127% | CZ 6B | 49.7% | 64.58% | 2.842% | 63.22% | -135% | 50.39% | 44.96% | 12.14% |  | 52.11% |  | 2.834% | 61.95% |  | 0% | 9.145% | 20.8% | 0.09127%
CZ 7 | 49.68% | 64.48% | 2.707% | 83.18% | -2340% | 48.99% | 46.99% | 19.2% |  | 57.37% |  | 2.834% | 61.95% |  | 0% | 9.145% | 25.47% | 0.2174% | CZ 7 | 49.68% | 64.48% | 2.707% | 83.18% | -2340% | 48.99% | 46.99% | 19.2% |  | 57.37% |  | 2.834% | 61.95% |  | 0% | 9.145% | 37.34% | 0.2174% | CZ 7 | 49.68% | 64.48% |  |  | -2340% | 48.99% | 46.99% | 19.2% |  | 57.37% |  | 2.834% | 61.95% |  | 0% | 9.145% | 17.44% | 0.2174% | CZ 7 |  |  | 2.707% | 83.18% | [12 empty] | 79.31% | 0.2174% | CZ 7 | 49.68% | 64.48% | 2.707% | 83.18% | -2340% | 48.99% | 46.99% | 19.2% |  | 57.37% |  | 2.834% | 61.95% |  | 0% | 9.145% | 26.38% | 0.2174%
CZ 8 | 48.58% | 61.49% | 2.506% | 81.61% | -453.2% | 56.91% | 50.32% | 16.89% |  | 53.37% |  | 2.834% | 61.93% |  | 0% | 9.145% | 26.48% | 0% | CZ 8 | 48.58% | 61.49% | 2.506% | 81.61% | -453.2% | 56.91% | 50.32% | 16.89% |  | 53.37% |  | 2.834% | 61.93% |  | 0% | 9.145% | 40.1% | 0% | CZ 8 | 48.58% | 61.49% |  |  | -453.2% | 56.91% | 50.32% | 16.89% |  | 53.37% |  | 2.834% | 61.93% |  | 0% | 9.145% | 16.35% | 0% | CZ 8 |  |  | 2.506% | 81.61% | [12 empty] | 78.42% | 0% | CZ 8 | 48.58% | 61.49% | 2.506% | 81.61% | -453.2% | 56.91% | 50.32% | 16.89% |  | 53.37% |  | 2.834% | 61.93% |  | 0% | 9.145% | 27.57% | 0%
US Weighted | 49.75% | 65.11% | 3.379% | 84.3% | -2602% | 44.26% | 46.17% | 17.08% | 0% | 64.96% | 0% | 2.834% | 61.95% | 0% | 0% | 9.145% | 23.44% | 100% | US Weighted | 49.75% | 65.11% | 3.379% | 84.3% | -2602% | 44.26% | 46.17% | 17.08% | 0% | 64.96% | 0% | 2.834% | 61.95% | 0% | 0% | 9.145% | 27.75% | 100% | US Weighted | 49.75% | 65.11% | 0% | 0% | -2602% | 44.26% | 46.17% | 17.08% | 0% | 64.96% | 0% | 2.834% | 61.95% | 0% | 0% | 9.145% | 21.05% | 100% | US Weighted | 0% | 0% | 3.379% | 84.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 69.82% | 100% | US Weighted | 49.75% | 65.11% | 3.379% | 84.3% | -2602% | 44.26% | 46.17% | 17.08% | 0% | 64.96% | 0% | 2.834% | 61.95% | 0% | 0% | 9.145% | 23.73% | 100%

## RtlStA
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Standalone Retail |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 24692 |  | Building Type: | Standalone Retail |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 |  | Building Type: | Standalone Retail |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Standalone Retail |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Standalone Retail | [14 empty] | Prototype Floor Area: | 24692 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.28499 | 0.046105 | 0.034911 | 0.11616 | 0 | 0.21956 | 0 | 0.17285 | 0.00013288 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1071 |  | STD2019 | 9.1474 | 1.4799 | 3.5623 | 11.8533 | 0 | 7.0474 | 0 | 5.5482 | 0.0042652 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.1029 |  | STD2019 | 2.681 | 0.43372 | 0 | 0 | 0 | 2.0655 | 0 | 1.6261 | 0.0012501 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.9939 |  | STD2019 | 0 | 0 | 0.035623 | 0.11853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15416 |  | STD2019 | 28.067 | 4.5406 | 3.8936 | 12.9557 | 0 | 21.6233 | 0 | 17.0235 | 0.013087 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 111.0066
STD2016 | 0.35968 | 0.046105 | 0.034907 | 0.10848 | 0 | 0.2336 | 0 | 0.18061 | 0.00012978 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1959 |  | STD2016 | 11.5448 | 1.4799 | 3.562 | 11.0693 | 0 | 7.498 | 0 | 5.7973 | 0.0041657 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 48.4156 |  | STD2016 | 3.3836 | 0.43372 | 0 | 0 | 0 | 2.1975 | 0 | 1.6991 | 0.0012209 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.9016 |  | STD2016 | 0 | 0 | 0.03562 | 0.11069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14631 |  | STD2016 | 35.4229 | 4.5406 | 3.8932 | 12.0987 | 0 | 23.0059 | 0 | 17.7879 | 0.012781 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 119.6519
STD2013 | 0.44263 | 0.072171 | 0.034902 | 0.054628 | 0 | 0.23783 | 0 | 0.18045 | 0.018255 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2733 |  | STD2013 | 14.2076 | 2.3165 | 3.5615 | 5.5743 | 0 | 7.6339 | 0 | 5.792 | 0.58596 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.1319 |  | STD2013 | 4.164 | 0.67894 | 0 | 0 | 0 | 2.2374 | 0 | 1.6975 | 0.17174 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 11.136 |  | STD2013 | 0 | 0 | 0.035615 | 0.055743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091358 |  | STD2013 | 43.5929 | 7.1078 | 3.8927 | 6.0927 | 0 | 23.4231 | 0 | 17.7714 | 1.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 126.5684
STD2010 | 0.50606 | 0.072171 | 0.03491 | 0.12007 | 0 | 0.26481 | 0 | 0.24163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.4725 |  | STD2010 | 16.2434 | 2.3165 | 3.5622 | 12.2517 | 0 | 8.4999 | 0 | 7.7559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 58.1025 |  | STD2010 | 4.7607 | 0.67894 | 0 | 0 | 0 | 2.4912 | 0 | 2.2731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 12.3941 |  | STD2010 | 0 | 0 | 0.035622 | 0.12252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15814 |  | STD2010 | 49.8394 | 7.1078 | 3.8935 | 13.3911 | 0 | 26.0803 | 0 | 23.7972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 147.0381
STD2007 | 0.58858 | 0.1376 | 0.035652 | 0.1062 | 0 | 0.40476 | 0 | 0.47676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.983 |  | STD2007 | 18.8922 | 4.4167 | 3.638 | 10.8372 | 0 | 12.9919 | 0 | 15.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 73.5721 |  | STD2007 | 5.537 | 1.2945 | 0 | 0 | 0 | 3.8077 | 0 | 4.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 17.3203 |  | STD2007 | 0 | 0 | 0.03638 | 0.10837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14475 |  | STD2007 | 57.9668 | 13.5518 | 3.9763 | 11.845 | 0 | 39.8629 | 0 | 46.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 197.148
STD2004 | 0.58858 | 0.1376 | 0.03567 | 0.16932 | 0 | 0.44671 | 0 | 0.54528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.1566 |  | STD2004 | 18.8922 | 4.4167 | 3.6398 | 17.2778 | 0 | 14.3384 | 0 | 17.5023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 83.5604 |  | STD2004 | 5.537 | 1.2945 | 0 | 0 | 0 | 4.2023 | 0 | 5.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 18.3596 |  | STD2004 | 0 | 0 | 0.036398 | 0.17278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20918 |  | STD2004 | 57.9668 | 13.5518 | 3.9783 | 18.8846 | 0 | 43.9944 | 0 | 53.7021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 215.0691
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 1.8317e-05 | 0.063118 | 0 | 0.04195 | 0 | 0.068518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1736 |  | 2004-2007 | 0 | 0 | 0.001869 | 6.4406 | 0 | 1.3465 | 0 | 2.1993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9883 |  | 2004-2007 | 0 | 0 | 0 | 0 | 0 | 0.39464 | 0 | 0.64457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0392 |  | 2004-2007 | 0 | 0 | 1.869e-05 | 0.064406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064425 |  | 2004-2007 | 0 | 0 | 0.0020429 | 7.0396 | 0 | 4.1315 | 0 | 6.748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.9211
2007-2010 | 0.082523 | 0.06543 | 0.00074196 | -0.013862 | 0 | 0.13995 | 0 | 0.23513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00063398 | 0.51054 |  | 2007-2010 | 2.6488 | 2.1002 | 0.07571 | -1.4145 | 0 | 4.492 | 0 | 7.5472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020349 | 15.4697 |  | 2007-2010 | 0.77633 | 0.61552 | 0 | 0 | 0 | 1.3165 | 0 | 2.2119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005964 | 4.9263 |  | 2007-2010 | 0 | 0 | 0.0007571 | -0.014145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.013388 |  | 2007-2010 | 8.1274 | 6.4439 | 0.082751 | -1.5461 | 0 | 13.7826 | 0 | 23.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062438 | 50.1099
2010-2013 | 0.063426 | 0 | 7.5412e-06 | 0.065438 | 0 | 0.02698 | 0 | 0.061185 | -0.018255 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00039474 | 0.19918 |  | 2010-2013 | 2.0358 | 0 | 0.00076951 | 6.6774 | 0 | 0.86599 | 0 | 1.9639 | -0.58596 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01267 | 10.9706 |  | 2010-2013 | 0.59667 | 0 | 0 | 0 | 0 | 0.25381 | 0 | 0.57559 | -0.17174 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037135 | 1.258 |  | 2010-2013 | 0 | 0 | 7.6951e-06 | 0.066774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066781 |  | 2010-2013 | 6.2465 | 0 | 0.00084107 | 7.2984 | 0 | 2.6571 | 0 | 6.0259 | -1.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038876 | 20.4697
2013-2016 | 0.082956 | 0.026067 | -4.9388e-06 | -0.053851 | 0 | 0.0042361 | 0 | -0.00016775 | 0.018126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077362 |  | 2013-2016 | 2.6627 | 0.83669 | -0.00050396 | -5.495 | 0 | 0.13597 | 0 | -0.0053844 | 0.5818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2837 |  | 2013-2016 | 0.7804 | 0.24522 | 0 | 0 | 0 | 0.03985 | 0 | -0.0015781 | 0.17051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2344 |  | 2013-2016 | 0 | 0 | -5.0396e-06 | -0.05495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.054955 |  | 2013-2016 | 8.17 | 2.5672 | -0.00055083 | -6.006 | 0 | 0.41719 | 0 | -0.016521 | 1.7851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9165
2016-2019 | 0.07469 | 0 | -3.3186e-06 | -0.0076835 | 0 | 0.014039 | 0 | 0.0077613 | -3.1013e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088801 |  | 2016-2019 | 2.3974 | 0 | -0.00033863 | -0.78403 | 0 | 0.45062 | 0 | 0.24912 | -9.9546e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3127 |  | 2016-2019 | 0.70264 | 0 | 0 | 0 | 0 | 0.13207 | 0 | 0.073013 | -2.9175e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90769 |  | 2016-2019 | 0 | 0 | -3.3863e-06 | -0.0078403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0078437 |  | 2016-2019 | 7.3559 | 0 | -0.00037012 | -0.85694 | 0 | 1.3826 | 0 | 0.76437 | -0.00030544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6453
2004-2019 | 0.3036 | 0.091497 | 0.00075956 | 0.05316 | 0 | 0.22715 | 0 | 0.37243 | -0.00013288 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.0495 |  | 2004-2019 | 9.7448 | 2.9369 | 0.077506 | 5.4245 | 0 | 7.2911 | 0 | 11.9541 | -0.0042652 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 37.4575 |  | 2004-2019 | 2.856 | 0.86074 | 0 | 0 | 0 | 2.1369 | 0 | 3.5035 | -0.0012501 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 9.3656 |  | 2004-2019 | 0 | 0 | 0.00077506 | 0.054245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05502 |  | 2004-2019 | 29.8998 | 9.0111 | 0.084714 | 5.9289 | 0 | 22.3711 | 0 | 36.6786 | -0.013087 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 104.0625
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.05135% | 37.28% |  | 9.391% |  | 12.57% | [7 empty] | 0% | 8.05% |  | 2004-2007 | 0% | 0% | 0.05135% | 37.28% |  | 9.391% |  | 12.57% | [7 empty] | 0% | 11.95% |  | 2004-2007 | 0% | 0% |  |  |  | 9.391% |  | 12.57% | [7 empty] | 0% | 5.66% |  | 2004-2007 |  |  | 0.05135% | 37.28% | [12 empty] | 30.8% |  | 2004-2007 | 0% | 0% | 0.05135% | 37.28% |  | 9.391% |  | 12.57% | [7 empty] | 0% | 8.333%
2007-2010 | 14.02% | 47.55% | 2.081% | -13.05% |  | 34.58% |  | 49.32% | [7 empty] | 0.2716% | 25.75% |  | 2007-2010 | 14.02% | 47.55% | 2.081% | -13.05% |  | 34.58% |  | 49.32% | [7 empty] | 0.2716% | 21.03% |  | 2007-2010 | 14.02% | 47.55% |  |  |  | 34.58% |  | 49.32% | [7 empty] | 0.2716% | 28.44% |  | 2007-2010 |  |  | 2.081% | -13.05% | [12 empty] | -9.249% |  | 2007-2010 | 14.02% | 47.55% | 2.081% | -13.05% |  | 34.58% |  | 49.32% | [7 empty] | 0.2716% | 25.42%
2010-2013 | 12.53% | 0% | 0.0216% | 54.5% |  | 10.19% |  | 25.32% | [7 empty] | 0.1696% | 13.53% |  | 2010-2013 | 12.53% | 0% | 0.0216% | 54.5% |  | 10.19% |  | 25.32% | [7 empty] | 0.1696% | 18.88% |  | 2010-2013 | 12.53% | 0% |  |  |  | 10.19% |  | 25.32% | [7 empty] | 0.1696% | 10.15% |  | 2010-2013 |  |  | 0.0216% | 54.5% | [12 empty] | 42.23% |  | 2010-2013 | 12.53% | 0% | 0.0216% | 54.5% |  | 10.19% |  | 25.32% | [7 empty] | 0.1696% | 13.92%
2013-2016 | 18.74% | 36.12% | -0.01415% | -98.58% |  | 1.781% |  | -0.09296% | 99.29% | [6 empty] | 0% | 6.076% |  | 2013-2016 | 18.74% | 36.12% | -0.01415% | -98.58% |  | 1.781% |  | -0.09296% | 99.29% | [6 empty] | 0% | -2.724% |  | 2013-2016 | 18.74% | 36.12% |  |  |  | 1.781% |  | -0.09296% | 99.29% | [6 empty] | 0% | 11.08% |  | 2013-2016 |  |  | -0.01415% | -98.58% | [12 empty] | -60.15% |  | 2013-2016 | 18.74% | 36.12% | -0.01415% | -98.58% |  | 1.781% |  | -0.09296% | 99.29% | [6 empty] | 0% | 5.465%
2016-2019 | 20.77% | 0% | -0.009507% | -7.083% |  | 6.01% |  | 4.297% | -2.39% | [6 empty] | 0% | 7.425% |  | 2016-2019 | 20.77% | 0% | -0.009507% | -7.083% |  | 6.01% |  | 4.297% | -2.39% | [6 empty] | 0% | 4.777% |  | 2016-2019 | 20.77% | 0% |  |  |  | 6.01% |  | 4.297% | -2.39% | [6 empty] | 0% | 9.167% |  | 2016-2019 |  |  | -0.009507% | -7.083% | [12 empty] | -5.361% |  | 2016-2019 | 20.77% | 0% | -0.009507% | -7.083% |  | 6.01% |  | 4.297% | -2.39% | [6 empty] | 0% | 7.225%
2004-2019 | 51.58% | 66.49% | 2.129% | 31.4% |  | 50.85% |  | 68.3% | [7 empty] | 0.4407% | 48.66% |  | 2004-2019 | 51.58% | 66.49% | 2.129% | 31.4% |  | 50.85% |  | 68.3% | [7 empty] | 0.4407% | 44.83% |  | 2004-2019 | 51.58% | 66.49% |  |  |  | 50.85% |  | 68.3% | [7 empty] | 0.4407% | 51.01% |  | 2004-2019 |  |  | 2.129% | 31.4% | [12 empty] | 26.3% |  | 2004-2019 | 51.58% | 66.49% | 2.129% | 31.4% |  | 50.85% |  | 68.3% | [7 empty] | 0.4407% | 48.39%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.25494 | 0.046113 | 0.031418 | 0 | 0 | 0.95563 | 0 | 0.2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.7239 | 0% | CZ 0A | 8.1831 | 1.4801 | 3.206 | 0 | 0 | 30.6737 | 0 | 6.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 57.5317 | 0% | CZ 0A | 2.3983 | 0.4338 | 0 | 0 | 0 | 8.9899 | 0 | 1.9134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 15.922 | 0% | CZ 0A | 0 | 0 | 0.03206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03206 | 0% | CZ 0A | 25.1081 | 4.5414 | 3.5041 | 0 | 0 | 94.1157 | 0 | 20.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 170.1911 | 0%
CZ 0B | 0.25962 | 0.046089 | 0.031317 | 3.7618e-06 | 0 | 0.84724 | 0 | 0.21332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.63 | 0% | CZ 0B | 8.3332 | 1.4794 | 3.1956 | 0.00038386 | 0 | 27.1947 | 0 | 6.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 54.5104 | 0% | CZ 0B | 2.4423 | 0.43357 | 0 | 0 | 0 | 7.9703 | 0 | 2.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 15.0394 | 0% | CZ 0B | 0 | 0 | 0.031956 | 3.8386e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03196 | 0% | CZ 0B | 25.5688 | 4.5391 | 3.4928 | 0.00041955 | 0 | 83.4413 | 0 | 21.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 160.9406 | 0%
CZ 1A | 0.27524 | 0.046089 | 0.032114 | 0 | 0 | 0.63442 | 0 | 0.16646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.3867 | 2.651% | CZ 1A | 8.8347 | 1.4794 | 3.277 | 0 | 0 | 20.3635 | 0 | 5.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.7577 | 2.651% | CZ 1A | 2.5893 | 0.43357 | 0 | 0 | 0 | 5.9682 | 0 | 1.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 12.7435 | 2.651% | CZ 1A | 0 | 0 | 0.03277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03277 | 2.651% | CZ 1A | 27.1073 | 4.5391 | 3.5817 | 0 | 0 | 62.4811 | 0 | 16.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 136.993 | 2.651%
CZ 1B | 0.27228 | 0.046017 | 0.032111 | 0.0068728 | 0 | 0.6793 | 0 | 0.20073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.4697 | 0% | CZ 1B | 8.7394 | 1.4771 | 3.2766 | 0.7013 | 0 | 21.8041 | 0 | 6.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 49.9017 | 0% | CZ 1B | 2.5614 | 0.4329 | 0 | 0 | 0 | 6.3904 | 0 | 1.8883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 13.4595 | 0% | CZ 1B | 0 | 0 | 0.032766 | 0.007013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039779 | 0% | CZ 1B | 26.8151 | 4.532 | 3.5813 | 0.76653 | 0 | 66.9012 | 0 | 19.7691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 145.2552 | 0%
CZ 2A | 0.27554 | 0.045993 | 0.032931 | 0.0049167 | 0 | 0.44122 | 0 | 0.15177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1848 | 16.38% | CZ 2A | 8.8443 | 1.4763 | 3.3603 | 0.5017 | 0 | 14.1623 | 0 | 4.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 40.6765 | 16.38% | CZ 2A | 2.5921 | 0.43267 | 0 | 0 | 0 | 4.1507 | 0 | 1.4278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.7897 | 16.38% | CZ 2A | 0 | 0 | 0.033603 | 0.005017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03862 | 16.38% | CZ 2A | 27.1368 | 4.5297 | 3.6728 | 0.54836 | 0 | 43.4542 | 0 | 14.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 117.1789 | 16.38%
CZ 2B | 0.28761 | 0.046041 | 0.032968 | 0.0028552 | 0 | 0.33808 | 0 | 0.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1211 | 2.81% | CZ 2B | 9.2317 | 1.4778 | 3.3641 | 0.29135 | 0 | 10.8516 | 0 | 5.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 38.4896 | 2.81% | CZ 2B | 2.7056 | 0.43312 | 0 | 0 | 0 | 3.1804 | 0 | 1.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.2093 | 2.81% | CZ 2B | 0 | 0 | 0.033641 | 0.0029135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036555 | 2.81% | CZ 2B | 28.3254 | 4.5344 | 3.677 | 0.31844 | 0 | 33.2957 | 0 | 17.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 110.8767 | 2.81%
CZ 3A | 0.2776 | 0.046029 | 0.034341 | 0.064518 | 0 | 0.24314 | 0 | 0.16524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.0633 | 16.25% | CZ 3A | 8.9103 | 1.4774 | 3.5042 | 6.5835 | 0 | 7.8041 | 0 | 5.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 41.0436 | 16.25% | CZ 3A | 2.6115 | 0.43301 | 0 | 0 | 0 | 2.2873 | 0 | 1.5545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.0727 | 16.25% | CZ 3A | 0 | 0 | 0.035042 | 0.065835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10088 | 16.25% | CZ 3A | 27.3394 | 4.5332 | 3.8301 | 7.1958 | 0 | 23.9454 | 0 | 16.2738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 106.0075 | 16.25%
CZ 3B | 0.28644 | 0.046017 | 0.033969 | 0.02201 | 0 | 0.23687 | 0 | 0.17854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.0363 | 7.8% | CZ 3B | 9.194 | 1.4771 | 3.4662 | 2.2459 | 0 | 7.603 | 0 | 5.7308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 37.1772 | 7.8% | CZ 3B | 2.6946 | 0.4329 | 0 | 0 | 0 | 2.2283 | 0 | 1.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.2219 | 7.8% | CZ 3B | 0 | 0 | 0.034662 | 0.022459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057122 | 7.8% | CZ 3B | 28.21 | 4.532 | 3.7886 | 2.4548 | 0 | 23.3281 | 0 | 17.5838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 102.7871 | 7.8%
CZ 3C | 0.28625 | 0.046173 | 0.034473 | 0.0031749 | 0 | 0.10625 | 0 | 0.16154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 0.87028 | 1.112% | CZ 3C | 9.1879 | 1.482 | 3.5177 | 0.32397 | 0 | 3.4102 | 0 | 5.1852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 30.5672 | 1.112% | CZ 3C | 2.6928 | 0.43436 | 0 | 0 | 0 | 0.99948 | 0 | 1.5197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 7.8328 | 1.112% | CZ 3C | 0 | 0 | 0.035177 | 0.0032397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038416 | 1.112% | CZ 3C | 28.1911 | 4.5473 | 3.8448 | 0.3541 | 0 | 10.4636 | 0 | 15.9098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 86.2006 | 1.112%
CZ 4A | 0.28607 | 0.046256 | 0.035455 | 0.15055 | 0 | 0.1609 | 0 | 0.17389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.0855 | 17.53% | CZ 4A | 9.1821 | 1.4847 | 3.6178 | 15.3627 | 0 | 5.1645 | 0 | 5.5815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.8535 | 17.53% | CZ 4A | 2.6911 | 0.43515 | 0 | 0 | 0 | 1.5136 | 0 | 1.6358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.4622 | 17.53% | CZ 4A | 0 | 0 | 0.036178 | 0.15363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18981 | 17.53% | CZ 4A | 28.1735 | 4.5556 | 3.9543 | 16.7914 | 0 | 15.8462 | 0 | 17.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 109.3363 | 17.53%
CZ 4B | 0.28695 | 0.046017 | 0.035131 | 0.053718 | 0 | 0.16236 | 0 | 0.19296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.0096 | 0.7484% | CZ 4B | 9.2106 | 1.4771 | 3.5848 | 5.4815 | 0 | 5.2113 | 0 | 6.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 38.6189 | 0.7484% | CZ 4B | 2.6995 | 0.4329 | 0 | 0 | 0 | 1.5274 | 0 | 1.8152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.6614 | 0.7484% | CZ 4B | 0 | 0 | 0.035848 | 0.054815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090663 | 0.7484% | CZ 4B | 28.2606 | 4.532 | 3.9182 | 5.9912 | 0 | 15.9899 | 0 | 19.0034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 100.5852 | 0.7484%
CZ 4C | 0.29098 | 0.046292 | 0.03579 | 0.099891 | 0 | 0.046591 | 0 | 0.17712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 0.92908 | 2.419% | CZ 4C | 9.3399 | 1.4859 | 3.652 | 10.1929 | 0 | 1.4955 | 0 | 5.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 39.3115 | 2.419% | CZ 4C | 2.7374 | 0.43549 | 0 | 0 | 0 | 0.4383 | 0 | 1.6662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 7.4638 | 2.419% | CZ 4C | 0 | 0 | 0.03652 | 0.10193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13845 | 2.419% | CZ 4C | 28.6576 | 4.5591 | 3.9916 | 11.1409 | 0 | 4.5886 | 0 | 17.4436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 93.2713 | 2.419%
CZ 5A | 0.28584 | 0.046101 | 0.036384 | 0.23319 | 0 | 0.092776 | 0 | 0.17845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1052 | 21.62% | CZ 5A | 9.1748 | 1.4797 | 3.7127 | 23.7945 | 0 | 2.9779 | 0 | 5.7278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 54.3275 | 21.62% | CZ 5A | 2.689 | 0.43369 | 0 | 0 | 0 | 0.87278 | 0 | 1.6787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 7.8606 | 21.62% | CZ 5A | 0 | 0 | 0.037127 | 0.23794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27507 | 21.62% | CZ 5A | 28.1511 | 4.5403 | 4.0579 | 26.0073 | 0 | 9.1371 | 0 | 17.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 112.3579 | 21.62%
CZ 5B | 0.28864 | 0.046197 | 0.036113 | 0.12971 | 0 | 0.11465 | 0 | 0.20065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.0484 | 4.907% | CZ 5B | 9.2647 | 1.4828 | 3.685 | 13.2361 | 0 | 3.6802 | 0 | 6.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.2493 | 4.907% | CZ 5B | 2.7153 | 0.43459 | 0 | 0 | 0 | 1.0786 | 0 | 1.8876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.3025 | 4.907% | CZ 5B | 0 | 0 | 0.03685 | 0.13236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16921 | 4.907% | CZ 5B | 28.4267 | 4.5497 | 4.0277 | 14.4671 | 0 | 11.2918 | 0 | 19.7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 105.4137 | 4.907%
CZ 5C | 0.28895 | 0.046244 | 0.036316 | 0.11889 | 0 | 0.019749 | 0 | 0.17452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 0.91709 | 0.1033% | CZ 5C | 9.2747 | 1.4843 | 3.7057 | 12.1318 | 0 | 0.6339 | 0 | 5.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 40.2924 | 0.1033% | CZ 5C | 2.7183 | 0.43504 | 0 | 0 | 0 | 0.18579 | 0 | 1.6418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 7.1673 | 0.1033% | CZ 5C | 0 | 0 | 0.037057 | 0.12132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15838 | 0.1033% | CZ 5C | 28.4574 | 4.5544 | 4.0504 | 13.26 | 0 | 1.945 | 0 | 17.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 92.345 | 0.1033%
CZ 6A | 0.32201 | 0.046173 | 0.037069 | 0.31741 | 0 | 0.104 | 0 | 0.19564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2547 | 4.509% | CZ 6A | 10.3359 | 1.482 | 3.7825 | 32.389 | 0 | 3.3381 | 0 | 6.2795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 65.0671 | 4.509% | CZ 6A | 3.0293 | 0.43436 | 0 | 0 | 0 | 0.97833 | 0 | 1.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.4688 | 4.509% | CZ 6A | 0 | 0 | 0.037825 | 0.32389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36172 | 4.509% | CZ 6A | 31.7135 | 4.5473 | 4.1343 | 35.4012 | 0 | 10.2421 | 0 | 19.2673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 128.1956 | 4.509%
CZ 6B | 0.32314 | 0.046089 | 0.036896 | 0.21721 | 0 | 0.071484 | 0 | 0.20015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1274 | 0.5672% | CZ 6B | 10.372 | 1.4794 | 3.7649 | 22.1638 | 0 | 2.2945 | 0 | 6.4242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 53.9589 | 0.5672% | CZ 6B | 3.0399 | 0.43357 | 0 | 0 | 0 | 0.67247 | 0 | 1.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.2152 | 0.5672% | CZ 6B | 0 | 0 | 0.037649 | 0.22164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25929 | 0.5672% | CZ 6B | 31.8243 | 4.5391 | 4.115 | 24.2251 | 0 | 7.0401 | 0 | 19.7114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 114.3448 | 0.5672%
CZ 7 | 0.31878 | 0.046256 | 0.03787 | 0.22326 | 0 | 0.079116 | 0 | 0.19085 | 0.022572 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1511 | 0.5289% | CZ 7 | 10.2322 | 1.4847 | 3.8643 | 22.7815 | 0 | 2.5394 | 0 | 6.1259 | 0.72451 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 55.2127 | 0.5289% | CZ 7 | 2.9989 | 0.43515 | 0 | 0 | 0 | 0.74427 | 0 | 1.7954 | 0.21234 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.3725 | 0.5289% | CZ 7 | 0 | 0 | 0.038643 | 0.22781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26646 | 0.5289% | CZ 7 | 31.3955 | 4.5556 | 4.2237 | 24.9001 | 0 | 7.7917 | 0 | 18.796 | 2.223 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 116.7755 | 0.5289%
CZ 8 | 0.32456 | 0.047058 | 0.038961 | 0.33418 | 0 | 0.035754 | 0 | 0.21194 | 0.023314 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2482 | 0.05788% | CZ 8 | 10.4177 | 1.5105 | 3.9756 | 34.1002 | 0 | 1.1476 | 0 | 6.8028 | 0.74832 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 66.1628 | 0.05788% | CZ 8 | 3.0533 | 0.44269 | 0 | 0 | 0 | 0.33635 | 0 | 1.9938 | 0.21932 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.2318 | 0.05788% | CZ 8 | 0 | 0 | 0.039756 | 0.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38076 | 0.05788% | CZ 8 | 31.9645 | 4.6345 | 4.3453 | 37.2715 | 0 | 3.5212 | 0 | 20.873 | 2.2961 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 127.796 | 0.05788%
US Weighted | 0.28499 | 0.046105 | 0.034911 | 0.11616 | 0 | 0.21956 | 0 | 0.17285 | 0.00013288 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1071 | 100% | US Weighted | 9.1474 | 1.4799 | 3.5623 | 11.8533 | 0 | 7.0474 | 0 | 5.5482 | 0.0042652 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 46.1029 | 100% | US Weighted | 2.681 | 0.43372 | 0 | 0 | 0 | 2.0655 | 0 | 1.6261 | 0.0012501 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.9939 | 100% | US Weighted | 0 | 0 | 0.035623 | 0.11853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15416 | 100% | US Weighted | 28.067 | 4.5406 | 3.8936 | 12.9557 | 0 | 21.6233 | 0 | 17.0235 | 0.013087 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 111.0066 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.32522 | 0.046113 | 0.031418 | 0 | 0 | 0.83443 | 0 | 0.18733 | 0.031962 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.6889 | 0% | CZ 0A | 10.4388 | 1.4801 | 3.206 | 0 | 0 | 26.7835 | 0 | 6.013 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 56.4075 | 0% | CZ 0A | 3.0594 | 0.4338 | 0 | 0 | 0 | 7.8498 | 0 | 1.7623 | 0.30068 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 15.5925 | 0% | CZ 0A | 0 | 0 | 0.03206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03206 | 0% | CZ 0A | 32.0293 | 4.5414 | 3.5041 | 0 | 0 | 82.1796 | 0 | 18.4497 | 3.1478 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 166.7417 | 0%
CZ 0B | 0.33247 | 0.046089 | 0.031317 | 0 | 0 | 0.87439 | 0 | 0.21995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.7366 | 0% | CZ 0B | 10.6715 | 1.4794 | 3.1956 | 0 | 0 | 28.0659 | 0 | 7.0601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 57.9325 | 0% | CZ 0B | 3.1276 | 0.43357 | 0 | 0 | 0 | 8.2256 | 0 | 2.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 16.0425 | 0% | CZ 0B | 0 | 0 | 0.031956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031956 | 0% | CZ 0B | 32.7432 | 4.5391 | 3.4928 | 0 | 0 | 86.1143 | 0 | 21.6623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 171.4415 | 0%
CZ 1A | 0.3489 | 0.046089 | 0.032114 | 0 | 0 | 0.66035 | 0 | 0.17546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.4953 | 2.651% | CZ 1A | 11.199 | 1.4794 | 3.277 | 0 | 0 | 21.1959 | 0 | 5.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 50.2432 | 2.651% | CZ 1A | 3.2822 | 0.43357 | 0 | 0 | 0 | 6.2122 | 0 | 1.6506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 13.765 | 2.651% | CZ 1A | 0 | 0 | 0.03277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03277 | 2.651% | CZ 1A | 34.3618 | 4.5391 | 3.5817 | 0 | 0 | 65.0352 | 0 | 17.2799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 147.6875 | 2.651%
CZ 1B | 0.34573 | 0.046017 | 0.032107 | 0.0057894 | 0 | 0.70584 | 0 | 0.20816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.5761 | 0% | CZ 1B | 11.0973 | 1.4771 | 3.2762 | 0.59075 | 0 | 22.6561 | 0 | 6.6815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 53.239 | 0% | CZ 1B | 3.2524 | 0.4329 | 0 | 0 | 0 | 6.6401 | 0 | 1.9582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 14.4701 | 0% | CZ 1B | 0 | 0 | 0.032762 | 0.0059075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03867 | 0% | CZ 1B | 34.0497 | 4.532 | 3.5809 | 0.64569 | 0 | 69.5153 | 0 | 20.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 155.7141 | 0%
CZ 2A | 0.35077 | 0.045993 | 0.032931 | 0.0038596 | 0 | 0.46699 | 0 | 0.16013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2931 | 16.38% | CZ 2A | 11.2589 | 1.4763 | 3.3603 | 0.39384 | 0 | 14.9894 | 0 | 5.1399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 44.0787 | 16.38% | CZ 2A | 3.2998 | 0.43267 | 0 | 0 | 0 | 4.3931 | 0 | 1.5064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 11.8185 | 16.38% | CZ 2A | 0 | 0 | 0.033603 | 0.0039384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037541 | 16.38% | CZ 2A | 34.5456 | 4.5297 | 3.6728 | 0.43046 | 0 | 45.9917 | 0 | 15.7708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 127.8308 | 16.38%
CZ 2B | 0.36409 | 0.046041 | 0.032961 | 0.0022082 | 0 | 0.36002 | 0 | 0.17602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2138 | 2.81% | CZ 2B | 11.6866 | 1.4778 | 3.3633 | 0.22532 | 0 | 11.5557 | 0 | 5.6498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 41.4188 | 2.81% | CZ 2B | 3.4252 | 0.43312 | 0 | 0 | 0 | 3.3868 | 0 | 1.6559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 11.0874 | 2.81% | CZ 2B | 0 | 0 | 0.033633 | 0.0022532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035887 | 2.81% | CZ 2B | 35.858 | 4.5344 | 3.6761 | 0.24628 | 0 | 35.4563 | 0 | 17.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 119.9961 | 2.81%
CZ 3A | 0.35237 | 0.046029 | 0.034338 | 0.058259 | 0 | 0.25928 | 0 | 0.17408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1568 | 16.25% | CZ 3A | 11.3104 | 1.4774 | 3.5038 | 5.9448 | 0 | 8.3225 | 0 | 5.5876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.6066 | 16.25% | CZ 3A | 3.3149 | 0.43301 | 0 | 0 | 0 | 2.4392 | 0 | 1.6376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.0111 | 16.25% | CZ 3A | 0 | 0 | 0.035038 | 0.059448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094486 | 16.25% | CZ 3A | 34.7035 | 4.5332 | 3.8297 | 6.4976 | 0 | 25.5358 | 0 | 17.1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 115.134 | 16.25%
CZ 3B | 0.36248 | 0.046017 | 0.033965 | 0.017451 | 0 | 0.25303 | 0 | 0.18788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1332 | 7.8% | CZ 3B | 11.6348 | 1.4771 | 3.4658 | 1.7807 | 0 | 8.1217 | 0 | 6.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 39.9709 | 7.8% | CZ 3B | 3.41 | 0.4329 | 0 | 0 | 0 | 2.3803 | 0 | 1.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.1771 | 7.8% | CZ 3B | 0 | 0 | 0.034658 | 0.017807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052465 | 7.8% | CZ 3B | 35.6989 | 4.532 | 3.7882 | 1.9463 | 0 | 24.9196 | 0 | 18.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 112.2788 | 7.8%
CZ 3C | 0.36322 | 0.046173 | 0.034466 | 0.0020314 | 0 | 0.12235 | 0 | 0.17205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 0.9727 | 1.112% | CZ 3C | 11.6586 | 1.482 | 3.5169 | 0.20728 | 0 | 3.927 | 0 | 5.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 33.7743 | 1.112% | CZ 3C | 3.4169 | 0.43436 | 0 | 0 | 0 | 1.1509 | 0 | 1.6185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.8072 | 1.112% | CZ 3C | 0 | 0 | 0.035169 | 0.0020728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037242 | 1.112% | CZ 3C | 35.772 | 4.5473 | 3.844 | 0.22656 | 0 | 12.0493 | 0 | 16.9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 96.2731 | 1.112%
CZ 4A | 0.36095 | 0.046256 | 0.035451 | 0.13995 | 0 | 0.17146 | 0 | 0.18147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.168 | 17.53% | CZ 4A | 11.5857 | 1.4847 | 3.6175 | 14.281 | 0 | 5.5035 | 0 | 5.8249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 49.7574 | 17.53% | CZ 4A | 3.3956 | 0.43515 | 0 | 0 | 0 | 1.613 | 0 | 1.7072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.3373 | 17.53% | CZ 4A | 0 | 0 | 0.036175 | 0.14281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17898 | 17.53% | CZ 4A | 35.5482 | 4.5556 | 3.9539 | 15.6091 | 0 | 16.8864 | 0 | 17.8724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 117.3154 | 17.53%
CZ 4B | 0.3612 | 0.046017 | 0.035124 | 0.046725 | 0 | 0.17346 | 0 | 0.20163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.0966 | 0.7484% | CZ 4B | 11.5937 | 1.4771 | 3.5841 | 4.7679 | 0 | 5.5676 | 0 | 6.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 40.9223 | 0.7484% | CZ 4B | 3.3979 | 0.4329 | 0 | 0 | 0 | 1.6318 | 0 | 1.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.5458 | 0.7484% | CZ 4B | 0 | 0 | 0.035841 | 0.047679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083519 | 0.7484% | CZ 4B | 35.5729 | 4.532 | 3.9174 | 5.2113 | 0 | 17.0831 | 0 | 19.8575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 109.064 | 0.7484%
CZ 4C | 0.3663 | 0.046292 | 0.035782 | 0.09014 | 0 | 0.051759 | 0 | 0.16869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 0.99137 | 2.419% | CZ 4C | 11.7573 | 1.4859 | 3.6512 | 9.198 | 0 | 1.6613 | 0 | 5.4144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 40.6283 | 2.419% | CZ 4C | 3.4459 | 0.43549 | 0 | 0 | 0 | 0.48691 | 0 | 1.5869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.1416 | 2.419% | CZ 4C | 0 | 0 | 0.036512 | 0.09198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12849 | 2.419% | CZ 4C | 36.0747 | 4.5591 | 3.9908 | 10.0534 | 0 | 5.0975 | 0 | 16.6131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 99.2784 | 2.419%
CZ 5A | 0.36109 | 0.046101 | 0.03638 | 0.2205 | 0 | 0.099666 | 0 | 0.18704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1832 | 21.62% | CZ 5A | 11.5903 | 1.4797 | 3.7123 | 22.5005 | 0 | 3.1991 | 0 | 6.0034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 55.9454 | 21.62% | CZ 5A | 3.3969 | 0.43369 | 0 | 0 | 0 | 0.93759 | 0 | 1.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.7141 | 21.62% | CZ 5A | 0 | 0 | 0.037123 | 0.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26213 | 21.62% | CZ 5A | 35.5623 | 4.5403 | 4.0575 | 24.593 | 0 | 9.8156 | 0 | 18.4202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 119.8788 | 21.62%
CZ 5B | 0.36366 | 0.046197 | 0.036109 | 0.11927 | 0 | 0.1241 | 0 | 0.21018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1319 | 4.907% | CZ 5B | 11.6728 | 1.4828 | 3.6846 | 12.1702 | 0 | 3.9835 | 0 | 6.7464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.2004 | 4.907% | CZ 5B | 3.4211 | 0.43459 | 0 | 0 | 0 | 1.1675 | 0 | 1.9772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.1869 | 4.907% | CZ 5B | 0 | 0 | 0.036846 | 0.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15855 | 4.907% | CZ 5B | 35.8156 | 4.5497 | 4.0273 | 13.302 | 0 | 12.2224 | 0 | 20.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 113.5066 | 4.907%
CZ 5C | 0.36401 | 0.046244 | 0.036309 | 0.10494 | 0 | 0.024235 | 0 | 0.18328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 0.99144 | 0.1033% | CZ 5C | 11.684 | 1.4843 | 3.705 | 10.708 | 0 | 0.77788 | 0 | 5.8829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 41.7022 | 0.1033% | CZ 5C | 3.4244 | 0.43504 | 0 | 0 | 0 | 0.22798 | 0 | 1.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 7.998 | 0.1033% | CZ 5C | 0 | 0 | 0.03705 | 0.10708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14413 | 0.1033% | CZ 5C | 35.8497 | 4.5544 | 4.0495 | 11.7039 | 0 | 2.3868 | 0 | 18.0503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 99.4845 | 0.1033%
CZ 6A | 0.389 | 0.046173 | 0.037065 | 0.3051 | 0 | 0.11217 | 0 | 0.20397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.3259 | 4.509% | CZ 6A | 12.486 | 1.482 | 3.7821 | 31.1326 | 0 | 3.6003 | 0 | 6.5471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 66.4904 | 4.509% | CZ 6A | 3.6594 | 0.43436 | 0 | 0 | 0 | 1.0552 | 0 | 1.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.2543 | 4.509% | CZ 6A | 0 | 0 | 0.037821 | 0.31133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34915 | 4.509% | CZ 6A | 38.3107 | 4.5473 | 4.1339 | 34.028 | 0 | 11.0467 | 0 | 20.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 135.0448 | 4.509%
CZ 6B | 0.39029 | 0.046089 | 0.036892 | 0.20458 | 0 | 0.076197 | 0 | 0.20949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.196 | 0.5672% | CZ 6B | 12.5275 | 1.4794 | 3.7645 | 20.8752 | 0 | 2.4458 | 0 | 6.7241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 55.2765 | 0.5672% | CZ 6B | 3.6716 | 0.43357 | 0 | 0 | 0 | 0.71681 | 0 | 1.9707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.9791 | 0.5672% | CZ 6B | 0 | 0 | 0.037645 | 0.20875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2464 | 0.5672% | CZ 6B | 38.4379 | 4.5391 | 4.1146 | 22.8166 | 0 | 7.5043 | 0 | 20.6315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 120.9338 | 0.5672%
CZ 7 | 0.3852 | 0.046256 | 0.037866 | 0.21244 | 0 | 0.085635 | 0 | 0.20116 | 0.022058 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.223 | 0.5289% | CZ 7 | 12.3639 | 1.4847 | 3.8639 | 21.6779 | 0 | 2.7487 | 0 | 6.4569 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 56.7641 | 0.5289% | CZ 7 | 3.6237 | 0.43515 | 0 | 0 | 0 | 0.8056 | 0 | 1.8924 | 0.2075 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.1507 | 0.5289% | CZ 7 | 0 | 0 | 0.038639 | 0.21678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25542 | 0.5289% | CZ 7 | 37.9361 | 4.5556 | 4.2232 | 23.6939 | 0 | 8.4338 | 0 | 19.8115 | 2.1724 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 123.7163 | 0.5289%
CZ 8 | 0.39096 | 0.047058 | 0.038953 | 0.32217 | 0 | 0.040634 | 0 | 0.22251 | 0.022656 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.3174 | 0.05788% | CZ 8 | 12.549 | 1.5105 | 3.9748 | 32.8742 | 0 | 1.3043 | 0 | 7.1422 | 0.7272 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 67.5423 | 0.05788% | CZ 8 | 3.6779 | 0.44269 | 0 | 0 | 0 | 0.38226 | 0 | 2.0933 | 0.21313 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.9957 | 0.05788% | CZ 8 | 0 | 0 | 0.039748 | 0.32874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36849 | 0.05788% | CZ 8 | 38.5039 | 4.6345 | 4.3445 | 35.9315 | 0 | 4.0019 | 0 | 21.9144 | 2.2313 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 134.4518 | 0.05788%
US Weighted | 0.35968 | 0.046105 | 0.034907 | 0.10848 | 0 | 0.2336 | 0 | 0.18061 | 0.00012978 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1959 | 100% | US Weighted | 11.5448 | 1.4799 | 3.562 | 11.0693 | 0 | 7.498 | 0 | 5.7973 | 0.0041657 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 48.4156 | 100% | US Weighted | 3.3836 | 0.43372 | 0 | 0 | 0 | 2.1975 | 0 | 1.6991 | 0.0012209 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.9016 | 100% | US Weighted | 0 | 0 | 0.03562 | 0.11069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14631 | 100% | US Weighted | 35.4229 | 4.5406 | 3.8932 | 12.0987 | 0 | 23.0059 | 0 | 17.7879 | 0.012781 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 119.6519 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.40188 | 0.072226 | 0.031418 | 0 | 0 | 0.86454 | 0 | 0.1956 | 0.031962 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.83 | 0% | CZ 0A | 12.8995 | 2.3183 | 3.206 | 0 | 0 | 27.7499 | 0 | 6.2783 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 60.9381 | 0% | CZ 0A | 3.7806 | 0.67945 | 0 | 0 | 0 | 8.133 | 0 | 1.8401 | 0.30068 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 16.9203 | 0% | CZ 0A | 0 | 0 | 0.03206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03206 | 0% | CZ 0A | 39.5795 | 7.1132 | 3.5041 | 0 | 0 | 85.1447 | 0 | 19.2637 | 3.1478 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 180.6429 | 0%
CZ 0B | 0.41048 | 0.072214 | 0.031317 | 0 | 0 | 0.90626 | 0 | 0.22595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.8786 | 0% | CZ 0B | 13.1756 | 2.3179 | 3.1956 | 0 | 0 | 29.0891 | 0 | 7.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 62.4908 | 0% | CZ 0B | 3.8615 | 0.67934 | 0 | 0 | 0 | 8.5255 | 0 | 2.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 17.3784 | 0% | CZ 0B | 0 | 0 | 0.031956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031956 | 0% | CZ 0B | 40.4265 | 7.112 | 3.4928 | 0 | 0 | 89.2538 | 0 | 22.2525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 185.4275 | 0%
CZ 1A | 0.42988 | 0.072226 | 0.032114 | 0 | 0 | 0.62647 | 0 | 0.1768 | 0.031962 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.6019 | 2.651% | CZ 1A | 13.7984 | 2.3183 | 3.277 | 0 | 0 | 20.1082 | 0 | 5.6748 | 1.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 53.6626 | 2.651% | CZ 1A | 4.0441 | 0.67945 | 0 | 0 | 0 | 5.8934 | 0 | 1.6632 | 0.30068 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 14.7672 | 2.651% | CZ 1A | 0 | 0 | 0.03277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03277 | 2.651% | CZ 1A | 42.3373 | 7.1132 | 3.5817 | 0 | 0 | 61.6977 | 0 | 17.4118 | 3.1478 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 158.1794 | 2.651%
CZ 1B | 0.42616 | 0.072118 | 0.032107 | 0.0051273 | 0 | 0.73159 | 0 | 0.21482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.7143 | 0% | CZ 1B | 13.679 | 2.3148 | 3.2762 | 0.5232 | 0 | 23.4823 | 0 | 6.8953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 57.631 | 0% | CZ 1B | 4.0091 | 0.67844 | 0 | 0 | 0 | 6.8823 | 0 | 2.0209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 15.7771 | 0% | CZ 1B | 0 | 0 | 0.032762 | 0.005232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037994 | 0% | CZ 1B | 41.971 | 7.1026 | 3.5809 | 0.57185 | 0 | 72.0505 | 0 | 21.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 169.3235 | 0%
CZ 2A | 0.43212 | 0.072082 | 0.032927 | 0.0012188 | 0 | 0.44325 | 0 | 0.16409 | 0.024546 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.4027 | 16.38% | CZ 2A | 13.8702 | 2.3137 | 3.3599 | 0.12437 | 0 | 14.2272 | 0 | 5.267 | 0.78786 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.4103 | 16.38% | CZ 2A | 4.0651 | 0.6781 | 0 | 0 | 0 | 4.1698 | 0 | 1.5437 | 0.23091 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 12.874 | 16.38% | CZ 2A | 0 | 0 | 0.033599 | 0.0012437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034843 | 16.38% | CZ 2A | 42.5576 | 7.099 | 3.6724 | 0.13594 | 0 | 43.6532 | 0 | 16.1607 | 2.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 138.5862 | 16.38%
CZ 2B | 0.44786 | 0.072142 | 0.032961 | 0.0016401 | 0 | 0.37838 | 0 | 0.18424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.3496 | 2.81% | CZ 2B | 14.3754 | 2.3156 | 3.3633 | 0.16736 | 0 | 12.1451 | 0 | 5.9136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.7405 | 2.81% | CZ 2B | 4.2132 | 0.67866 | 0 | 0 | 0 | 3.5595 | 0 | 1.7332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 12.371 | 2.81% | CZ 2B | 0 | 0 | 0.033633 | 0.0016736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035307 | 2.81% | CZ 2B | 44.108 | 7.1049 | 3.6761 | 0.18293 | 0 | 37.2646 | 0 | 18.1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 133.371 | 2.81%
CZ 3A | 0.43401 | 0.07213 | 0.034334 | 0.02338 | 0 | 0.2636 | 0 | 0.16504 | 0.023038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.248 | 16.25% | CZ 3A | 13.9308 | 2.3152 | 3.5035 | 2.3857 | 0 | 8.4611 | 0 | 5.2973 | 0.73949 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 44.0932 | 16.25% | CZ 3A | 4.0829 | 0.67855 | 0 | 0 | 0 | 2.4798 | 0 | 1.5526 | 0.21673 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 11.197 | 16.25% | CZ 3A | 0 | 0 | 0.035035 | 0.023857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058891 | 16.25% | CZ 3A | 42.7438 | 7.1037 | 3.8293 | 2.6075 | 0 | 25.961 | 0 | 16.2538 | 2.269 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 123.6579 | 16.25%
CZ 3B | 0.44595 | 0.07213 | 0.033961 | 0.014694 | 0 | 0.26854 | 0 | 0.18121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2489 | 7.8% | CZ 3B | 14.314 | 2.3152 | 3.4655 | 1.4993 | 0 | 8.6197 | 0 | 5.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.4902 | 7.8% | CZ 3B | 4.1952 | 0.67855 | 0 | 0 | 0 | 2.5263 | 0 | 1.7047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 11.2912 | 7.8% | CZ 3B | 0 | 0 | 0.034655 | 0.014993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049648 | 7.8% | CZ 3B | 43.9195 | 7.1037 | 3.7877 | 1.6388 | 0 | 26.4476 | 0 | 17.8465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 123.6337 | 7.8%
CZ 3C | 0.44681 | 0.072249 | 0.034462 | 0.0014332 | 0 | 0.13446 | 0 | 0.18102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1029 | 1.112% | CZ 3C | 14.3416 | 2.3191 | 3.5165 | 0.14625 | 0 | 4.316 | 0 | 5.8103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 37.9099 | 1.112% | CZ 3C | 4.2033 | 0.67968 | 0 | 0 | 0 | 1.2649 | 0 | 1.7029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.0373 | 1.112% | CZ 3C | 0 | 0 | 0.035165 | 0.0014625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036628 | 1.112% | CZ 3C | 44.0043 | 7.1155 | 3.8435 | 0.15985 | 0 | 13.2426 | 0 | 17.8277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 109.0834 | 1.112%
CZ 4A | 0.44413 | 0.072285 | 0.035444 | 0.055204 | 0 | 0.18111 | 0 | 0.18279 | 0.023397 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2268 | 17.53% | CZ 4A | 14.2556 | 2.3202 | 3.6167 | 5.6331 | 0 | 5.8134 | 0 | 5.8671 | 0.751 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 45.7173 | 17.53% | CZ 4A | 4.1781 | 0.68001 | 0 | 0 | 0 | 1.7038 | 0 | 1.7196 | 0.22011 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.688 | 17.53% | CZ 4A | 0 | 0 | 0.036167 | 0.056331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092498 | 17.53% | CZ 4A | 43.7404 | 7.1191 | 3.953 | 6.157 | 0 | 17.8371 | 0 | 18.002 | 2.3043 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 122.0027 | 17.53%
CZ 4B | 0.44444 | 0.072106 | 0.035124 | 0.039743 | 0 | 0.18495 | 0 | 0.21036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2191 | 0.7484% | CZ 4B | 14.2656 | 2.3144 | 3.5841 | 4.0554 | 0 | 5.9366 | 0 | 6.7521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 44.3684 | 0.7484% | CZ 4B | 4.181 | 0.67832 | 0 | 0 | 0 | 1.7399 | 0 | 1.9789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.7646 | 0.7484% | CZ 4B | 0 | 0 | 0.035841 | 0.040554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076395 | 0.7484% | CZ 4B | 43.7711 | 7.1014 | 3.9174 | 4.4326 | 0 | 18.2153 | 0 | 20.7175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 121.045 | 0.7484%
CZ 4C | 0.45045 | 0.072273 | 0.035778 | 0.078509 | 0 | 0.057381 | 0 | 0.17771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.1045 | 2.419% | CZ 4C | 14.4584 | 2.3198 | 3.6509 | 8.0111 | 0 | 1.8418 | 0 | 5.7039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.446 | 2.419% | CZ 4C | 4.2375 | 0.6799 | 0 | 0 | 0 | 0.5398 | 0 | 1.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 9.3154 | 2.419% | CZ 4C | 0 | 0 | 0.036509 | 0.080111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11662 | 2.419% | CZ 4C | 44.3624 | 7.1179 | 3.9904 | 8.7561 | 0 | 5.6512 | 0 | 17.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 110.2692 | 2.419%
CZ 5A | 0.4443 | 0.072154 | 0.036373 | 0.10253 | 0 | 0.11602 | 0 | 0.18647 | 0.020515 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2108 | 21.62% | CZ 5A | 14.261 | 2.316 | 3.7115 | 10.462 | 0 | 3.7239 | 0 | 5.9854 | 0.65847 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 48.5784 | 21.62% | CZ 5A | 4.1797 | 0.67878 | 0 | 0 | 0 | 1.0914 | 0 | 1.7542 | 0.19299 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.0835 | 21.62% | CZ 5A | 0 | 0 | 0.037115 | 0.10462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14173 | 21.62% | CZ 5A | 43.7569 | 7.1061 | 4.0567 | 11.435 | 0 | 11.4261 | 0 | 18.3649 | 2.0204 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 121.0558 | 21.62%
CZ 5B | 0.44734 | 0.072238 | 0.036109 | 0.10945 | 0 | 0.13004 | 0 | 0.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2456 | 4.907% | CZ 5B | 14.3585 | 2.3187 | 3.6846 | 11.1679 | 0 | 4.1739 | 0 | 6.9975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 50.1613 | 4.907% | CZ 5B | 4.2082 | 0.67956 | 0 | 0 | 0 | 1.2233 | 0 | 2.0508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.3484 | 4.907% | CZ 5B | 0 | 0 | 0.036846 | 0.11168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14853 | 4.907% | CZ 5B | 44.0561 | 7.1143 | 4.0273 | 12.2065 | 0 | 12.8068 | 0 | 21.4703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 124.5712 | 4.907%
CZ 5C | 0.44774 | 0.072238 | 0.036309 | 0.093702 | 0 | 0.026232 | 0 | 0.17439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.083 | 0.1033% | CZ 5C | 14.3716 | 2.3187 | 3.705 | 9.5615 | 0 | 0.842 | 0 | 5.5976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 43.8564 | 0.1033% | CZ 5C | 4.2121 | 0.67956 | 0 | 0 | 0 | 0.24678 | 0 | 1.6406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 8.9654 | 0.1033% | CZ 5C | 0 | 0 | 0.03705 | 0.095615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13266 | 0.1033% | CZ 5C | 44.0962 | 7.1143 | 4.0495 | 10.4507 | 0 | 2.5835 | 0 | 17.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 108.3591 | 0.1033%
CZ 6A | 0.47727 | 0.072202 | 0.037057 | 0.16734 | 0 | 0.12646 | 0 | 0.20268 | 0.021723 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.3371 | 4.509% | CZ 6A | 15.3192 | 2.3175 | 3.7814 | 17.0751 | 0 | 4.0591 | 0 | 6.5056 | 0.69725 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 57.2153 | 4.509% | CZ 6A | 4.4898 | 0.67923 | 0 | 0 | 0 | 1.1897 | 0 | 1.9067 | 0.20435 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.6562 | 4.509% | CZ 6A | 0 | 0 | 0.037814 | 0.17075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20856 | 4.509% | CZ 6A | 47.0037 | 7.1108 | 4.133 | 18.663 | 0 | 12.4545 | 0 | 19.9612 | 2.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 134.3554 | 4.509%
CZ 6B | 0.4788 | 0.072118 | 0.036892 | 0.19351 | 0 | 0.08225 | 0 | 0.21818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.3142 | 0.5672% | CZ 6B | 15.3683 | 2.3148 | 3.7645 | 19.7456 | 0 | 2.64 | 0 | 7.0032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 58.2966 | 0.5672% | CZ 6B | 4.5042 | 0.67844 | 0 | 0 | 0 | 0.77375 | 0 | 2.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.1954 | 0.5672% | CZ 6B | 0 | 0 | 0.037645 | 0.19746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2351 | 0.5672% | CZ 6B | 47.1545 | 7.1026 | 4.1146 | 21.5819 | 0 | 8.1004 | 0 | 21.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 132.4316 | 0.5672%
CZ 7 | 0.47276 | 0.072238 | 0.037866 | 0.20498 | 0 | 0.092716 | 0 | 0.20944 | 0.021436 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.3438 | 0.5289% | CZ 7 | 15.1744 | 2.3187 | 3.8639 | 20.9159 | 0 | 2.976 | 0 | 6.7226 | 0.68804 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 60.1196 | 0.5289% | CZ 7 | 4.4474 | 0.67956 | 0 | 0 | 0 | 0.87221 | 0 | 1.9703 | 0.20165 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.3575 | 0.5289% | CZ 7 | 0 | 0 | 0.038639 | 0.20916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2478 | 0.5289% | CZ 7 | 46.5595 | 7.1143 | 4.2232 | 22.8611 | 0 | 9.1312 | 0 | 20.6268 | 2.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 135.5171 | 0.5289%
CZ 8 | 0.47957 | 0.072764 | 0.038953 | 0.31674 | 0 | 0.044103 | 0 | 0.23172 | 0.021998 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.4383 | 0.05788% | CZ 8 | 15.3933 | 2.3356 | 3.9748 | 32.3207 | 0 | 1.4156 | 0 | 7.4379 | 0.70608 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 71.044 | 0.05788% | CZ 8 | 4.5115 | 0.68451 | 0 | 0 | 0 | 0.41489 | 0 | 2.1799 | 0.20694 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 10.1842 | 0.05788% | CZ 8 | 0 | 0 | 0.039748 | 0.32321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36295 | 0.05788% | CZ 8 | 47.231 | 7.1662 | 4.3445 | 35.3265 | 0 | 4.3435 | 0 | 22.8215 | 2.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 146.2895 | 0.05788%
US Weighted | 0.44263 | 0.072171 | 0.034902 | 0.054628 | 0 | 0.23783 | 0 | 0.18045 | 0.018255 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23242 | 1.2733 | 100% | US Weighted | 14.2076 | 2.3165 | 3.5615 | 5.5743 | 0 | 7.6339 | 0 | 5.792 | 0.58596 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4601 | 47.1319 | 100% | US Weighted | 4.164 | 0.67894 | 0 | 0 | 0 | 2.2374 | 0 | 1.6975 | 0.17174 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1864 | 11.136 | 100% | US Weighted | 0 | 0 | 0.035615 | 0.055743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091358 | 100% | US Weighted | 43.5929 | 7.1078 | 3.8927 | 6.0927 | 0 | 23.4231 | 0 | 17.7714 | 1.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8898 | 126.5684 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.46768 | 0.072226 | 0.031418 | 0 | 0 | 1.1146 | 0 | 0.28243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 2.2012 | 0% | CZ 0A | 15.0116 | 2.3183 | 3.206 | 0 | 0 | 35.776 | 0 | 9.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 72.8501 | 0% | CZ 0A | 4.3997 | 0.67945 | 0 | 0 | 0 | 10.4853 | 0 | 2.6569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 20.4115 | 0% | CZ 0A | 0 | 0 | 0.03206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03206 | 0% | CZ 0A | 46.06 | 7.1132 | 3.5041 | 0 | 0 | 109.771 | 0 | 27.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 217.1924 | 0%
CZ 0B | 0.4779 | 0.072214 | 0.031317 | 9.7806e-05 | 0 | 0.96534 | 0 | 0.23761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 2.0173 | 0% | CZ 0B | 15.3395 | 2.3179 | 3.1956 | 0.0099803 | 0 | 30.9855 | 0 | 7.6268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 66.948 | 0% | CZ 0B | 4.4958 | 0.67934 | 0 | 0 | 0 | 9.0813 | 0 | 2.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 18.6818 | 0% | CZ 0B | 0 | 0 | 0.031956 | 9.9803e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032056 | 0% | CZ 0B | 47.0661 | 7.112 | 3.4928 | 0.010908 | 0 | 95.0723 | 0 | 23.4011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 199.0839 | 0%
CZ 1A | 0.50088 | 0.072226 | 0.032114 | 3.7618e-06 | 0 | 0.75363 | 0 | 0.24507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.8367 | 2.651% | CZ 1A | 16.0771 | 2.3183 | 3.277 | 0.00038386 | 0 | 24.1899 | 0 | 7.8663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 61.2018 | 2.651% | CZ 1A | 4.7119 | 0.67945 | 0 | 0 | 0 | 7.0897 | 0 | 2.3055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 16.9767 | 2.651% | CZ 1A | 0 | 0 | 0.03277 | 3.8386e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032774 | 2.651% | CZ 1A | 49.3292 | 7.1132 | 3.5817 | 0.00041955 | 0 | 74.2217 | 0 | 24.1362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 181.3111 | 2.651%
CZ 1B | 0.49649 | 0.072118 | 0.032111 | 0.0080088 | 0 | 0.77791 | 0 | 0.23109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.8505 | 0% | CZ 1B | 15.9362 | 2.3148 | 3.2766 | 0.81723 | 0 | 24.9694 | 0 | 7.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 62.2045 | 0% | CZ 1B | 4.6706 | 0.67844 | 0 | 0 | 0 | 7.3181 | 0 | 2.1739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 17.0313 | 0% | CZ 1B | 0 | 0 | 0.032766 | 0.0081723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040938 | 0% | CZ 1B | 48.8968 | 7.1026 | 3.5813 | 0.89323 | 0 | 76.6132 | 0 | 22.7591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 182.7749 | 0%
CZ 2A | 0.50127 | 0.072082 | 0.032931 | 0.0091148 | 0 | 0.52582 | 0 | 0.22495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.599 | 16.38% | CZ 2A | 16.0898 | 2.3137 | 3.3603 | 0.93008 | 0 | 16.8776 | 0 | 7.2205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 54.2648 | 16.38% | CZ 2A | 4.7156 | 0.6781 | 0 | 0 | 0 | 4.9466 | 0 | 2.1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 14.6467 | 16.38% | CZ 2A | 0 | 0 | 0.033603 | 0.0093008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042904 | 16.38% | CZ 2A | 49.368 | 7.099 | 3.6728 | 1.0166 | 0 | 51.7854 | 0 | 22.1547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 158.0253 | 16.38%
CZ 2B | 0.52014 | 0.072142 | 0.032961 | 0.0052402 | 0 | 0.40018 | 0 | 0.24065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.5041 | 2.81% | CZ 2B | 16.6953 | 2.3156 | 3.3633 | 0.53471 | 0 | 12.845 | 0 | 7.7243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 50.951 | 2.81% | CZ 2B | 4.8931 | 0.67866 | 0 | 0 | 0 | 3.7647 | 0 | 2.2639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 13.7904 | 2.81% | CZ 2B | 0 | 0 | 0.033633 | 0.0053471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038981 | 2.81% | CZ 2B | 51.2259 | 7.1049 | 3.6761 | 0.58444 | 0 | 39.4122 | 0 | 23.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 148.6326 | 2.81%
CZ 3A | 0.50288 | 0.07213 | 0.034338 | 0.061377 | 0 | 0.29588 | 0 | 0.22729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.4267 | 16.25% | CZ 3A | 16.1412 | 2.3152 | 3.5038 | 6.263 | 0 | 9.497 | 0 | 7.2954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 52.4885 | 16.25% | CZ 3A | 4.7307 | 0.67855 | 0 | 0 | 0 | 2.7834 | 0 | 2.1382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 12.521 | 16.25% | CZ 3A | 0 | 0 | 0.035038 | 0.06263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097668 | 16.25% | CZ 3A | 49.5259 | 7.1037 | 3.8297 | 6.8455 | 0 | 29.1395 | 0 | 22.3844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 141.7574 | 16.25%
CZ 3B | 0.51706 | 0.07213 | 0.033961 | 0.020833 | 0 | 0.28494 | 0 | 0.23981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.4016 | 7.8% | CZ 3B | 16.5966 | 2.3152 | 3.4655 | 2.1258 | 0 | 9.146 | 0 | 7.6974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 48.8193 | 7.8% | CZ 3B | 4.8642 | 0.67855 | 0 | 0 | 0 | 2.6806 | 0 | 2.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 12.6694 | 7.8% | CZ 3B | 0 | 0 | 0.034655 | 0.021258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055912 | 7.8% | CZ 3B | 50.9231 | 7.1037 | 3.7877 | 2.3235 | 0 | 28.0627 | 0 | 23.6179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 138.7474 | 7.8%
CZ 3C | 0.51758 | 0.072249 | 0.034458 | 0.0075198 | 0 | 0.14538 | 0 | 0.23131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.2413 | 1.112% | CZ 3C | 16.6131 | 2.3191 | 3.5161 | 0.76733 | 0 | 4.6665 | 0 | 7.4244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 42.7793 | 1.112% | CZ 3C | 4.869 | 0.67968 | 0 | 0 | 0 | 1.3677 | 0 | 2.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 11.2825 | 1.112% | CZ 3C | 0 | 0 | 0.035161 | 0.0076733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042834 | 1.112% | CZ 3C | 50.9738 | 7.1155 | 3.8431 | 0.83869 | 0 | 14.3182 | 0 | 22.7803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 122.7983 | 1.112%
CZ 4A | 0.49956 | 0.072285 | 0.035455 | 0.1545 | 0 | 0.1955 | 0 | 0.23999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.4301 | 17.53% | CZ 4A | 16.0349 | 2.3202 | 3.6178 | 15.7657 | 0 | 6.2753 | 0 | 7.7032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 59.1899 | 17.53% | CZ 4A | 4.6995 | 0.68001 | 0 | 0 | 0 | 1.8392 | 0 | 2.2577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 11.6666 | 17.53% | CZ 4A | 0 | 0 | 0.036178 | 0.15766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19384 | 17.53% | CZ 4A | 49.1996 | 7.1191 | 3.9543 | 17.2319 | 0 | 19.2543 | 0 | 23.6355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 143.3235 | 17.53%
CZ 4B | 0.50183 | 0.072106 | 0.035131 | 0.056513 | 0 | 0.20306 | 0 | 0.26491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.3664 | 0.7484% | CZ 4B | 16.1078 | 2.3144 | 3.5848 | 5.7667 | 0 | 6.5179 | 0 | 8.5029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 50.2674 | 0.7484% | CZ 4B | 4.7209 | 0.67832 | 0 | 0 | 0 | 1.9103 | 0 | 2.4921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 11.9918 | 0.7484% | CZ 4B | 0 | 0 | 0.035848 | 0.057667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.093515 | 0.7484% | CZ 4B | 49.4234 | 7.1014 | 3.9182 | 6.303 | 0 | 19.9989 | 0 | 26.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 135.763 | 0.7484%
CZ 4C | 0.50961 | 0.072273 | 0.035782 | 0.10312 | 0 | 0.059989 | 0 | 0.25479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.2684 | 2.419% | CZ 4C | 16.3574 | 2.3198 | 3.6512 | 10.5226 | 0 | 1.9255 | 0 | 8.1781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 50.4275 | 2.419% | CZ 4C | 4.7941 | 0.6799 | 0 | 0 | 0 | 0.56433 | 0 | 2.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 10.6253 | 2.419% | CZ 4C | 0 | 0 | 0.036512 | 0.10523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14174 | 2.419% | CZ 4C | 50.1892 | 7.1179 | 3.9908 | 11.5012 | 0 | 5.908 | 0 | 25.0928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 126.7286 | 2.419%
CZ 5A | 0.49962 | 0.072154 | 0.036388 | 0.24019 | 0 | 0.11342 | 0 | 0.24732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.4419 | 21.62% | CZ 5A | 16.0368 | 2.316 | 3.713 | 24.5088 | 0 | 3.6406 | 0 | 7.9385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 65.6266 | 21.62% | CZ 5A | 4.7001 | 0.67878 | 0 | 0 | 0 | 1.067 | 0 | 2.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 10.9627 | 21.62% | CZ 5A | 0 | 0 | 0.03713 | 0.24509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28222 | 21.62% | CZ 5A | 49.2055 | 7.1061 | 4.0584 | 26.7881 | 0 | 11.1704 | 0 | 24.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 145.6149 | 21.62%
CZ 5B | 0.50483 | 0.072238 | 0.036117 | 0.13279 | 0 | 0.13863 | 0 | 0.27391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.3913 | 4.907% | CZ 5B | 16.2038 | 2.3187 | 3.6854 | 13.5497 | 0 | 4.4496 | 0 | 8.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 56.472 | 4.907% | CZ 5B | 4.7491 | 0.67956 | 0 | 0 | 0 | 1.3041 | 0 | 2.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 11.4997 | 4.907% | CZ 5B | 0 | 0 | 0.036854 | 0.1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17235 | 4.907% | CZ 5B | 49.7179 | 7.1143 | 4.0281 | 14.8099 | 0 | 13.6526 | 0 | 26.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 139.2281 | 4.907%
CZ 5C | 0.50559 | 0.072238 | 0.036313 | 0.12564 | 0 | 0.026005 | 0 | 0.24956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.2482 | 0.1033% | CZ 5C | 16.2284 | 2.3187 | 3.7054 | 12.8208 | 0 | 0.83471 | 0 | 8.0103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 51.391 | 0.1033% | CZ 5C | 4.7563 | 0.67956 | 0 | 0 | 0 | 0.24464 | 0 | 2.3477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 10.2183 | 0.1033% | CZ 5C | 0 | 0 | 0.037054 | 0.12821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16526 | 0.1033% | CZ 5C | 49.7933 | 7.1143 | 4.05 | 14.0131 | 0 | 2.5611 | 0 | 24.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 125.0386 | 0.1033%
CZ 6A | 0.55209 | 0.072202 | 0.037069 | 0.32198 | 0 | 0.13109 | 0 | 0.27472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.622 | 4.509% | CZ 6A | 17.7208 | 2.3175 | 3.7825 | 32.8546 | 0 | 4.2077 | 0 | 8.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 77.1737 | 4.509% | CZ 6A | 5.1937 | 0.67923 | 0 | 0 | 0 | 1.2332 | 0 | 2.5843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 11.8806 | 4.509% | CZ 6A | 0 | 0 | 0.037825 | 0.32855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36637 | 4.509% | CZ 6A | 54.3725 | 7.1108 | 4.1343 | 35.9101 | 0 | 12.9104 | 0 | 27.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 164.4223 | 4.509%
CZ 6B | 0.55456 | 0.072118 | 0.036896 | 0.21795 | 0 | 0.090097 | 0 | 0.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.4904 | 0.5672% | CZ 6B | 17.8003 | 2.3148 | 3.7649 | 22.2398 | 0 | 2.8919 | 0 | 9.1798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 65.6643 | 0.5672% | CZ 6B | 5.217 | 0.67844 | 0 | 0 | 0 | 0.84757 | 0 | 2.6905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 11.6236 | 0.5672% | CZ 6B | 0 | 0 | 0.037649 | 0.2224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26005 | 0.5672% | CZ 6B | 54.6163 | 7.1026 | 4.115 | 24.3082 | 0 | 8.8732 | 0 | 28.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 150.1103 | 0.5672%
CZ 7 | 0.54623 | 0.072238 | 0.037877 | 0.3903 | 0 | 0.091687 | 0 | 0.3172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.6883 | 0.5289% | CZ 7 | 17.5326 | 2.3187 | 3.865 | 39.8262 | 0 | 2.943 | 0 | 10.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 84.1399 | 0.5289% | CZ 7 | 5.1385 | 0.67956 | 0 | 0 | 0 | 0.86253 | 0 | 2.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 11.8548 | 0.5289% | CZ 7 | 0 | 0 | 0.03865 | 0.39826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43691 | 0.5289% | CZ 7 | 53.7952 | 7.1143 | 4.2245 | 43.53 | 0 | 9.0299 | 0 | 31.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 171.8627 | 0.5289%
CZ 8 | 0.5599 | 0.072764 | 0.038976 | 0.58757 | 0 | 0.034893 | 0 | 0.39022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.9171 | 0.05788% | CZ 8 | 17.9715 | 2.3356 | 3.9771 | 59.956 | 0 | 1.12 | 0 | 12.5252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 105.3582 | 0.05788% | CZ 8 | 5.2671 | 0.68451 | 0 | 0 | 0 | 0.32825 | 0 | 3.6709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 12.141 | 0.05788% | CZ 8 | 0 | 0 | 0.039771 | 0.59956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63933 | 0.05788% | CZ 8 | 55.1418 | 7.1662 | 4.347 | 65.5319 | 0 | 3.4364 | 0 | 38.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 196.9828 | 0.05788%
US Weighted | 0.50606 | 0.072171 | 0.03491 | 0.12007 | 0 | 0.26481 | 0 | 0.24163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23281 | 1.4725 | 100% | US Weighted | 16.2434 | 2.3165 | 3.5622 | 12.2517 | 0 | 8.4999 | 0 | 7.7559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4728 | 58.1025 | 100% | US Weighted | 4.7607 | 0.67894 | 0 | 0 | 0 | 2.4912 | 0 | 2.2731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1902 | 12.3941 | 100% | US Weighted | 0 | 0 | 0.035622 | 0.12252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15814 | 100% | US Weighted | 49.8394 | 7.1078 | 3.8935 | 13.3911 | 0 | 26.0803 | 0 | 23.7972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9287 | 147.0381 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.58858 | 0.13782 | 0.032137 | 0 | 0 | 1.4637 | 0 | 0.54096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.9966 | 0% | CZ 0A | 18.8922 | 4.4239 | 3.2793 | 0 | 0 | 46.9804 | 0 | 17.3637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 98.4326 | 0% | CZ 0A | 5.537 | 1.2966 | 0 | 0 | 0 | 13.7692 | 0 | 5.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 27.8878 | 0% | CZ 0A | 0 | 0 | 0.032793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032793 | 0% | CZ 0A | 57.9668 | 13.5737 | 3.5843 | 0 | 0 | 144.1494 | 0 | 53.2769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 295.5421 | 0%
CZ 0B | 0.58858 | 0.13785 | 0.032009 | 9.0283e-05 | 0 | 1.3249 | 0 | 0.56283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.8797 | 0% | CZ 0B | 18.8922 | 4.4246 | 3.2662 | 0.0092125 | 0 | 42.5273 | 0 | 18.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 94.6783 | 0% | CZ 0B | 5.537 | 1.2968 | 0 | 0 | 0 | 12.4641 | 0 | 5.2947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 26.7887 | 0% | CZ 0B | 0 | 0 | 0.032662 | 9.2125e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032754 | 0% | CZ 0B | 57.9668 | 13.576 | 3.57 | 0.010069 | 0 | 130.4862 | 0 | 55.4304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 284.0305 | 0%
CZ 1A | 0.58858 | 0.13786 | 0.032833 | 3.7618e-06 | 0 | 1.0288 | 0 | 0.50205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.5236 | 2.651% | CZ 1A | 18.8922 | 4.425 | 3.3503 | 0.00038386 | 0 | 33.0223 | 0 | 16.1147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 83.2981 | 2.651% | CZ 1A | 5.537 | 1.2969 | 0 | 0 | 0 | 9.6783 | 0 | 4.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 23.4312 | 2.651% | CZ 1A | 0 | 0 | 0.033503 | 3.8386e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033507 | 2.651% | CZ 1A | 57.9668 | 13.5772 | 3.6619 | 0.00041955 | 0 | 101.322 | 0 | 49.4446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 248.964 | 2.651%
CZ 1B | 0.58858 | 0.13769 | 0.032807 | 0.0037392 | 0 | 1.0709 | 0 | 0.55568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.6228 | 0% | CZ 1B | 18.8922 | 4.4196 | 3.3476 | 0.38155 | 0 | 34.3723 | 0 | 17.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 86.7424 | 0% | CZ 1B | 5.537 | 1.2953 | 0 | 0 | 0 | 10.0739 | 0 | 5.2274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 24.3298 | 0% | CZ 1B | 0 | 0 | 0.033476 | 0.0038155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037292 | 0% | CZ 1B | 57.9668 | 13.5607 | 3.6589 | 0.41704 | 0 | 105.464 | 0 | 54.7259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 258.7845 | 0%
CZ 2A | 0.58858 | 0.13764 | 0.033649 | 0.0079449 | 0 | 0.78472 | 0 | 0.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.2527 | 16.38% | CZ 2A | 18.8922 | 4.4181 | 3.4336 | 0.8107 | 0 | 25.1878 | 0 | 14.9802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 75.2157 | 16.38% | CZ 2A | 5.537 | 1.2949 | 0 | 0 | 0 | 7.3821 | 0 | 4.3904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 20.8005 | 16.38% | CZ 2A | 0 | 0 | 0.034336 | 0.008107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042443 | 16.38% | CZ 2A | 57.9668 | 13.556 | 3.7529 | 0.8861 | 0 | 77.2835 | 0 | 45.9634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 222.3999 | 16.38%
CZ 2B | 0.58858 | 0.13774 | 0.033668 | 0.0038483 | 0 | 0.62083 | 0 | 0.50261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.1207 | 2.81% | CZ 2B | 18.8922 | 4.4212 | 3.4355 | 0.39268 | 0 | 19.9273 | 0 | 16.1328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 70.6948 | 2.81% | CZ 2B | 5.537 | 1.2958 | 0 | 0 | 0 | 5.8404 | 0 | 4.7282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 19.5975 | 2.81% | CZ 2B | 0 | 0 | 0.034355 | 0.0039268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038282 | 2.81% | CZ 2B | 57.9668 | 13.5654 | 3.755 | 0.4292 | 0 | 61.1428 | 0 | 49.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 209.3504 | 2.81%
CZ 3A | 0.58858 | 0.13772 | 0.035075 | 0.051322 | 0 | 0.46886 | 0 | 0.46935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.9843 | 16.25% | CZ 3A | 18.8922 | 4.4204 | 3.5791 | 5.2369 | 0 | 15.0493 | 0 | 15.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 69.7361 | 16.25% | CZ 3A | 5.537 | 1.2955 | 0 | 0 | 0 | 4.4107 | 0 | 4.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 17.8546 | 16.25% | CZ 3A | 0 | 0 | 0.035791 | 0.052369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08816 | 16.25% | CZ 3A | 57.9668 | 13.5631 | 3.9119 | 5.724 | 0 | 46.1755 | 0 | 46.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 196.5562 | 16.25%
CZ 3B | 0.58858 | 0.13772 | 0.034676 | 0.011105 | 0 | 0.40455 | 0 | 0.51149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.9216 | 7.8% | CZ 3B | 18.8922 | 4.4204 | 3.5384 | 1.1331 | 0 | 12.9852 | 0 | 16.4177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 64.8801 | 7.8% | CZ 3B | 5.537 | 1.2955 | 0 | 0 | 0 | 3.8057 | 0 | 4.8117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 17.6461 | 7.8% | CZ 3B | 0 | 0 | 0.035384 | 0.011331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046715 | 7.8% | CZ 3B | 57.9668 | 13.5631 | 3.8675 | 1.2385 | 0 | 39.8422 | 0 | 50.3741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 189.8433 | 7.8%
CZ 3C | 0.58858 | 0.13769 | 0.03518 | 0.0065154 | 0 | 0.19427 | 0 | 0.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.6411 | 1.112% | CZ 3C | 18.8922 | 4.4196 | 3.5898 | 0.66484 | 0 | 6.2357 | 0 | 14.2963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 55.5917 | 1.112% | CZ 3C | 5.537 | 1.2953 | 0 | 0 | 0 | 1.8276 | 0 | 4.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 15.046 | 1.112% | CZ 3C | 0 | 0 | 0.035898 | 0.0066484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042547 | 1.112% | CZ 3C | 57.9668 | 13.5607 | 3.9237 | 0.72667 | 0 | 19.133 | 0 | 43.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 162.1672 | 1.112%
CZ 4A | 0.58858 | 0.1375 | 0.036211 | 0.13905 | 0 | 0.30584 | 0 | 0.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.9069 | 17.53% | CZ 4A | 18.8922 | 4.4135 | 3.695 | 14.1889 | 0 | 9.8168 | 0 | 14.9671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 73.4666 | 17.53% | CZ 4A | 5.537 | 1.2935 | 0 | 0 | 0 | 2.8771 | 0 | 4.3866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.2904 | 17.53% | CZ 4A | 0 | 0 | 0.03695 | 0.14189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17884 | 17.53% | CZ 4A | 57.9668 | 13.5419 | 4.0386 | 15.5084 | 0 | 30.1208 | 0 | 45.9234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 190.091 | 17.53%
CZ 4B | 0.58858 | 0.13761 | 0.035869 | 0.03582 | 0 | 0.26531 | 0 | 0.53559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.8322 | 0.7484% | CZ 4B | 18.8922 | 4.4169 | 3.6601 | 3.6551 | 0 | 8.516 | 0 | 17.1913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 63.8248 | 0.7484% | CZ 4B | 5.537 | 1.2945 | 0 | 0 | 0 | 2.4959 | 0 | 5.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.562 | 0.7484% | CZ 4B | 0 | 0 | 0.036601 | 0.036551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073151 | 0.7484% | CZ 4B | 57.9668 | 13.5525 | 4.0005 | 3.995 | 0 | 26.1295 | 0 | 52.7479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 181.3833 | 0.7484%
CZ 4C | 0.58858 | 0.13735 | 0.036534 | 0.078967 | 0 | 0.07823 | 0 | 0.44457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.5977 | 2.419% | CZ 4C | 18.8922 | 4.4085 | 3.728 | 8.0579 | 0 | 2.511 | 0 | 14.2698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 59.3607 | 2.419% | CZ 4C | 5.537 | 1.2921 | 0 | 0 | 0 | 0.73594 | 0 | 4.1823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 13.9434 | 2.419% | CZ 4C | 0 | 0 | 0.03728 | 0.080579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11786 | 2.419% | CZ 4C | 57.9668 | 13.5266 | 4.0747 | 8.8073 | 0 | 7.7046 | 0 | 43.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 158.855 | 2.419%
CZ 5A | 0.58858 | 0.13755 | 0.037148 | 0.21422 | 0 | 0.19016 | 0 | 0.4637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.8648 | 21.62% | CZ 5A | 18.8922 | 4.415 | 3.7906 | 21.8587 | 0 | 6.1036 | 0 | 14.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 77.4371 | 21.62% | CZ 5A | 5.537 | 1.294 | 0 | 0 | 0 | 1.7889 | 0 | 4.3622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 15.1781 | 21.62% | CZ 5A | 0 | 0 | 0.037906 | 0.21859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25649 | 21.62% | CZ 5A | 57.9668 | 13.5466 | 4.1431 | 23.8915 | 0 | 18.7277 | 0 | 45.6677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 186.9346 | 21.62%
CZ 5B | 0.58858 | 0.13755 | 0.036869 | 0.099796 | 0 | 0.24073 | 0 | 0.53204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.869 | 4.907% | CZ 5B | 18.8922 | 4.415 | 3.7622 | 10.1833 | 0 | 7.727 | 0 | 17.0773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 69.5501 | 4.907% | CZ 5B | 5.537 | 1.294 | 0 | 0 | 0 | 2.2646 | 0 | 5.0051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.2968 | 4.907% | CZ 5B | 0 | 0 | 0.037622 | 0.10183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13945 | 4.907% | CZ 5B | 57.9668 | 13.5466 | 4.1121 | 11.1304 | 0 | 23.7086 | 0 | 52.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 185.8535 | 4.907%
CZ 5C | 0.58858 | 0.13733 | 0.037065 | 0.091995 | 0 | 0.034019 | 0 | 0.43122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.5537 | 0.1033% | CZ 5C | 18.8922 | 4.4081 | 3.7821 | 9.3872 | 0 | 1.092 | 0 | 13.8414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 58.8961 | 0.1033% | CZ 5C | 5.537 | 1.2919 | 0 | 0 | 0 | 0.32003 | 0 | 4.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 13.4018 | 0.1033% | CZ 5C | 0 | 0 | 0.037821 | 0.093872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13169 | 0.1033% | CZ 5C | 57.9668 | 13.5254 | 4.1339 | 10.2602 | 0 | 3.3504 | 0 | 42.4693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 154.6971 | 0.1033%
CZ 6A | 0.58858 | 0.13749 | 0.037836 | 0.31532 | 0 | 0.2059 | 0 | 0.49573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.0143 | 4.509% | CZ 6A | 18.8922 | 4.4131 | 3.8608 | 32.1752 | 0 | 6.6089 | 0 | 15.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 89.3554 | 4.509% | CZ 6A | 5.537 | 1.2934 | 0 | 0 | 0 | 1.937 | 0 | 4.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 15.627 | 4.509% | CZ 6A | 0 | 0 | 0.038608 | 0.32175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36036 | 4.509% | CZ 6A | 57.9668 | 13.5407 | 4.2199 | 35.1675 | 0 | 20.2781 | 0 | 48.8226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 202.9866 | 4.509%
CZ 6B | 0.58858 | 0.13738 | 0.037659 | 0.19451 | 0 | 0.164 | 0 | 0.51875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.8743 | 0.5672% | CZ 6B | 18.8922 | 4.4097 | 3.8428 | 19.848 | 0 | 5.2639 | 0 | 16.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 76.4005 | 0.5672% | CZ 6B | 5.537 | 1.2924 | 0 | 0 | 0 | 1.5428 | 0 | 4.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 15.4483 | 0.5672% | CZ 6B | 0 | 0 | 0.038428 | 0.19848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23691 | 0.5672% | CZ 6B | 57.9668 | 13.5301 | 4.2002 | 21.6939 | 0 | 16.1513 | 0 | 51.0892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 187.6226 | 0.5672%
CZ 7 | 0.58858 | 0.1373 | 0.038649 | 0.37709 | 0 | 0.16165 | 0 | 0.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.0672 | 0.5289% | CZ 7 | 18.8922 | 4.407 | 3.9437 | 38.4785 | 0 | 5.1887 | 0 | 17.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 95.431 | 0.5289% | CZ 7 | 5.537 | 1.2916 | 0 | 0 | 0 | 1.5207 | 0 | 4.9905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 15.536 | 0.5289% | CZ 7 | 0 | 0 | 0.039437 | 0.38478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42422 | 0.5289% | CZ 7 | 57.9668 | 13.5218 | 4.3105 | 42.057 | 0 | 15.9204 | 0 | 52.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 209.0137 | 0.5289%
CZ 8 | 0.58858 | 0.13654 | 0.039755 | 0.57549 | 0 | 0.088446 | 0 | 0.56371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.226 | 0.05788% | CZ 8 | 18.8922 | 4.3828 | 4.0566 | 58.7238 | 0 | 2.8389 | 0 | 18.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 114.4814 | 0.05788% | CZ 8 | 5.537 | 1.2845 | 0 | 0 | 0 | 0.83204 | 0 | 5.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 15.1527 | 0.05788% | CZ 8 | 0 | 0 | 0.040566 | 0.58724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6278 | 0.05788% | CZ 8 | 57.9668 | 13.4476 | 4.4339 | 64.1851 | 0 | 8.7106 | 0 | 55.5176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 227.2527 | 0.05788%
US Weighted | 0.58858 | 0.1376 | 0.035652 | 0.1062 | 0 | 0.40476 | 0 | 0.47676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.983 | 100% | US Weighted | 18.8922 | 4.4167 | 3.638 | 10.8372 | 0 | 12.9919 | 0 | 15.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 73.5721 | 100% | US Weighted | 5.537 | 1.2945 | 0 | 0 | 0 | 3.8077 | 0 | 4.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 17.3203 | 100% | US Weighted | 0 | 0 | 0.03638 | 0.10837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14475 | 100% | US Weighted | 57.9668 | 13.5518 | 3.9763 | 11.845 | 0 | 39.8629 | 0 | 46.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 197.148 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 24692 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.58858 | 0.13782 | 0.032137 | 0 | 0 | 1.6209 | 0 | 0.57772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 3.1906 | 0% | CZ 0A | 18.8922 | 4.4239 | 3.2793 | 0 | 0 | 52.0278 | 0 | 18.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 104.6599 | 0% | CZ 0A | 5.537 | 1.2966 | 0 | 0 | 0 | 15.2485 | 0 | 5.4348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 29.713 | 0% | CZ 0A | 0 | 0 | 0.032793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032793 | 0% | CZ 0A | 57.9668 | 13.5737 | 3.5843 | 0 | 0 | 159.6362 | 0 | 56.8971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 314.6491 | 0%
CZ 0B | 0.58858 | 0.13785 | 0.032009 | 9.0283e-05 | 0 | 1.3986 | 0 | 0.56283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.9534 | 0% | CZ 0B | 18.8922 | 4.4246 | 3.2662 | 0.0092125 | 0 | 44.8906 | 0 | 18.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 97.0416 | 0% | CZ 0B | 5.537 | 1.2968 | 0 | 0 | 0 | 13.1567 | 0 | 5.2947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 27.4813 | 0% | CZ 0B | 0 | 0 | 0.032662 | 9.2125e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032754 | 0% | CZ 0B | 57.9668 | 13.576 | 3.57 | 0.010069 | 0 | 137.7372 | 0 | 55.4304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 291.2815 | 0%
CZ 1A | 0.58858 | 0.13786 | 0.032833 | 3.7618e-06 | 0 | 1.0943 | 0 | 0.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.622 | 2.651% | CZ 1A | 18.8922 | 4.425 | 3.3503 | 0.00038386 | 0 | 35.126 | 0 | 17.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 86.4561 | 2.651% | CZ 1A | 5.537 | 1.2969 | 0 | 0 | 0 | 10.2948 | 0 | 5.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 24.3568 | 2.651% | CZ 1A | 0 | 0 | 0.033503 | 3.8386e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033507 | 2.651% | CZ 1A | 57.9668 | 13.5772 | 3.6619 | 0.00041955 | 0 | 107.7766 | 0 | 52.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 258.6536 | 2.651%
CZ 1B | 0.58858 | 0.13769 | 0.03281 | 0.0052364 | 0 | 1.1279 | 0 | 0.55571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.6814 | 0% | CZ 1B | 18.8922 | 4.4196 | 3.348 | 0.53433 | 0 | 36.2029 | 0 | 17.8371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 88.7274 | 0% | CZ 1B | 5.537 | 1.2953 | 0 | 0 | 0 | 10.6105 | 0 | 5.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 24.8667 | 0% | CZ 1B | 0 | 0 | 0.03348 | 0.0053433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038823 | 0% | CZ 1B | 57.9668 | 13.5607 | 3.6594 | 0.58402 | 0 | 111.0811 | 0 | 54.7294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 264.5725 | 0%
CZ 2A | 0.58858 | 0.13764 | 0.033676 | 0.018865 | 0 | 0.9349 | 0 | 0.55173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.4988 | 16.38% | CZ 2A | 18.8922 | 4.4181 | 3.4363 | 1.925 | 0 | 30.0083 | 0 | 17.7093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 83.8823 | 16.38% | CZ 2A | 5.537 | 1.2949 | 0 | 0 | 0 | 8.7949 | 0 | 5.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 23.0132 | 16.38% | CZ 2A | 0 | 0 | 0.034363 | 0.01925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053613 | 16.38% | CZ 2A | 57.9668 | 13.556 | 3.7559 | 2.1041 | 0 | 92.0741 | 0 | 54.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 246.7851 | 16.38%
CZ 2B | 0.58858 | 0.13774 | 0.033687 | 0.011075 | 0 | 0.72111 | 0 | 0.58106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.3067 | 2.81% | CZ 2B | 18.8922 | 4.4212 | 3.4374 | 1.1301 | 0 | 23.146 | 0 | 18.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 77.1707 | 2.81% | CZ 2B | 5.537 | 1.2958 | 0 | 0 | 0 | 6.7837 | 0 | 5.4662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 21.2788 | 2.81% | CZ 2B | 0 | 0 | 0.034374 | 0.011301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045675 | 2.81% | CZ 2B | 57.9668 | 13.5654 | 3.7571 | 1.2352 | 0 | 71.0186 | 0 | 57.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 227.7599 | 2.81%
CZ 3A | 0.58858 | 0.13772 | 0.035086 | 0.086698 | 0 | 0.50163 | 0 | 0.51779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.101 | 16.25% | CZ 3A | 18.8922 | 4.4204 | 3.5802 | 8.8467 | 0 | 16.1013 | 0 | 16.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 75.954 | 16.25% | CZ 3A | 5.537 | 1.2955 | 0 | 0 | 0 | 4.719 | 0 | 4.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 18.6187 | 16.25% | CZ 3A | 0 | 0 | 0.035802 | 0.088467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12427 | 16.25% | CZ 3A | 57.9668 | 13.5631 | 3.9132 | 9.6695 | 0 | 49.4034 | 0 | 50.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 208.502 | 16.25%
CZ 3B | 0.58858 | 0.13772 | 0.034691 | 0.023884 | 0 | 0.43772 | 0 | 0.53551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.9915 | 7.8% | CZ 3B | 18.8922 | 4.4204 | 3.5399 | 2.4371 | 0 | 14.0498 | 0 | 17.1886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.0213 | 7.8% | CZ 3B | 5.537 | 1.2955 | 0 | 0 | 0 | 4.1178 | 0 | 5.0377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 18.1841 | 7.8% | CZ 3B | 0 | 0 | 0.035399 | 0.024371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05977 | 7.8% | CZ 3B | 57.9668 | 13.5631 | 3.8691 | 2.6638 | 0 | 43.109 | 0 | 52.7397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 196.9025 | 7.8%
CZ 3C | 0.58858 | 0.13769 | 0.035195 | 0.010089 | 0 | 0.2229 | 0 | 0.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.7304 | 1.112% | CZ 3C | 18.8922 | 4.4196 | 3.5914 | 1.0295 | 0 | 7.1545 | 0 | 16.1293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 58.7097 | 1.112% | CZ 3C | 5.537 | 1.2953 | 0 | 0 | 0 | 2.0969 | 0 | 4.7272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 15.8525 | 1.112% | CZ 3C | 0 | 0 | 0.035914 | 0.010295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046209 | 1.112% | CZ 3C | 57.9668 | 13.5607 | 3.9254 | 1.1252 | 0 | 21.9521 | 0 | 49.4894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 171.0107 | 1.112%
CZ 4A | 0.58858 | 0.1375 | 0.03623 | 0.23762 | 0 | 0.32106 | 0 | 0.5182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.0726 | 17.53% | CZ 4A | 18.8922 | 4.4135 | 3.6969 | 24.2474 | 0 | 10.3052 | 0 | 16.6331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 85.6814 | 17.53% | CZ 4A | 5.537 | 1.2935 | 0 | 0 | 0 | 3.0203 | 0 | 4.8749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.9218 | 17.53% | CZ 4A | 0 | 0 | 0.036969 | 0.24247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27944 | 17.53% | CZ 4A | 57.9668 | 13.5419 | 4.0407 | 26.5024 | 0 | 31.6193 | 0 | 51.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 207.6972 | 17.53%
CZ 4B | 0.58858 | 0.13761 | 0.035891 | 0.079197 | 0 | 0.28283 | 0 | 0.56578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.9233 | 0.7484% | CZ 4B | 18.8922 | 4.4169 | 3.6624 | 8.0813 | 0 | 9.0781 | 0 | 18.1604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 69.7845 | 0.7484% | CZ 4B | 5.537 | 1.2945 | 0 | 0 | 0 | 2.6606 | 0 | 5.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 17.0108 | 0.7484% | CZ 4B | 0 | 0 | 0.036624 | 0.080813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11744 | 0.7484% | CZ 4B | 57.9668 | 13.5525 | 4.003 | 8.8329 | 0 | 27.8542 | 0 | 55.7214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 190.9218 | 0.7484%
CZ 4C | 0.58858 | 0.13735 | 0.036565 | 0.15253 | 0 | 0.078422 | 0 | 0.49083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.7177 | 2.419% | CZ 4C | 18.8922 | 4.4085 | 3.7311 | 15.5642 | 0 | 2.5172 | 0 | 15.7546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 68.3609 | 2.419% | CZ 4C | 5.537 | 1.2921 | 0 | 0 | 0 | 0.73774 | 0 | 4.6174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 14.3803 | 2.419% | CZ 4C | 0 | 0 | 0.037311 | 0.15564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19295 | 2.419% | CZ 4C | 57.9668 | 13.5266 | 4.0781 | 17.0117 | 0 | 7.7234 | 0 | 48.3396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 171.6372 | 2.419%
CZ 5A | 0.58858 | 0.13755 | 0.037166 | 0.32268 | 0 | 0.19668 | 0 | 0.56106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.0772 | 21.62% | CZ 5A | 18.8922 | 4.415 | 3.7925 | 32.9268 | 0 | 6.3129 | 0 | 18.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 91.8413 | 21.62% | CZ 5A | 5.537 | 1.294 | 0 | 0 | 0 | 1.8502 | 0 | 5.2781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.1553 | 21.62% | CZ 5A | 0 | 0 | 0.037925 | 0.32927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36719 | 21.62% | CZ 5A | 57.9668 | 13.5466 | 4.1452 | 35.989 | 0 | 19.3698 | 0 | 55.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 209.2644 | 21.62%
CZ 5B | 0.58858 | 0.13755 | 0.036888 | 0.16909 | 0 | 0.24552 | 0 | 0.60002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.0111 | 4.907% | CZ 5B | 18.8922 | 4.415 | 3.7641 | 17.2539 | 0 | 7.8806 | 0 | 19.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 78.9582 | 4.907% | CZ 5B | 5.537 | 1.294 | 0 | 0 | 0 | 2.3097 | 0 | 5.6446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.9813 | 4.907% | CZ 5B | 0 | 0 | 0.037641 | 0.17254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21018 | 4.907% | CZ 5B | 57.9668 | 13.5466 | 4.1142 | 18.8586 | 0 | 24.1798 | 0 | 59.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 200.75 | 4.907%
CZ 5C | 0.58858 | 0.13733 | 0.037099 | 0.17587 | 0 | 0.033362 | 0 | 0.48169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 1.6874 | 0.1033% | CZ 5C | 18.8922 | 4.4081 | 3.7856 | 17.9456 | 0 | 1.0708 | 0 | 15.4612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 69.0568 | 0.1033% | CZ 5C | 5.537 | 1.2919 | 0 | 0 | 0 | 0.31384 | 0 | 4.5314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 13.8703 | 0.1033% | CZ 5C | 0 | 0 | 0.037856 | 0.17946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21731 | 0.1033% | CZ 5C | 57.9668 | 13.5254 | 4.1376 | 19.6146 | 0 | 3.2856 | 0 | 47.4396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 168.9607 | 0.1033%
CZ 6A | 0.58858 | 0.13749 | 0.037855 | 0.45627 | 0 | 0.20968 | 0 | 0.60602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.2693 | 4.509% | CZ 6A | 18.8922 | 4.4131 | 3.8627 | 46.5587 | 0 | 6.7302 | 0 | 19.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 107.4021 | 4.509% | CZ 6A | 5.537 | 1.2934 | 0 | 0 | 0 | 1.9725 | 0 | 5.7011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.7001 | 4.509% | CZ 6A | 0 | 0 | 0.038627 | 0.46559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50421 | 4.509% | CZ 6A | 57.9668 | 13.5407 | 4.222 | 50.8886 | 0 | 20.6503 | 0 | 59.6844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 229.9439 | 4.509%
CZ 6B | 0.58858 | 0.13738 | 0.037682 | 0.29524 | 0 | 0.16212 | 0 | 0.64093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.0954 | 0.5672% | CZ 6B | 18.8922 | 4.4097 | 3.8451 | 30.1262 | 0 | 5.2037 | 0 | 20.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 90.5423 | 0.5672% | CZ 6B | 5.537 | 1.2924 | 0 | 0 | 0 | 1.5251 | 0 | 6.0294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.58 | 0.5672% | CZ 6B | 0 | 0 | 0.038451 | 0.30126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33971 | 0.5672% | CZ 6B | 57.9668 | 13.5301 | 4.2027 | 32.9279 | 0 | 15.9663 | 0 | 63.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 210.7069 | 0.5672%
CZ 7 | 0.58858 | 0.1373 | 0.038667 | 0.56311 | 0 | 0.15403 | 0 | 0.62736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.3425 | 0.5289% | CZ 7 | 18.8922 | 4.407 | 3.9457 | 57.4605 | 0 | 4.9441 | 0 | 20.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 117.2796 | 0.5289% | CZ 7 | 5.537 | 1.2916 | 0 | 0 | 0 | 1.449 | 0 | 5.9018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.3756 | 0.5289% | CZ 7 | 0 | 0 | 0.039457 | 0.57461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61406 | 0.5289% | CZ 7 | 57.9668 | 13.5218 | 4.3126 | 62.8044 | 0 | 15.17 | 0 | 61.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 238.5527 | 0.5289%
CZ 8 | 0.58858 | 0.13654 | 0.039762 | 0.75466 | 0 | 0.077812 | 0 | 0.68631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.5171 | 0.05788% | CZ 8 | 18.8922 | 4.3828 | 4.0574 | 77.0057 | 0 | 2.4976 | 0 | 22.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 136.3579 | 0.05788% | CZ 8 | 5.537 | 1.2845 | 0 | 0 | 0 | 0.732 | 0 | 6.4564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 16.206 | 0.05788% | CZ 8 | 0 | 0 | 0.040574 | 0.77006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81063 | 0.05788% | CZ 8 | 57.9668 | 13.4476 | 4.4347 | 84.1673 | 0 | 7.6633 | 0 | 67.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 258.2624 | 0.05788%
US Weighted | 0.58858 | 0.1376 | 0.03567 | 0.16932 | 0 | 0.44671 | 0 | 0.54528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23345 | 2.1566 | 100% | US Weighted | 18.8922 | 4.4167 | 3.6398 | 17.2778 | 0 | 14.3384 | 0 | 17.5023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4931 | 83.5604 | 100% | US Weighted | 5.537 | 1.2945 | 0 | 0 | 0 | 4.2023 | 0 | 5.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1961 | 18.3596 | 100% | US Weighted | 0 | 0 | 0.036398 | 0.17278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20918 | 100% | US Weighted | 57.9668 | 13.5518 | 3.9783 | 18.8846 | 0 | 43.9944 | 0 | 53.7021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9911 | 215.0691 | 100%
Building Type: | Standalone Retail |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 24692 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 24692 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.33364 | 0.091711 | 0.0007185 | 0 | 0 | 0.66528 | 0 | 0.37432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.4667 | 0% | CZ 0A | 10.7091 | 2.9437 | 0.073316 | 0 | 0 | 21.3541 | 0 | 12.0149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 47.1282 | 0% | CZ 0A | 3.1387 | 0.86276 | 0 | 0 | 0 | 6.2585 | 0 | 3.5214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 13.791 | 0% | CZ 0A | 0 | 0 | 0.00073316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00073316 | 0% | CZ 0A | 32.8586 | 9.0322 | 0.080135 | 0 | 0 | 65.5205 | 0 | 36.8652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 144.4581 | 0%
CZ 0B | 0.32896 | 0.091759 | 0.00069217 | 8.6521e-05 | 0 | 0.55131 | 0 | 0.34951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.3234 | 0% | CZ 0B | 10.559 | 2.9453 | 0.070629 | 0.0088287 | 0 | 17.6958 | 0 | 11.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 42.5312 | 0% | CZ 0B | 3.0947 | 0.86321 | 0 | 0 | 0 | 5.1864 | 0 | 3.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 12.4419 | 0% | CZ 0B | 0 | 0 | 0.00070629 | 8.8287e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00079458 | 0% | CZ 0B | 32.398 | 9.0369 | 0.077198 | 0.0096498 | 0 | 54.2959 | 0 | 34.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 130.3409 | 0%
CZ 1A | 0.31334 | 0.091771 | 0.0007185 | 3.7618e-06 | 0 | 0.45992 | 0 | 0.36844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.2352 | 2.651% | CZ 1A | 10.0575 | 2.9457 | 0.073316 | 0.00038386 | 0 | 14.7625 | 0 | 11.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 39.6984 | 2.651% | CZ 1A | 2.9477 | 0.86332 | 0 | 0 | 0 | 4.3266 | 0 | 3.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 11.6133 | 2.651% | CZ 1A | 0 | 0 | 0.00073316 | 3.8386e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000737 | 2.651% | CZ 1A | 30.8594 | 9.0381 | 0.080135 | 0.00041955 | 0 | 45.2955 | 0 | 36.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 121.6605 | 2.651%
CZ 1B | 0.31631 | 0.091676 | 0.00069969 | -0.0016364 | 0 | 0.44859 | 0 | 0.35498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.2116 | 0% | CZ 1B | 10.1528 | 2.9426 | 0.071397 | -0.16698 | 0 | 14.3989 | 0 | 11.3941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 38.8257 | 0% | CZ 1B | 2.9756 | 0.86242 | 0 | 0 | 0 | 4.2201 | 0 | 3.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 11.4072 | 0% | CZ 1B | 0 | 0 | 0.00071397 | -0.0016698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0009558 | 0% | CZ 1B | 31.1516 | 9.0287 | 0.078037 | -0.18251 | 0 | 44.1798 | 0 | 34.9603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 119.3173 | 0%
CZ 2A | 0.31304 | 0.091652 | 0.00074483 | 0.013949 | 0 | 0.49368 | 0 | 0.39996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.314 | 16.38% | CZ 2A | 10.0479 | 2.9418 | 0.076003 | 1.4233 | 0 | 15.846 | 0 | 12.8377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 43.2058 | 16.38% | CZ 2A | 2.9449 | 0.8622 | 0 | 0 | 0 | 4.6442 | 0 | 3.7625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 12.2235 | 16.38% | CZ 2A | 0 | 0 | 0.00076003 | 0.014233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014993 | 16.38% | CZ 2A | 30.83 | 9.0263 | 0.083072 | 1.5557 | 0 | 48.62 | 0 | 39.3898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 129.6062 | 16.38%
CZ 2B | 0.30097 | 0.091699 | 0.0007185 | 0.0082195 | 0 | 0.38303 | 0 | 0.39996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.1856 | 2.81% | CZ 2B | 9.6605 | 2.9434 | 0.073316 | 0.83873 | 0 | 12.2944 | 0 | 12.8377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 38.6811 | 2.81% | CZ 2B | 2.8313 | 0.86265 | 0 | 0 | 0 | 3.6033 | 0 | 3.7625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 11.0695 | 2.81% | CZ 2B | 0 | 0 | 0.00073316 | 0.0083873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0091204 | 2.81% | CZ 2B | 29.6413 | 9.0311 | 0.080135 | 0.91673 | 0 | 37.7229 | 0 | 39.3898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 116.8832 | 2.81%
CZ 3A | 0.31098 | 0.091687 | 0.00074483 | 0.02218 | 0 | 0.2585 | 0 | 0.35255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.0377 | 16.25% | CZ 3A | 9.9819 | 2.943 | 0.076003 | 2.2632 | 0 | 8.2971 | 0 | 11.3161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 34.9104 | 16.25% | CZ 3A | 2.9255 | 0.86253 | 0 | 0 | 0 | 2.4318 | 0 | 3.3166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 9.5461 | 16.25% | CZ 3A | 0 | 0 | 0.00076003 | 0.022632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023392 | 16.25% | CZ 3A | 30.6274 | 9.0299 | 0.083072 | 2.4737 | 0 | 25.458 | 0 | 34.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 102.4945 | 16.25%
CZ 3B | 0.30214 | 0.091699 | 0.00072226 | 0.0018734 | 0 | 0.20085 | 0 | 0.35697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.95528 | 7.8% | CZ 3B | 9.6982 | 2.9434 | 0.0737 | 0.19116 | 0 | 6.4469 | 0 | 11.4578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 30.8441 | 7.8% | CZ 3B | 2.8424 | 0.86265 | 0 | 0 | 0 | 1.8895 | 0 | 3.3581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.9623 | 7.8% | CZ 3B | 0 | 0 | 0.000737 | 0.0019116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026486 | 7.8% | CZ 3B | 29.7568 | 9.0311 | 0.080554 | 0.20894 | 0 | 19.7809 | 0 | 35.1559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 94.1154 | 7.8%
CZ 3C | 0.30234 | 0.09152 | 0.00072226 | 0.0069142 | 0 | 0.11665 | 0 | 0.34096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.86013 | 1.112% | CZ 3C | 9.7043 | 2.9376 | 0.0737 | 0.70553 | 0 | 3.7443 | 0 | 10.9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 28.1425 | 1.112% | CZ 3C | 2.8442 | 0.86096 | 0 | 0 | 0 | 1.0974 | 0 | 3.2075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.0197 | 1.112% | CZ 3C | 0 | 0 | 0.000737 | 0.0070553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0077923 | 1.112% | CZ 3C | 29.7756 | 9.0134 | 0.080554 | 0.77114 | 0 | 11.4885 | 0 | 33.5796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 84.8101 | 1.112%
CZ 4A | 0.30251 | 0.091245 | 0.00077493 | 0.08707 | 0 | 0.16016 | 0 | 0.34431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.9871 | 17.53% | CZ 4A | 9.7101 | 2.9288 | 0.079074 | 8.8847 | 0 | 5.1407 | 0 | 11.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 37.8279 | 17.53% | CZ 4A | 2.8459 | 0.85837 | 0 | 0 | 0 | 1.5067 | 0 | 3.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.4596 | 17.53% | CZ 4A | 0 | 0 | 0.00079074 | 0.088847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089638 | 17.53% | CZ 4A | 29.7933 | 8.9863 | 0.086428 | 9.711 | 0 | 15.7731 | 0 | 33.9095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 98.3609 | 17.53%
CZ 4B | 0.30163 | 0.091592 | 0.00075988 | 0.025479 | 0 | 0.12047 | 0 | 0.37283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.91378 | 0.7484% | CZ 4B | 9.6817 | 2.9399 | 0.077539 | 2.5999 | 0 | 3.8668 | 0 | 11.9669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 31.1656 | 0.7484% | CZ 4B | 2.8375 | 0.86163 | 0 | 0 | 0 | 1.1333 | 0 | 3.5073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.3494 | 0.7484% | CZ 4B | 0 | 0 | 0.00077539 | 0.025999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026774 | 0.7484% | CZ 4B | 29.7061 | 9.0205 | 0.08475 | 2.8416 | 0 | 11.8643 | 0 | 36.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 90.3366 | 0.7484%
CZ 4C | 0.2976 | 0.091053 | 0.00077493 | 0.052639 | 0 | 0.03183 | 0 | 0.31371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.78864 | 2.419% | CZ 4C | 9.5523 | 2.9226 | 0.079074 | 5.3713 | 0 | 1.0217 | 0 | 10.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 29.0494 | 2.419% | CZ 4C | 2.7996 | 0.85657 | 0 | 0 | 0 | 0.29944 | 0 | 2.9512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 6.9165 | 2.419% | CZ 4C | 0 | 0 | 0.00079074 | 0.053713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054504 | 2.419% | CZ 4C | 29.3091 | 8.9674 | 0.086428 | 5.8708 | 0 | 3.1348 | 0 | 30.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 78.3659 | 2.419%
CZ 5A | 0.30274 | 0.091448 | 0.00078245 | 0.089497 | 0 | 0.1039 | 0 | 0.38261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.97201 | 21.62% | CZ 5A | 9.7174 | 2.9353 | 0.079842 | 9.1323 | 0 | 3.335 | 0 | 12.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 37.5138 | 21.62% | CZ 5A | 2.848 | 0.86028 | 0 | 0 | 0 | 0.97743 | 0 | 3.5994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.2947 | 21.62% | CZ 5A | 0 | 0 | 0.00079842 | 0.091323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092122 | 21.62% | CZ 5A | 29.8157 | 9.0063 | 0.087267 | 9.9816 | 0 | 10.2327 | 0 | 37.6816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 96.9065 | 21.62%
CZ 5B | 0.29994 | 0.091353 | 0.00077493 | 0.039375 | 0 | 0.13086 | 0 | 0.39937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.96271 | 4.907% | CZ 5B | 9.6275 | 2.9322 | 0.079074 | 4.0178 | 0 | 4.2004 | 0 | 12.8189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 33.709 | 4.907% | CZ 5B | 2.8217 | 0.85938 | 0 | 0 | 0 | 1.2311 | 0 | 3.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.6788 | 4.907% | CZ 5B | 0 | 0 | 0.00079074 | 0.040178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040969 | 4.907% | CZ 5B | 29.54 | 8.9969 | 0.086428 | 4.3915 | 0 | 12.888 | 0 | 39.3321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 95.3363 | 4.907%
CZ 5C | 0.29963 | 0.091089 | 0.00078245 | 0.056976 | 0 | 0.013613 | 0 | 0.30717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.77029 | 0.1033% | CZ 5C | 9.6175 | 2.9238 | 0.079842 | 5.8139 | 0 | 0.43693 | 0 | 9.8594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 28.7644 | 0.1033% | CZ 5C | 2.8187 | 0.85691 | 0 | 0 | 0 | 0.12806 | 0 | 2.8896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 6.703 | 0.1033% | CZ 5C | 0 | 0 | 0.00079842 | 0.058139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058937 | 0.1033% | CZ 5C | 29.5094 | 8.971 | 0.087267 | 6.3546 | 0 | 1.3406 | 0 | 30.2516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 76.6157 | 0.1033%
CZ 6A | 0.26657 | 0.091317 | 0.00078621 | 0.13886 | 0 | 0.10568 | 0 | 0.41039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.0146 | 4.509% | CZ 6A | 8.5563 | 2.9311 | 0.080226 | 14.1697 | 0 | 3.3922 | 0 | 13.1725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 42.335 | 4.509% | CZ 6A | 2.5077 | 0.85905 | 0 | 0 | 0 | 0.99419 | 0 | 3.8606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.2313 | 4.509% | CZ 6A | 0 | 0 | 0.00080226 | 0.1417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1425 | 4.509% | CZ 6A | 26.2532 | 8.9934 | 0.087687 | 15.4874 | 0 | 10.4082 | 0 | 40.4171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 101.7483 | 4.509%
CZ 6B | 0.26545 | 0.091293 | 0.00078621 | 0.078031 | 0 | 0.090635 | 0 | 0.44078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 0.968 | 0.5672% | CZ 6B | 8.5202 | 2.9303 | 0.080226 | 7.9623 | 0 | 2.9092 | 0 | 14.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 36.5834 | 0.5672% | CZ 6B | 2.4971 | 0.85882 | 0 | 0 | 0 | 0.85263 | 0 | 4.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.3648 | 0.5672% | CZ 6B | 0 | 0 | 0.00080226 | 0.079623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080425 | 0.5672% | CZ 6B | 26.1425 | 8.991 | 0.087687 | 8.7028 | 0 | 8.9262 | 0 | 43.4106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 96.3621 | 0.5672%
CZ 7 | 0.2698 | 0.091042 | 0.0007975 | 0.33986 | 0 | 0.074917 | 0 | 0.43651 | -0.022572 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.1914 | 0.5289% | CZ 7 | 8.66 | 2.9222 | 0.081377 | 34.6791 | 0 | 2.4047 | 0 | 14.0111 | -0.72451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 62.0669 | 0.5289% | CZ 7 | 2.5381 | 0.85646 | 0 | 0 | 0 | 0.70477 | 0 | 4.1064 | -0.21234 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 8.0031 | 0.5289% | CZ 7 | 0 | 0 | 0.00081377 | 0.34679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3476 | 0.5289% | CZ 7 | 26.5713 | 8.9663 | 0.088946 | 37.9042 | 0 | 7.3782 | 0 | 42.99 | -2.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 121.7773 | 0.5289%
CZ 8 | 0.26402 | 0.089486 | 0.00080126 | 0.42047 | 0 | 0.042058 | 0 | 0.47437 | -0.023314 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.2689 | 0.05788% | CZ 8 | 8.4745 | 2.8723 | 0.081761 | 42.9055 | 0 | 1.35 | 0 | 15.2263 | -0.74832 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 70.195 | 0.05788% | CZ 8 | 2.4837 | 0.84183 | 0 | 0 | 0 | 0.39565 | 0 | 4.4626 | -0.21932 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 7.9741 | 0.05788% | CZ 8 | 0 | 0 | 0.00081761 | 0.42905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42987 | 0.05788% | CZ 8 | 26.0023 | 8.8131 | 0.089365 | 46.8957 | 0 | 4.1421 | 0 | 46.7186 | -2.2961 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 130.4664 | 0.05788%
US Weighted | 0.3036 | 0.091497 | 0.00075956 | 0.05316 | 0 | 0.22715 | 0 | 0.37243 | -0.00013288 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010287 | 1.0495 | 100% | US Weighted | 9.7448 | 2.9369 | 0.077506 | 5.4245 | 0 | 7.2911 | 0 | 11.9541 | -0.0042652 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03302 | 37.4575 | 100% | US Weighted | 2.856 | 0.86074 | 0 | 0 | 0 | 2.1369 | 0 | 3.5035 | -0.0012501 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096775 | 9.3656 | 100% | US Weighted | 0 | 0 | 0.00077506 | 0.054245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05502 | 100% | US Weighted | 29.8998 | 9.0111 | 0.084714 | 5.9289 | 0 | 22.3711 | 0 | 36.6786 | -0.013087 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10131 | 104.0625 | 100%
Building Type: | Standalone Retail |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Standalone Retail |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Standalone Retail |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 24692 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 24692 | [17 empty] | Prototype Floor Area: | 24692 | Building Type: | Standalone Retail | [15 empty] | Prototype Floor Area: | 24692 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 56.69% | 66.54% | 2.236% |  |  | 41.04% |  | 64.79% | [7 empty] | 0.4407% | 45.97% | 0% | CZ 0A | 56.69% | 66.54% | 2.236% |  |  | 41.04% |  | 64.79% | [7 empty] | 0.4407% | 45.03% | 0% | CZ 0A | 56.69% | 66.54% |  |  |  | 41.04% |  | 64.79% | [7 empty] | 0.4407% | 46.41% | 0% | CZ 0A |  |  | 2.236% | [13 empty] | 2.236% | 0% | CZ 0A | 56.69% | 66.54% | 2.236% |  |  | 41.04% |  | 64.79% | [7 empty] | 0.4407% | 45.91% | 0%
CZ 0B | 55.89% | 66.57% | 2.162% | 95.83% |  | 39.42% |  | 62.1% | [7 empty] | 0.4407% | 44.81% | 0% | CZ 0B | 55.89% | 66.57% | 2.162% | 95.83% |  | 39.42% |  | 62.1% | [7 empty] | 0.4407% | 43.83% | 0% | CZ 0B | 55.89% | 66.57% |  |  |  | 39.42% |  | 62.1% | [7 empty] | 0.4407% | 45.27% | 0% | CZ 0B |  |  | 2.162% | 95.83% | [12 empty] | 2.426% | 0% | CZ 0B | 55.89% | 66.57% | 2.162% | 95.83% |  | 39.42% |  | 62.1% | [7 empty] | 0.4407% | 44.75% | 0%
CZ 1A | 53.24% | 66.57% | 2.188% | 100% |  | 42.03% |  | 68.88% | [7 empty] | 0.4407% | 47.11% | 2.651% | CZ 1A | 53.24% | 66.57% | 2.188% | 100% |  | 42.03% |  | 68.88% | [7 empty] | 0.4407% | 45.92% | 2.651% | CZ 1A | 53.24% | 66.57% |  |  |  | 42.03% |  | 68.88% | [7 empty] | 0.4407% | 47.68% | 2.651% | CZ 1A |  |  | 2.188% | 100% | [12 empty] | 2.2% | 2.651% | CZ 1A | 53.24% | 66.57% | 2.188% | 100% |  | 42.03% |  | 68.88% | [7 empty] | 0.4407% | 47.04% | 2.651%
CZ 1B | 53.74% | 66.58% | 2.133% | -31.25% |  | 39.77% |  | 63.88% | [7 empty] | 0.4407% | 45.19% | 0% | CZ 1B | 53.74% | 66.58% | 2.133% | -31.25% |  | 39.77% |  | 63.88% | [7 empty] | 0.4407% | 43.76% | 0% | CZ 1B | 53.74% | 66.58% |  |  |  | 39.77% |  | 63.88% | [7 empty] | 0.4407% | 45.87% | 0% | CZ 1B |  |  | 2.133% | -31.25% | [12 empty] | -2.462% | 0% | CZ 1B | 53.74% | 66.58% | 2.133% | -31.25% |  | 39.77% |  | 63.88% | [7 empty] | 0.4407% | 45.1% | 0%
CZ 2A | 53.19% | 66.59% | 2.212% | 73.94% |  | 52.81% |  | 72.49% | [7 empty] | 0.4407% | 52.59% | 16.38% | CZ 2A | 53.19% | 66.59% | 2.212% | 73.94% |  | 52.81% |  | 72.49% | [7 empty] | 0.4407% | 51.51% | 16.38% | CZ 2A | 53.19% | 66.59% |  |  |  | 52.81% |  | 72.49% | [7 empty] | 0.4407% | 53.12% | 16.38% | CZ 2A |  |  | 2.212% | 73.94% | [12 empty] | 27.97% | 16.38% | CZ 2A | 53.19% | 66.59% | 2.212% | 73.94% |  | 52.81% |  | 72.49% | [7 empty] | 0.4407% | 52.52% | 16.38%
CZ 2B | 51.14% | 66.57% | 2.133% | 74.22% |  | 53.12% |  | 68.83% | [7 empty] | 0.4407% | 51.4% | 2.81% | CZ 2B | 51.14% | 66.57% | 2.133% | 74.22% |  | 53.12% |  | 68.83% | [7 empty] | 0.4407% | 50.12% | 2.81% | CZ 2B | 51.14% | 66.57% |  |  |  | 53.12% |  | 68.83% | [7 empty] | 0.4407% | 52.02% | 2.81% | CZ 2B |  |  | 2.133% | 74.22% | [12 empty] | 19.97% | 2.81% | CZ 2B | 51.14% | 66.57% | 2.133% | 74.22% |  | 53.12% |  | 68.83% | [7 empty] | 0.4407% | 51.32% | 2.81%
CZ 3A | 52.84% | 66.58% | 2.123% | 25.58% |  | 51.53% |  | 68.09% | [7 empty] | 0.4407% | 49.39% | 16.25% | CZ 3A | 52.84% | 66.58% | 2.123% | 25.58% |  | 51.53% |  | 68.09% | [7 empty] | 0.4407% | 45.96% | 16.25% | CZ 3A | 52.84% | 66.58% |  |  |  | 51.53% |  | 68.09% | [7 empty] | 0.4407% | 51.27% | 16.25% | CZ 3A |  |  | 2.123% | 25.58% | [12 empty] | 18.82% | 16.25% | CZ 3A | 52.84% | 66.58% | 2.123% | 25.58% |  | 51.53% |  | 68.09% | [7 empty] | 0.4407% | 49.16% | 16.25%
CZ 3B | 51.33% | 66.59% | 2.082% | 7.844% |  | 45.89% |  | 66.66% | [7 empty] | 0.4407% | 47.97% | 7.8% | CZ 3B | 51.33% | 66.59% | 2.082% | 7.844% |  | 45.89% |  | 66.66% | [7 empty] | 0.4407% | 45.34% | 7.8% | CZ 3B | 51.33% | 66.59% |  |  |  | 45.89% |  | 66.66% | [7 empty] | 0.4407% | 49.29% | 7.8% | CZ 3B |  |  | 2.082% | 7.844% | [12 empty] | 4.431% | 7.8% | CZ 3B | 51.33% | 66.59% | 2.082% | 7.844% |  | 45.89% |  | 66.66% | [7 empty] | 0.4407% | 47.8% | 7.8%
CZ 3C | 51.37% | 66.47% | 2.052% | 68.53% |  | 52.33% |  | 67.85% | [7 empty] | 0.4407% | 49.71% | 1.112% | CZ 3C | 51.37% | 66.47% | 2.052% | 68.53% |  | 52.33% |  | 67.85% | [7 empty] | 0.4407% | 47.94% | 1.112% | CZ 3C | 51.37% | 66.47% |  |  |  | 52.33% |  | 67.85% | [7 empty] | 0.4407% | 50.59% | 1.112% | CZ 3C |  |  | 2.052% | 68.53% | [12 empty] | 16.86% | 1.112% | CZ 3C | 51.37% | 66.47% | 2.052% | 68.53% |  | 52.33% |  | 67.85% | [7 empty] | 0.4407% | 49.59% | 1.112%
CZ 4A | 51.4% | 66.36% | 2.139% | 36.64% |  | 49.88% |  | 66.44% | [7 empty] | 0.4407% | 47.63% | 17.53% | CZ 4A | 51.4% | 66.36% | 2.139% | 36.64% |  | 49.88% |  | 66.44% | [7 empty] | 0.4407% | 44.15% | 17.53% | CZ 4A | 51.4% | 66.36% |  |  |  | 49.88% |  | 66.44% | [7 empty] | 0.4407% | 49.99% | 17.53% | CZ 4A |  |  | 2.139% | 36.64% | [12 empty] | 32.08% | 17.53% | CZ 4A | 51.4% | 66.36% | 2.139% | 36.64% |  | 49.88% |  | 66.44% | [7 empty] | 0.4407% | 47.36% | 17.53%
CZ 4B | 51.25% | 66.56% | 2.117% | 32.17% |  | 42.59% |  | 65.9% | [7 empty] | 0.4407% | 47.51% | 0.7484% | CZ 4B | 51.25% | 66.56% | 2.117% | 32.17% |  | 42.59% |  | 65.9% | [7 empty] | 0.4407% | 44.66% | 0.7484% | CZ 4B | 51.25% | 66.56% |  |  |  | 42.59% |  | 65.9% | [7 empty] | 0.4407% | 49.08% | 0.7484% | CZ 4B |  |  | 2.117% | 32.17% | [12 empty] | 22.8% | 0.7484% | CZ 4B | 51.25% | 66.56% | 2.117% | 32.17% |  | 42.59% |  | 65.9% | [7 empty] | 0.4407% | 47.32% | 0.7484%
CZ 4C | 50.56% | 66.3% | 2.119% | 34.51% |  | 40.59% |  | 63.91% | [7 empty] | 0.4407% | 45.91% | 2.419% | CZ 4C | 50.56% | 66.3% | 2.119% | 34.51% |  | 40.59% |  | 63.91% | [7 empty] | 0.4407% | 42.49% | 2.419% | CZ 4C | 50.56% | 66.3% |  |  |  | 40.59% |  | 63.91% | [7 empty] | 0.4407% | 48.1% | 2.419% | CZ 4C |  |  | 2.119% | 34.51% | [12 empty] | 28.25% | 2.419% | CZ 4C | 50.56% | 66.3% | 2.119% | 34.51% |  | 40.59% |  | 63.91% | [7 empty] | 0.4407% | 45.66% | 2.419%
CZ 5A | 51.44% | 66.48% | 2.105% | 27.74% |  | 52.83% |  | 68.19% | [7 empty] | 0.4407% | 46.8% | 21.62% | CZ 5A | 51.44% | 66.48% | 2.105% | 27.74% |  | 52.83% |  | 68.19% | [7 empty] | 0.4407% | 40.85% | 21.62% | CZ 5A | 51.44% | 66.48% |  |  |  | 52.83% |  | 68.19% | [7 empty] | 0.4407% | 51.34% | 21.62% | CZ 5A |  |  | 2.105% | 27.74% | [12 empty] | 25.09% | 21.62% | CZ 5A | 51.44% | 66.48% | 2.105% | 27.74% |  | 52.83% |  | 68.19% | [7 empty] | 0.4407% | 46.31% | 21.62%
CZ 5B | 50.96% | 66.41% | 2.101% | 23.29% |  | 53.3% |  | 66.56% | [7 empty] | 0.4407% | 47.87% | 4.907% | CZ 5B | 50.96% | 66.41% | 2.101% | 23.29% |  | 53.3% |  | 66.56% | [7 empty] | 0.4407% | 42.69% | 4.907% | CZ 5B | 50.96% | 66.41% |  |  |  | 53.3% |  | 66.56% | [7 empty] | 0.4407% | 51.11% | 4.907% | CZ 5B |  |  | 2.101% | 23.29% | [12 empty] | 19.49% | 4.907% | CZ 5B | 50.96% | 66.41% | 2.101% | 23.29% |  | 53.3% |  | 66.56% | [7 empty] | 0.4407% | 47.49% | 4.907%
CZ 5C | 50.91% | 66.33% | 2.109% | 32.4% |  | 40.8% |  | 63.77% | [7 empty] | 0.4407% | 45.65% | 0.1033% | CZ 5C | 50.91% | 66.33% | 2.109% | 32.4% |  | 40.8% |  | 63.77% | [7 empty] | 0.4407% | 41.65% | 0.1033% | CZ 5C | 50.91% | 66.33% |  |  |  | 40.8% |  | 63.77% | [7 empty] | 0.4407% | 48.33% | 0.1033% | CZ 5C |  |  | 2.109% | 32.4% | [12 empty] | 27.12% | 0.1033% | CZ 5C | 50.91% | 66.33% | 2.109% | 32.4% |  | 40.8% |  | 63.77% | [7 empty] | 0.4407% | 45.35% | 0.1033%
CZ 6A | 45.29% | 66.42% | 2.077% | 30.43% |  | 50.4% |  | 67.72% | [7 empty] | 0.4407% | 44.71% | 4.509% | CZ 6A | 45.29% | 66.42% | 2.077% | 30.43% |  | 50.4% |  | 67.72% | [7 empty] | 0.4407% | 39.42% | 4.509% | CZ 6A | 45.29% | 66.42% |  |  |  | 50.4% |  | 67.72% | [7 empty] | 0.4407% | 49.29% | 4.509% | CZ 6A |  |  | 2.077% | 30.43% | [12 empty] | 28.26% | 4.509% | CZ 6A | 45.29% | 66.42% | 2.077% | 30.43% |  | 50.4% |  | 67.72% | [7 empty] | 0.4407% | 44.25% | 4.509%
CZ 6B | 45.1% | 66.45% | 2.086% | 26.43% |  | 55.91% |  | 68.77% | [7 empty] | 0.4407% | 46.2% | 0.5672% | CZ 6B | 45.1% | 66.45% | 2.086% | 26.43% |  | 55.91% |  | 68.77% | [7 empty] | 0.4407% | 40.4% | 0.5672% | CZ 6B | 45.1% | 66.45% |  |  |  | 55.91% |  | 68.77% | [7 empty] | 0.4407% | 50.45% | 0.5672% | CZ 6B |  |  | 2.086% | 26.43% | [12 empty] | 23.67% | 0.5672% | CZ 6B | 45.1% | 66.45% | 2.086% | 26.43% |  | 55.91% |  | 68.77% | [7 empty] | 0.4407% | 45.73% | 0.5672%
CZ 7 | 45.84% | 66.31% | 2.062% | 60.35% |  | 48.64% |  | 69.58% | [7 empty] | 0.4407% | 50.86% | 0.5289% | CZ 7 | 45.84% | 66.31% | 2.062% | 60.35% |  | 48.64% |  | 69.58% | [7 empty] | 0.4407% | 52.92% | 0.5289% | CZ 7 | 45.84% | 66.31% |  |  |  | 48.64% |  | 69.58% | [7 empty] | 0.4407% | 48.87% | 0.5289% | CZ 7 |  |  | 2.062% | 60.35% | [12 empty] | 56.61% | 0.5289% | CZ 7 | 45.84% | 66.31% | 2.062% | 60.35% |  | 48.64% |  | 69.58% | [7 empty] | 0.4407% | 51.05% | 0.5289%
CZ 8 | 44.86% | 65.54% | 2.015% | 55.72% |  | 54.05% |  | 69.12% | [7 empty] | 0.4407% | 50.41% | 0.05788% | CZ 8 | 44.86% | 65.54% | 2.015% | 55.72% |  | 54.05% |  | 69.12% | [7 empty] | 0.4407% | 51.48% | 0.05788% | CZ 8 | 44.86% | 65.54% |  |  |  | 54.05% |  | 69.12% | [7 empty] | 0.4407% | 49.2% | 0.05788% | CZ 8 |  |  | 2.015% | 55.72% | [12 empty] | 53.03% | 0.05788% | CZ 8 | 44.86% | 65.54% | 2.015% | 55.72% |  | 54.05% |  | 69.12% | [7 empty] | 0.4407% | 50.52% | 0.05788%
US Weighted | 51.58% | 66.49% | 2.131% | 38.93% | 0% | 50.8% | 0% | 68.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 48.53% | 100% | US Weighted | 51.58% | 66.49% | 2.131% | 38.93% | 0% | 50.8% | 0% | 68.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 44.99% | 100% | US Weighted | 51.58% | 66.49% | 0% | 0% | 0% | 50.8% | 0% | 68.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 50.92% | 100% | US Weighted | 0% | 0% | 2.131% | 38.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 23.42% | 100% | US Weighted | 51.58% | 66.49% | 2.131% | 38.93% | 0% | 50.8% | 0% | 68.27% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4407% | 48.27% | 100%

## RtlMall
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Strip Mall |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 22500 |  | Building Type: | Strip Mall |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 |  | Building Type: | Strip Mall |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Strip Mall |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Strip Mall | [14 empty] | Prototype Floor Area: | 22500 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.52845 | 0.078047 | 0.081896 | 0.11357 | 0 | 0.22672 | 0 | 0.14392 | 3.1875e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3408 |  | STD2019 | 16.962 | 2.5051 | 2.6287 | 11.589 | 0 | 7.2772 | 0 | 4.6195 | 0.00010231 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 50.9813 |  | STD2019 | 4.9713 | 0.73422 | 0.77042 | 0 | 0 | 2.1328 | 0 | 1.3539 | 2.9986e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.5452 |  | STD2019 | 0 | 0 | 0 | 0.11589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11589 |  | STD2019 | 52.0444 | 7.6865 | 8.0656 | 12.6667 | 0 | 22.3284 | 0 | 14.174 | 0.00031393 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 133.5337
STD2016 | 0.59189 | 0.078047 | 0.081874 | 0.10995 | 0 | 0.23785 | 0 | 0.14217 | 3.1124e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.41 |  | STD2016 | 18.9984 | 2.5051 | 2.628 | 11.2196 | 0 | 7.6345 | 0 | 4.5634 | 9.9902e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.9488 |  | STD2016 | 5.5681 | 0.73422 | 0.77022 | 0 | 0 | 2.2375 | 0 | 1.3374 | 2.928e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.2301 |  | STD2016 | 0 | 0 | 0 | 0.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1122 |  | STD2016 | 58.2927 | 7.6865 | 8.0634 | 12.2631 | 0 | 23.4248 | 0 | 14.0017 | 0.00030653 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 140.3002
STD2013 | 0.72311 | 0.12064 | 0.08182 | 0.099421 | 0 | 0.2584 | 0 | 0.14059 | 2.9948e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5922 |  | STD2013 | 23.2103 | 3.8724 | 2.6262 | 10.145 | 0 | 8.294 | 0 | 4.5128 | 9.6128e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.0605 |  | STD2013 | 6.8025 | 1.1349 | 0.7697 | 0 | 0 | 2.4308 | 0 | 1.3226 | 2.8174e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.0432 |  | STD2013 | 0 | 0 | 0 | 0.10145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10145 |  | STD2013 | 71.2159 | 11.8817 | 8.058 | 11.0885 | 0 | 25.4485 | 0 | 13.8465 | 0.00029495 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 158.1071
STD2010 | 0.80123 | 0.12064 | 0.081921 | 0.098982 | 0 | 0.28657 | 0 | 0.26815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.8257 |  | STD2010 | 25.7178 | 3.8724 | 2.6295 | 10.1002 | 0 | 9.1982 | 0 | 8.6071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 65.5249 |  | STD2010 | 7.5374 | 1.1349 | 0.77066 | 0 | 0 | 2.6958 | 0 | 2.5226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 16.244 |  | STD2010 | 0 | 0 | 0 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.101 |  | STD2010 | 78.9096 | 11.8817 | 8.068 | 11.0396 | 0 | 28.2227 | 0 | 26.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 181.0984
STD2007 | 0.89433 | 0.21919 | 0.089124 | 0.10056 | 0 | 0.43486 | 0 | 0.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2613 |  | STD2007 | 28.706 | 7.0354 | 2.8607 | 10.2616 | 0 | 13.958 | 0 | 11.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 79.6176 |  | STD2007 | 8.4133 | 2.062 | 0.83842 | 0 | 0 | 4.0908 | 0 | 3.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.3271 |  | STD2007 | 0 | 0 | 0 | 0.10262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10262 |  | STD2007 | 88.0783 | 21.5866 | 8.7774 | 11.2159 | 0 | 42.827 | 0 | 34.8934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 224.0201
STD2004 | 0.8297 | 0.21919 | 0.089296 | 0.18115 | 0 | 0.45174 | 0 | 0.37824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.3183 |  | STD2004 | 26.6317 | 7.0354 | 2.8662 | 18.4843 | 0 | 14.4999 | 0 | 12.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 87.0818 |  | STD2004 | 7.8053 | 2.062 | 0.84004 | 0 | 0 | 4.2497 | 0 | 3.5582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.1048 |  | STD2004 | 0 | 0 | 0 | 0.18484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18484 |  | STD2004 | 81.7137 | 21.5866 | 8.7944 | 20.2033 | 0 | 44.4899 | 0 | 37.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 230.6802
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | -0.064625 | 0 | 0.00017239 | 0.080583 | 0 | 0.016884 | 0 | 0.023938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056952 |  | 2004-2007 | -2.0743 | 0 | 0.0055332 | 8.2227 | 0 | 0.54194 | 0 | 0.76835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4642 |  | 2004-2007 | -0.60795 | 0 | 0.0016217 | 0 | 0 | 0.15883 | 0 | 0.22519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.2223 |  | 2004-2007 | 0 | 0 | 0 | 0.082227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082227 |  | 2004-2007 | -6.3646 | 0 | 0.016978 | 8.9874 | 0 | 1.6628 | 0 | 2.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6601
2007-2010 | 0.093098 | 0.098541 | 0.0072028 | 0.0015811 | 0 | 0.14829 | 0 | 0.086148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.43561 |  | 2007-2010 | 2.9882 | 3.1629 | 0.2312 | 0.16134 | 0 | 4.7598 | 0 | 2.7652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 14.0927 |  | 2007-2010 | 0.8758 | 0.92701 | 0.06776 | 0 | 0 | 1.395 | 0 | 0.81042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 4.083 |  | 2007-2010 | 0 | 0 | 0 | 0.0016134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016134 |  | 2007-2010 | 9.1688 | 9.7048 | 0.70937 | 0.17634 | 0 | 14.6044 | 0 | 8.4843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 42.9217
2010-2013 | 0.07812 | 0 | 0.00010151 | -0.00043854 | 0 | 0.028168 | 0 | 0.12756 | -2.9948e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23351 |  | 2010-2013 | 2.5075 | 0 | 0.0032583 | -0.044749 | 0 | 0.90414 | 0 | 4.0943 | -9.6128e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4644 |  | 2010-2013 | 0.7349 | 0 | 0.00095495 | 0 | 0 | 0.26499 | 0 | 1.2 | -2.8174e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2008 |  | 2010-2013 | 0 | 0 | 0 | -0.00044749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00044749 |  | 2010-2013 | 7.6937 | 0 | 0.0099973 | -0.048911 | 0 | 2.7742 | 0 | 12.5626 | -0.00029495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9912
2013-2016 | 0.13122 | 0.042598 | -5.4807e-05 | -0.010531 | 0 | 0.020549 | 0 | -0.0015762 | -1.1757e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1822 |  | 2013-2016 | 4.2119 | 1.3673 | -0.0017592 | -1.0746 | 0 | 0.65956 | 0 | -0.050594 | -3.7738e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1117 |  | 2013-2016 | 1.2344 | 0.40073 | -0.00051558 | 0 | 0 | 0.19331 | 0 | -0.014828 | -1.1061e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8131 |  | 2013-2016 | 0 | 0 | 0 | -0.010746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.010746 |  | 2013-2016 | 12.9232 | 4.1952 | -0.0053976 | -1.1746 | 0 | 2.0237 | 0 | -0.15524 | -1.1579e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8069
2016-2019 | 0.063444 | 0 | -2.1599e-05 | -0.0036194 | 0 | 0.011132 | 0 | -0.0017495 | -7.5116e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069185 |  | 2016-2019 | 2.0364 | 0 | -0.00069327 | -0.36933 | 0 | 0.35732 | 0 | -0.056156 | -2.4111e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9675 |  | 2016-2019 | 0.59684 | 0 | -0.00020319 | 0 | 0 | 0.10472 | 0 | -0.016459 | -7.0664e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6849 |  | 2016-2019 | 0 | 0 | 0 | -0.0036933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0036933 |  | 2016-2019 | 6.2483 | 0 | -0.0021272 | -0.40367 | 0 | 1.0964 | 0 | -0.1723 | -7.3978e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7665
2004-2019 | 0.30126 | 0.14114 | 0.0074003 | 0.067574 | 0 | 0.22502 | 0 | 0.23432 | -3.1875e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.97745 |  | 2004-2019 | 9.6697 | 4.5302 | 0.23753 | 6.8953 | 0 | 7.2227 | 0 | 7.5211 | -0.00010231 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 36.1005 |  | 2004-2019 | 2.834 | 1.3277 | 0.069617 | 0 | 0 | 2.1169 | 0 | 2.2043 | -2.9986e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 8.5596 |  | 2004-2019 | 0 | 0 | 0 | 0.068953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068953 |  | 2004-2019 | 29.6693 | 13.9001 | 0.72882 | 7.5366 | 0 | 22.1614 | 0 | 23.0769 | -0.00031393 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 97.1465
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | -7.789% | 0% | 0.1931% | 44.48% |  | 3.738% |  | 6.329% | [7 empty] | 0% | 2.457% |  | 2004-2007 | -7.789% | 0% | 0.1931% | 44.48% |  | 3.738% |  | 6.329% | [7 empty] | 0% | 8.571% |  | 2004-2007 | -7.789% | 0% | 0.1931% |  |  | 3.738% |  | 6.329% | [7 empty] | 0% | -1.106% |  | 2004-2007 |  |  |  | 44.48% | [12 empty] | 44.48% |  | 2004-2007 | -7.789% | 0% | 0.1931% | 44.48% |  | 3.738% |  | 6.329% | [7 empty] | 0% | 2.887%
2007-2010 | 10.41% | 44.96% | 8.082% | 1.572% |  | 34.1% |  | 24.31% | [7 empty] | 0.4428% | 19.26% |  | 2007-2010 | 10.41% | 44.96% | 8.082% | 1.572% |  | 34.1% |  | 24.31% | [7 empty] | 0.4428% | 17.7% |  | 2007-2010 | 10.41% | 44.96% | 8.082% |  |  | 34.1% |  | 24.31% | [7 empty] | 0.4428% | 20.09% |  | 2007-2010 |  |  |  | 1.572% | [12 empty] | 1.572% |  | 2007-2010 | 10.41% | 44.96% | 8.082% | 1.572% |  | 34.1% |  | 24.31% | [7 empty] | 0.4428% | 19.16%
2010-2013 | 9.75% | 0% | 0.1239% | -0.443% |  | 9.83% |  | 47.57% | [7 empty] | 0% | 12.79% |  | 2010-2013 | 9.75% | 0% | 0.1239% | -0.443% |  | 9.83% |  | 47.57% | [7 empty] | 0% | 11.39% |  | 2010-2013 | 9.75% | 0% | 0.1239% |  |  | 9.83% |  | 47.57% | [7 empty] | 0% | 13.55% |  | 2010-2013 |  |  |  | -0.443% | [12 empty] | -0.443% |  | 2010-2013 | 9.75% | 0% | 0.1239% | -0.443% |  | 9.83% |  | 47.57% | [7 empty] | 0% | 12.7%
2013-2016 | 18.15% | 35.31% | -0.06698% | -10.59% |  | 7.952% |  | -1.121% | -3.926% | [6 empty] | 0% | 11.44% |  | 2013-2016 | 18.15% | 35.31% | -0.06698% | -10.59% |  | 7.952% |  | -1.121% | -3.926% | [6 empty] | 0% | 8.804% |  | 2013-2016 | 18.15% | 35.31% | -0.06698% |  |  | 7.952% |  | -1.121% | -3.926% | [6 empty] | 0% | 12.91% |  | 2013-2016 |  |  |  | -10.59% | [12 empty] | -10.59% |  | 2013-2016 | 18.15% | 35.31% | -0.06698% | -10.59% |  | 7.952% |  | -1.121% | -3.926% | [6 empty] | 0% | 11.26%
2016-2019 | 10.72% | 0% | -0.02638% | -3.292% |  | 4.68% |  | -1.231% | -2.413% | [6 empty] | 0% | 4.907% |  | 2016-2019 | 10.72% | 0% | -0.02638% | -3.292% |  | 4.68% |  | -1.231% | -2.413% | [6 empty] | 0% | 3.716% |  | 2016-2019 | 10.72% | 0% | -0.02638% |  |  | 4.68% |  | -1.231% | -2.413% | [6 empty] | 0% | 5.6% |  | 2016-2019 |  |  |  | -3.292% | [12 empty] | -3.292% |  | 2016-2019 | 10.72% | 0% | -0.02638% | -3.292% |  | 4.68% |  | -1.231% | -2.413% | [6 empty] | 0% | 4.823%
2004-2019 | 36.31% | 64.39% | 8.287% | 37.3% |  | 49.81% |  | 61.95% | [7 empty] | 0.4428% | 42.16% |  | 2004-2019 | 36.31% | 64.39% | 8.287% | 37.3% |  | 49.81% |  | 61.95% | [7 empty] | 0.4428% | 41.46% |  | 2004-2019 | 36.31% | 64.39% | 8.287% |  |  | 49.81% |  | 61.95% | [7 empty] | 0.4428% | 42.57% |  | 2004-2019 |  |  |  | 37.3% | [12 empty] | 37.3% |  | 2004-2019 | 36.31% | 64.39% | 8.287% | 37.3% |  | 49.81% |  | 61.95% | [7 empty] | 0.4428% | 42.11%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.52845 | 0.07808 | 0.075521 | 0 | 0 | 0.89682 | 0 | 0.15067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.8978 | 0% | CZ 0A | 16.962 | 2.5062 | 2.4241 | 0 | 0 | 28.7861 | 0 | 4.8363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.9143 | 0% | CZ 0A | 4.9713 | 0.73453 | 0.71045 | 0 | 0 | 8.4367 | 0 | 1.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 17.853 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 52.0444 | 7.6898 | 7.4377 | 0 | 0 | 88.324 | 0 | 14.8392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 186.9027 | 0%
CZ 0B | 0.52845 | 0.078028 | 0.075468 | 0 | 0 | 0.77716 | 0 | 0.18369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.811 | 0% | CZ 0B | 16.962 | 2.5045 | 2.4224 | 0 | 0 | 24.945 | 0 | 5.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.1296 | 0% | CZ 0B | 4.9713 | 0.73404 | 0.70995 | 0 | 0 | 7.311 | 0 | 1.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 17.0368 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 52.0444 | 7.6846 | 7.4325 | 0 | 0 | 76.5385 | 0 | 18.0907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 178.3584 | 0%
CZ 1A | 0.52845 | 0.078041 | 0.076899 | 0 | 0 | 0.56531 | 0 | 0.11736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5343 | 4.208% | CZ 1A | 16.962 | 2.505 | 2.4683 | 0 | 0 | 18.1452 | 0 | 3.7669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 49.247 | 4.208% | CZ 1A | 4.9713 | 0.73416 | 0.72342 | 0 | 0 | 5.3181 | 0 | 1.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.4335 | 4.208% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.208% | CZ 1A | 52.0444 | 7.6859 | 7.5734 | 0 | 0 | 55.6747 | 0 | 11.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 151.1041 | 4.208%
CZ 1B | 0.52845 | 0.07791 | 0.077004 | 0.0032655 | 0 | 0.61321 | 0 | 0.17124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.6393 | 0% | CZ 1B | 16.962 | 2.5007 | 2.4717 | 0.33321 | 0 | 19.6827 | 0 | 5.4966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.8466 | 0% | CZ 1B | 4.9713 | 0.73292 | 0.7244 | 0 | 0 | 5.7687 | 0 | 1.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 15.3908 | 0% | CZ 1B | 0 | 0 | 0 | 0.0033321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033321 | 0% | CZ 1B | 52.0444 | 7.673 | 7.5838 | 0.3642 | 0 | 60.3923 | 0 | 16.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 161.4904 | 0%
CZ 2A | 0.52845 | 0.07787 | 0.07854 | 0.0084671 | 0 | 0.45005 | 0 | 0.12317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4348 | 17.06% | CZ 2A | 16.962 | 2.4995 | 2.521 | 0.86399 | 0 | 14.4457 | 0 | 3.9536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 46.6454 | 17.06% | CZ 2A | 4.9713 | 0.73255 | 0.73885 | 0 | 0 | 4.2338 | 0 | 1.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.4178 | 17.06% | CZ 2A | 0 | 0 | 0 | 0.0086399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0086399 | 17.06% | CZ 2A | 52.0444 | 7.6691 | 7.735 | 0.94434 | 0 | 44.3236 | 0 | 12.1307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 141.4149 | 17.06%
CZ 2B | 0.52845 | 0.077949 | 0.078645 | 0.0023738 | 0 | 0.35135 | 0 | 0.15032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3573 | 3.729% | CZ 2B | 16.962 | 2.502 | 2.5243 | 0.24222 | 0 | 11.2775 | 0 | 4.8249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 43.7327 | 3.729% | CZ 2B | 4.9713 | 0.73329 | 0.73984 | 0 | 0 | 3.3053 | 0 | 1.4141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.7463 | 3.729% | CZ 2B | 0 | 0 | 0 | 0.0024222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0024222 | 3.729% | CZ 2B | 52.0444 | 7.6769 | 7.7454 | 0.26475 | 0 | 34.6028 | 0 | 14.8043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 133.7061 | 3.729%
CZ 3A | 0.52845 | 0.077923 | 0.081402 | 0.078941 | 0 | 0.22757 | 0 | 0.11363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.2761 | 18.76% | CZ 3A | 16.962 | 2.5012 | 2.6128 | 8.0552 | 0 | 7.3046 | 0 | 3.6472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 46.4827 | 18.76% | CZ 3A | 4.9713 | 0.73305 | 0.76577 | 0 | 0 | 2.1409 | 0 | 1.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.2625 | 18.76% | CZ 3A | 0 | 0 | 0 | 0.080552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080552 | 18.76% | CZ 3A | 52.0444 | 7.6743 | 8.0169 | 8.8043 | 0 | 22.4126 | 0 | 11.1908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 126.711 | 18.76%
CZ 3B | 0.52845 | 0.077923 | 0.08064 | 0.02254 | 0 | 0.21425 | 0 | 0.16674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.2588 | 11.42% | CZ 3B | 16.962 | 2.5012 | 2.5884 | 2.3 | 0 | 6.8769 | 0 | 5.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 41.9802 | 11.42% | CZ 3B | 4.9713 | 0.73305 | 0.75861 | 0 | 0 | 2.0155 | 0 | 1.5686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.6296 | 11.42% | CZ 3B | 0 | 0 | 0 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023 | 11.42% | CZ 3B | 52.0444 | 7.6743 | 7.9419 | 2.5139 | 0 | 21.1004 | 0 | 16.4216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 124.2642 | 11.42%
CZ 3C | 0.52845 | 0.078186 | 0.081546 | 0.003926 | 0 | 0.084001 | 0 | 0.19647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.1408 | 2.391% | CZ 3C | 16.962 | 2.5096 | 2.6175 | 0.40061 | 0 | 2.6962 | 0 | 6.3064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 36.892 | 2.391% | CZ 3C | 4.9713 | 0.73552 | 0.76713 | 0 | 0 | 0.79022 | 0 | 1.8483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.695 | 2.391% | CZ 3C | 0 | 0 | 0 | 0.0040061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0040061 | 2.391% | CZ 3C | 52.0444 | 7.7001 | 8.0311 | 0.43787 | 0 | 8.2729 | 0 | 19.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 112.4039 | 2.391%
CZ 4A | 0.52845 | 0.07833 | 0.083607 | 0.1872 | 0 | 0.14162 | 0 | 0.13459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.322 | 17.79% | CZ 4A | 16.962 | 2.5142 | 2.6836 | 19.1025 | 0 | 4.5456 | 0 | 4.3201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.5277 | 17.79% | CZ 4A | 4.9713 | 0.73688 | 0.78652 | 0 | 0 | 1.3322 | 0 | 1.2662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.6756 | 17.79% | CZ 4A | 0 | 0 | 0 | 0.19103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19103 | 17.79% | CZ 4A | 52.0444 | 7.7144 | 8.2341 | 20.8791 | 0 | 13.9471 | 0 | 13.2554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 132.6422 | 17.79%
CZ 4B | 0.52845 | 0.077923 | 0.082846 | 0.048528 | 0 | 0.13701 | 0 | 0.24389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.2869 | 0.4638% | CZ 4B | 16.962 | 2.5012 | 2.6592 | 4.9518 | 0 | 4.3977 | 0 | 7.8283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 44.6998 | 0.4638% | CZ 4B | 4.9713 | 0.73305 | 0.77936 | 0 | 0 | 1.2889 | 0 | 2.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.6495 | 0.4638% | CZ 4B | 0 | 0 | 0 | 0.049518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049518 | 0.4638% | CZ 4B | 52.0444 | 7.6743 | 8.1591 | 5.4123 | 0 | 13.4933 | 0 | 24.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 127.3707 | 0.4638%
CZ 4C | 0.52845 | 0.078382 | 0.084277 | 0.12677 | 0 | 0.039395 | 0 | 0.19818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.2237 | 2.358% | CZ 4C | 16.962 | 2.5159 | 2.7051 | 12.9358 | 0 | 1.2645 | 0 | 6.3612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 48.1442 | 2.358% | CZ 4C | 4.9713 | 0.73737 | 0.79282 | 0 | 0 | 0.3706 | 0 | 1.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.319 | 2.358% | CZ 4C | 0 | 0 | 0 | 0.12936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12936 | 2.358% | CZ 4C | 52.0444 | 7.7195 | 8.3 | 14.1388 | 0 | 3.8798 | 0 | 19.5179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 122.1682 | 2.358%
CZ 5A | 0.52845 | 0.078054 | 0.085445 | 0.27821 | 0 | 0.073827 | 0 | 0.16286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3751 | 16.36% | CZ 5A | 16.962 | 2.5054 | 2.7426 | 28.3886 | 0 | 2.3697 | 0 | 5.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 63.5953 | 16.36% | CZ 5A | 4.9713 | 0.73428 | 0.80381 | 0 | 0 | 0.69452 | 0 | 1.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.3185 | 16.36% | CZ 5A | 0 | 0 | 0 | 0.28389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28389 | 16.36% | CZ 5A | 52.0444 | 7.6872 | 8.4151 | 31.0287 | 0 | 7.2709 | 0 | 16.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 139.053 | 16.36%
CZ 5B | 0.52845 | 0.078225 | 0.084802 | 0.13811 | 0 | 0.099964 | 0 | 0.23491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3327 | 3.359% | CZ 5B | 16.962 | 2.5108 | 2.7219 | 14.093 | 0 | 3.2086 | 0 | 7.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.4362 | 3.359% | CZ 5B | 4.9713 | 0.73589 | 0.79776 | 0 | 0 | 0.94039 | 0 | 2.2099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.2378 | 3.359% | CZ 5B | 0 | 0 | 0 | 0.14093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14093 | 3.359% | CZ 5B | 52.0444 | 7.704 | 8.3517 | 15.4036 | 0 | 9.8449 | 0 | 23.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 133.0517 | 3.359%
CZ 5C | 0.52845 | 0.078304 | 0.08534 | 0.15562 | 0 | 0.021529 | 0 | 0.18986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.2273 | 0.05591% | CZ 5C | 16.962 | 2.5134 | 2.7392 | 15.8795 | 0 | 0.69102 | 0 | 6.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 50.2789 | 0.05591% | CZ 5C | 4.9713 | 0.73663 | 0.80282 | 0 | 0 | 0.20253 | 0 | 1.7861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.0819 | 0.05591% | CZ 5C | 0 | 0 | 0 | 0.1588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1588 | 0.05591% | CZ 5C | 52.0444 | 7.7118 | 8.4047 | 17.3563 | 0 | 2.1203 | 0 | 18.6983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 122.9035 | 0.05591%
CZ 6A | 0.52845 | 0.078172 | 0.086784 | 0.38678 | 0 | 0.090473 | 0 | 0.12447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4634 | 1.584% | CZ 6A | 16.962 | 2.5092 | 2.7856 | 39.4671 | 0 | 2.904 | 0 | 3.9953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 74.0228 | 1.584% | CZ 6A | 4.9713 | 0.73539 | 0.8164 | 0 | 0 | 0.85111 | 0 | 1.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.1277 | 1.584% | CZ 6A | 0 | 0 | 0 | 0.39467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39467 | 1.584% | CZ 6A | 52.0444 | 7.6988 | 8.5469 | 43.1375 | 0 | 8.9102 | 0 | 12.2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 149.1643 | 1.584%
CZ 6B | 0.52845 | 0.078041 | 0.08639 | 0.25228 | 0 | 0.060398 | 0 | 0.23323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.407 | 0.2227% | CZ 6B | 16.962 | 2.505 | 2.7729 | 25.7431 | 0 | 1.9387 | 0 | 7.4862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.8076 | 0.2227% | CZ 6B | 4.9713 | 0.73416 | 0.8127 | 0 | 0 | 0.56819 | 0 | 2.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.863 | 0.2227% | CZ 6B | 0 | 0 | 0 | 0.25743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25743 | 0.2227% | CZ 6B | 52.0444 | 7.6859 | 8.5082 | 28.1372 | 0 | 5.9483 | 0 | 22.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 141.8616 | 0.2227%
CZ 7 | 0.52845 | 0.07833 | 0.088293 | 0.45446 | 0 | 0.055265 | 0 | 0.17015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5432 | 0.2165% | CZ 7 | 16.962 | 2.5142 | 2.834 | 46.3735 | 0 | 1.7739 | 0 | 5.4616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 81.319 | 0.2165% | CZ 7 | 4.9713 | 0.73688 | 0.83061 | 0 | 0 | 0.5199 | 0 | 1.6007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.2419 | 0.2165% | CZ 7 | 0 | 0 | 0 | 0.46374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46374 | 0.2165% | CZ 7 | 52.0444 | 7.7144 | 8.6956 | 50.6863 | 0 | 5.4428 | 0 | 16.7577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 157.9089 | 0.2165%
CZ 8 | 0.52845 | 0.080548 | 0.090341 | 0.5326 | 0 | 0.017 | 0 | 0.24617 | 0.012812 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.6762 | 0.02488% | CZ 8 | 16.962 | 2.5854 | 2.8998 | 54.3474 | 0 | 0.54565 | 0 | 7.9017 | 0.41124 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 91.0528 | 0.02488% | CZ 8 | 4.9713 | 0.75775 | 0.84987 | 0 | 0 | 0.15992 | 0 | 2.3158 | 0.12053 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.7577 | 0.02488% | CZ 8 | 0 | 0 | 0 | 0.54347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54347 | 0.02488% | CZ 8 | 52.0444 | 7.9328 | 8.8973 | 59.4017 | 0 | 1.6742 | 0 | 24.2446 | 1.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 172.0246 | 0.02488%
US Weighted | 0.52845 | 0.078047 | 0.081896 | 0.11357 | 0 | 0.22672 | 0 | 0.14392 | 3.1875e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3408 | 100% | US Weighted | 16.962 | 2.5051 | 2.6287 | 11.589 | 0 | 7.2772 | 0 | 4.6195 | 0.00010231 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 50.9813 | 100% | US Weighted | 4.9713 | 0.73422 | 0.77042 | 0 | 0 | 2.1328 | 0 | 1.3539 | 2.9986e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.5452 | 100% | US Weighted | 0 | 0 | 0 | 0.11589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11589 | 100% | US Weighted | 52.0444 | 7.6865 | 8.0656 | 12.6667 | 0 | 22.3284 | 0 | 14.174 | 0.00031393 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 133.5337 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.59189 | 0.07808 | 0.075508 | 0 | 0 | 0.917 | 0 | 0.15371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.9844 | 0% | CZ 0A | 18.9984 | 2.5062 | 2.4236 | 0 | 0 | 29.4337 | 0 | 4.9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 63.6953 | 0% | CZ 0A | 5.5681 | 0.73453 | 0.71033 | 0 | 0 | 8.6265 | 0 | 1.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 18.668 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 58.2927 | 7.6898 | 7.4364 | 0 | 0 | 90.3111 | 0 | 15.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 195.4355 | 0%
CZ 0B | 0.59189 | 0.078028 | 0.075455 | 0 | 0 | 0.7948 | 0 | 0.18718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.8956 | 0% | CZ 0B | 18.9984 | 2.5045 | 2.4219 | 0 | 0 | 25.5113 | 0 | 6.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.844 | 0% | CZ 0B | 5.5681 | 0.73404 | 0.70983 | 0 | 0 | 7.4769 | 0 | 1.7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 17.8323 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 58.2927 | 7.6846 | 7.4312 | 0 | 0 | 78.2761 | 0 | 18.4346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 186.6868 | 0%
CZ 1A | 0.59189 | 0.078041 | 0.076886 | 0 | 0 | 0.58644 | 0 | 0.12195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.6234 | 4.208% | CZ 1A | 18.9984 | 2.505 | 2.4679 | 0 | 0 | 18.8236 | 0 | 3.9144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.1089 | 4.208% | CZ 1A | 5.5681 | 0.73416 | 0.72329 | 0 | 0 | 5.5169 | 0 | 1.1472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 15.2722 | 4.208% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.208% | CZ 1A | 58.2927 | 7.6859 | 7.5721 | 0 | 0 | 57.7562 | 0 | 12.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 159.8851 | 4.208%
CZ 1B | 0.59189 | 0.07791 | 0.076978 | 0.0027329 | 0 | 0.63354 | 0 | 0.17548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7268 | 0% | CZ 1B | 18.9984 | 2.5007 | 2.4708 | 0.27887 | 0 | 20.3354 | 0 | 5.6327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.6166 | 0% | CZ 1B | 5.5681 | 0.73292 | 0.72416 | 0 | 0 | 5.96 | 0 | 1.6508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 16.2186 | 0% | CZ 1B | 0 | 0 | 0 | 0.0027887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027887 | 0% | CZ 1B | 58.2927 | 7.673 | 7.5812 | 0.3048 | 0 | 62.3949 | 0 | 17.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 170.0969 | 0%
CZ 2A | 0.59189 | 0.07787 | 0.078527 | 0.0074722 | 0 | 0.46701 | 0 | 0.12666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5177 | 17.06% | CZ 2A | 18.9984 | 2.4995 | 2.5205 | 0.76247 | 0 | 14.9901 | 0 | 4.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 49.2363 | 17.06% | CZ 2A | 5.5681 | 0.73255 | 0.73873 | 0 | 0 | 4.3933 | 0 | 1.1916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.2069 | 17.06% | CZ 2A | 0 | 0 | 0 | 0.0076247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0076247 | 17.06% | CZ 2A | 58.2927 | 7.6691 | 7.7337 | 0.83338 | 0 | 45.9939 | 0 | 12.4746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 149.5651 | 17.06%
CZ 2B | 0.59189 | 0.077949 | 0.078619 | 0.0018949 | 0 | 0.36404 | 0 | 0.15485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4375 | 3.729% | CZ 2B | 18.9984 | 2.502 | 2.5235 | 0.19335 | 0 | 11.685 | 0 | 4.9703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 46.2722 | 3.729% | CZ 2B | 5.5681 | 0.73329 | 0.73959 | 0 | 0 | 3.4247 | 0 | 1.4567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.5049 | 3.729% | CZ 2B | 0 | 0 | 0 | 0.0019335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019335 | 3.729% | CZ 2B | 58.2927 | 7.6769 | 7.7428 | 0.21134 | 0 | 35.8529 | 0 | 15.2503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 141.5946 | 3.729%
CZ 3A | 0.59189 | 0.077923 | 0.081375 | 0.074932 | 0 | 0.23857 | 0 | 0.11522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3481 | 18.76% | CZ 3A | 18.9984 | 2.5012 | 2.612 | 7.6461 | 0 | 7.6577 | 0 | 3.6982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 48.5133 | 18.76% | CZ 3A | 5.5681 | 0.73305 | 0.76553 | 0 | 0 | 2.2443 | 0 | 1.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.9775 | 18.76% | CZ 3A | 0 | 0 | 0 | 0.076461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076461 | 18.76% | CZ 3A | 58.2927 | 7.6743 | 8.0143 | 8.3572 | 0 | 23.496 | 0 | 11.3472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 133.7494 | 18.76%
CZ 3B | 0.59189 | 0.077923 | 0.080614 | 0.019048 | 0 | 0.2243 | 0 | 0.17299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.335 | 11.42% | CZ 3B | 18.9984 | 2.5012 | 2.5875 | 1.9437 | 0 | 7.1997 | 0 | 5.5526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 44.1827 | 11.42% | CZ 3B | 5.5681 | 0.73305 | 0.75836 | 0 | 0 | 2.1101 | 0 | 1.6274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.3796 | 11.42% | CZ 3B | 0 | 0 | 0 | 0.019437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019437 | 11.42% | CZ 3B | 58.2927 | 7.6743 | 7.9393 | 2.1244 | 0 | 22.0907 | 0 | 17.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 131.7261 | 11.42%
CZ 3C | 0.59189 | 0.078186 | 0.081507 | 0.0028568 | 0 | 0.09403 | 0 | 0.20636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.2231 | 2.391% | CZ 3C | 18.9984 | 2.5096 | 2.6162 | 0.29151 | 0 | 3.0182 | 0 | 6.6237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 39.4572 | 2.391% | CZ 3C | 5.5681 | 0.73552 | 0.76676 | 0 | 0 | 0.88457 | 0 | 1.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.4788 | 2.391% | CZ 3C | 0 | 0 | 0 | 0.0029151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029151 | 2.391% | CZ 3C | 58.2927 | 7.7001 | 8.0272 | 0.31862 | 0 | 9.2606 | 0 | 20.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 120.4903 | 2.391%
CZ 4A | 0.59189 | 0.07833 | 0.083594 | 0.18407 | 0 | 0.15171 | 0 | 0.11536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3732 | 17.79% | CZ 4A | 18.9984 | 2.5142 | 2.6832 | 18.7824 | 0 | 4.8696 | 0 | 3.7029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 56.9503 | 17.79% | CZ 4A | 5.5681 | 0.73688 | 0.7864 | 0 | 0 | 1.4272 | 0 | 1.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.1864 | 17.79% | CZ 4A | 0 | 0 | 0 | 0.18782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18782 | 17.79% | CZ 4A | 58.2927 | 7.7144 | 8.2328 | 20.5291 | 0 | 14.9413 | 0 | 11.3614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 137.6394 | 17.79%
CZ 4B | 0.59189 | 0.077923 | 0.082833 | 0.047054 | 0 | 0.14655 | 0 | 0.2039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.3184 | 0.4638% | CZ 4B | 18.9984 | 2.5012 | 2.6587 | 4.8014 | 0 | 4.704 | 0 | 6.5449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 45.6083 | 0.4638% | CZ 4B | 5.5681 | 0.73305 | 0.77923 | 0 | 0 | 1.3787 | 0 | 1.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.9598 | 0.4638% | CZ 4B | 0 | 0 | 0 | 0.048014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048014 | 0.4638% | CZ 4B | 58.2927 | 7.6743 | 8.1578 | 5.248 | 0 | 14.4332 | 0 | 20.0816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 130.4553 | 0.4638%
CZ 4C | 0.59189 | 0.078382 | 0.08425 | 0.11718 | 0 | 0.043989 | 0 | 0.20751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.2914 | 2.358% | CZ 4C | 18.9984 | 2.5159 | 2.7043 | 11.9568 | 0 | 1.412 | 0 | 6.6608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 49.6478 | 2.358% | CZ 4C | 5.5681 | 0.73737 | 0.79257 | 0 | 0 | 0.41382 | 0 | 1.9522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.0466 | 2.358% | CZ 4C | 0 | 0 | 0 | 0.11957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11957 | 2.358% | CZ 4C | 58.2927 | 7.7195 | 8.2974 | 13.0688 | 0 | 4.3323 | 0 | 20.4372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 128.7156 | 2.358%
CZ 5A | 0.59189 | 0.078054 | 0.085419 | 0.27197 | 0 | 0.081179 | 0 | 0.15705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4338 | 16.36% | CZ 5A | 18.9984 | 2.5054 | 2.7418 | 27.7517 | 0 | 2.6057 | 0 | 5.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 65.0436 | 16.36% | CZ 5A | 5.5681 | 0.73428 | 0.80356 | 0 | 0 | 0.76367 | 0 | 1.4775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.9296 | 16.36% | CZ 5A | 0 | 0 | 0 | 0.27752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27752 | 16.36% | CZ 5A | 58.2927 | 7.6872 | 8.4125 | 30.3326 | 0 | 7.9949 | 0 | 15.4675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 144.755 | 16.36%
CZ 5B | 0.59189 | 0.078225 | 0.084775 | 0.13027 | 0 | 0.10364 | 0 | 0.24619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4032 | 3.359% | CZ 5B | 18.9984 | 2.5108 | 2.7211 | 13.2926 | 0 | 3.3266 | 0 | 7.9021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 54.1513 | 3.359% | CZ 5B | 5.5681 | 0.73589 | 0.79751 | 0 | 0 | 0.97497 | 0 | 2.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.975 | 3.359% | CZ 5B | 0 | 0 | 0 | 0.13293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13293 | 3.359% | CZ 5B | 58.2927 | 7.704 | 8.3491 | 14.5288 | 0 | 10.2069 | 0 | 24.2459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 139.8951 | 3.359%
CZ 5C | 0.59189 | 0.078304 | 0.0853 | 0.14411 | 0 | 0.018562 | 0 | 0.19893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.2853 | 0.05591% | CZ 5C | 18.9984 | 2.5134 | 2.738 | 14.7055 | 0 | 0.59579 | 0 | 6.3852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 51.3359 | 0.05591% | CZ 5C | 5.5681 | 0.73663 | 0.80245 | 0 | 0 | 0.17462 | 0 | 1.8714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.7358 | 0.05591% | CZ 5C | 0 | 0 | 0 | 0.14705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14705 | 0.05591% | CZ 5C | 58.2927 | 7.7118 | 8.4008 | 16.0731 | 0 | 1.8281 | 0 | 19.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 128.4658 | 0.05591%
CZ 6A | 0.59189 | 0.078172 | 0.086744 | 0.37874 | 0 | 0.098414 | 0 | 0.12346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5257 | 1.584% | CZ 6A | 18.9984 | 2.5092 | 2.7843 | 38.6473 | 0 | 3.1589 | 0 | 3.9628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 75.4606 | 1.584% | CZ 6A | 5.5681 | 0.73539 | 0.81603 | 0 | 0 | 0.92582 | 0 | 1.1614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.7894 | 1.584% | CZ 6A | 0 | 0 | 0 | 0.38647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38647 | 1.584% | CZ 6A | 58.2927 | 7.6988 | 8.5431 | 42.2416 | 0 | 9.6924 | 0 | 12.1591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 155.1954 | 1.584%
CZ 6B | 0.59189 | 0.078041 | 0.086364 | 0.24236 | 0 | 0.065176 | 0 | 0.23513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4672 | 0.2227% | CZ 6B | 18.9984 | 2.505 | 2.7721 | 24.7309 | 0 | 2.092 | 0 | 7.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 64.0453 | 0.2227% | CZ 6B | 5.5681 | 0.73416 | 0.81245 | 0 | 0 | 0.61314 | 0 | 2.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.5224 | 0.2227% | CZ 6B | 0 | 0 | 0 | 0.24731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24731 | 0.2227% | CZ 6B | 58.2927 | 7.6859 | 8.5056 | 27.0308 | 0 | 6.4189 | 0 | 23.1573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 147.6589 | 0.2227%
CZ 7 | 0.59189 | 0.07833 | 0.088267 | 0.44449 | 0 | 0.062013 | 0 | 0.17413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.6074 | 0.2165% | CZ 7 | 18.9984 | 2.5142 | 2.8332 | 45.3566 | 0 | 1.9905 | 0 | 5.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 82.6819 | 0.2165% | CZ 7 | 5.5681 | 0.73688 | 0.83036 | 0 | 0 | 0.58338 | 0 | 1.6381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 10.9394 | 0.2165% | CZ 7 | 0 | 0 | 0 | 0.45357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45357 | 0.2165% | CZ 7 | 58.2927 | 7.7144 | 8.693 | 49.5748 | 0 | 6.1074 | 0 | 17.1495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 164.0994 | 0.2165%
CZ 8 | 0.59189 | 0.080548 | 0.090302 | 0.52342 | 0 | 0.020071 | 0 | 0.24818 | 0.01251 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7352 | 0.02488% | CZ 8 | 18.9984 | 2.5854 | 2.8985 | 53.4101 | 0 | 0.64425 | 0 | 7.9661 | 0.40155 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 92.3041 | 0.02488% | CZ 8 | 5.5681 | 0.75775 | 0.8495 | 0 | 0 | 0.18882 | 0 | 2.3347 | 0.11769 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 11.3992 | 0.02488% | CZ 8 | 0 | 0 | 0 | 0.5341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5341 | 0.02488% | CZ 8 | 58.2927 | 7.9328 | 8.8934 | 58.3773 | 0 | 1.9767 | 0 | 24.4424 | 1.2321 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 177.7151 | 0.02488%
US Weighted | 0.59189 | 0.078047 | 0.081874 | 0.10995 | 0 | 0.23785 | 0 | 0.14217 | 3.1124e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.41 | 100% | US Weighted | 18.9984 | 2.5051 | 2.628 | 11.2196 | 0 | 7.6345 | 0 | 4.5634 | 9.9902e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.9488 | 100% | US Weighted | 5.5681 | 0.73422 | 0.77022 | 0 | 0 | 2.2375 | 0 | 1.3374 | 2.928e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.2301 | 100% | US Weighted | 0 | 0 | 0 | 0.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1122 | 100% | US Weighted | 58.2927 | 7.6865 | 8.0634 | 12.2631 | 0 | 23.4248 | 0 | 14.0017 | 0.00030653 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 140.3002 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.72311 | 0.12074 | 0.075481 | 0 | 0 | 0.96751 | 0 | 0.16146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 2.2165 | 0% | CZ 0A | 23.2103 | 3.8756 | 2.4228 | 0 | 0 | 31.0551 | 0 | 5.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 71.1461 | 0% | CZ 0A | 6.8025 | 1.1359 | 0.71008 | 0 | 0 | 9.1017 | 0 | 1.5189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 20.8517 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 71.2159 | 11.8915 | 7.4338 | 0 | 0 | 95.2859 | 0 | 15.9019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 218.2967 | 0%
CZ 0B | 0.72311 | 0.12072 | 0.075416 | 0 | 0 | 0.83986 | 0 | 0.19359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 2.1209 | 0% | CZ 0B | 23.2103 | 3.8748 | 2.4207 | 0 | 0 | 26.9578 | 0 | 6.2137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 68.0769 | 0% | CZ 0B | 6.8025 | 1.1356 | 0.70946 | 0 | 0 | 7.9009 | 0 | 1.8211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 19.9522 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 71.2159 | 11.8889 | 7.4273 | 0 | 0 | 82.7144 | 0 | 19.0655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 208.8797 | 0%
CZ 1A | 0.72311 | 0.12073 | 0.07686 | 0 | 0 | 0.62253 | 0 | 0.12825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.8397 | 4.208% | CZ 1A | 23.2103 | 3.8752 | 2.467 | 0 | 0 | 19.9819 | 0 | 4.1166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 59.0507 | 4.208% | CZ 1A | 6.8025 | 1.1358 | 0.72304 | 0 | 0 | 5.8564 | 0 | 1.2065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 17.3068 | 4.208% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.208% | CZ 1A | 71.2159 | 11.8902 | 7.5696 | 0 | 0 | 61.3102 | 0 | 12.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 181.1845 | 4.208%
CZ 1B | 0.72311 | 0.12055 | 0.076938 | 0.0018536 | 0 | 0.66908 | 0 | 0.18294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.9427 | 0% | CZ 1B | 23.2103 | 3.8693 | 2.4696 | 0.18914 | 0 | 21.476 | 0 | 5.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 62.4859 | 0% | CZ 1B | 6.8025 | 1.134 | 0.72379 | 0 | 0 | 6.2943 | 0 | 1.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 18.2581 | 0% | CZ 1B | 0 | 0 | 0 | 0.0018914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018914 | 0% | CZ 1B | 71.2159 | 11.8721 | 7.5773 | 0.20673 | 0 | 65.8946 | 0 | 18.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 191.3513 | 0%
CZ 2A | 0.72311 | 0.12051 | 0.078474 | 0.0053337 | 0 | 0.50064 | 0 | 0.13312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7294 | 17.06% | CZ 2A | 23.2103 | 3.868 | 2.5189 | 0.54426 | 0 | 16.0696 | 0 | 4.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.8837 | 17.06% | CZ 2A | 6.8025 | 1.1337 | 0.73823 | 0 | 0 | 4.7097 | 0 | 1.2523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 16.219 | 17.06% | CZ 2A | 0 | 0 | 0 | 0.0054426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054426 | 17.06% | CZ 2A | 71.2159 | 11.8682 | 7.7286 | 0.59487 | 0 | 49.3062 | 0 | 13.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 170.3921 | 17.06%
CZ 2B | 0.72311 | 0.12061 | 0.078566 | 0.0010238 | 0 | 0.38835 | 0 | 0.16225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.6421 | 3.729% | CZ 2B | 23.2103 | 3.8714 | 2.5218 | 0.10447 | 0 | 12.4653 | 0 | 5.2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 52.7809 | 3.729% | CZ 2B | 6.8025 | 1.1346 | 0.7391 | 0 | 0 | 3.6534 | 0 | 1.5264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 15.4386 | 3.729% | CZ 2B | 0 | 0 | 0 | 0.0010447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010447 | 3.729% | CZ 2B | 71.2159 | 11.8786 | 7.7376 | 0.11419 | 0 | 38.2473 | 0 | 15.9795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 161.7407 | 3.729%
CZ 3A | 0.72311 | 0.12059 | 0.081323 | 0.066354 | 0 | 0.25924 | 0 | 0.12182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5407 | 18.76% | CZ 3A | 23.2103 | 3.8706 | 2.6103 | 6.7708 | 0 | 8.3209 | 0 | 3.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 54.0927 | 18.76% | CZ 3A | 6.8025 | 1.1344 | 0.76503 | 0 | 0 | 2.4387 | 0 | 1.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.8692 | 18.76% | CZ 3A | 0 | 0 | 0 | 0.067708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067708 | 18.76% | CZ 3A | 71.2159 | 11.876 | 8.0091 | 7.4005 | 0 | 25.5309 | 0 | 11.9975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 152.5976 | 18.76%
CZ 3B | 0.72311 | 0.12057 | 0.080562 | 0.01636 | 0 | 0.24611 | 0 | 0.13877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4937 | 11.42% | CZ 3B | 23.2103 | 3.8701 | 2.5859 | 1.6694 | 0 | 7.8995 | 0 | 4.4541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 49.089 | 11.42% | CZ 3B | 6.8025 | 1.1343 | 0.75787 | 0 | 0 | 2.3152 | 0 | 1.3054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.8979 | 11.42% | CZ 3B | 0 | 0 | 0 | 0.016694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016694 | 11.42% | CZ 3B | 71.2159 | 11.8747 | 7.9341 | 1.8247 | 0 | 24.2381 | 0 | 13.6666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 147.3218 | 11.42%
CZ 3C | 0.72311 | 0.12078 | 0.081454 | 0.0016224 | 0 | 0.10078 | 0 | 0.21517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4111 | 2.391% | CZ 3C | 23.2103 | 3.8769 | 2.6145 | 0.16555 | 0 | 3.2347 | 0 | 6.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 45.408 | 2.391% | CZ 3C | 6.8025 | 1.1362 | 0.76627 | 0 | 0 | 0.94805 | 0 | 2.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.2598 | 2.391% | CZ 3C | 0 | 0 | 0 | 0.0016555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016555 | 2.391% | CZ 3C | 71.2159 | 11.8954 | 8.022 | 0.18095 | 0 | 9.9251 | 0 | 21.1909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 138.9979 | 2.391%
CZ 4A | 0.72311 | 0.12082 | 0.083528 | 0.16336 | 0 | 0.16874 | 0 | 0.12278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5506 | 17.79% | CZ 4A | 23.2103 | 3.8781 | 2.6811 | 16.6689 | 0 | 5.4161 | 0 | 3.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 61.1951 | 17.79% | CZ 4A | 6.8025 | 1.1366 | 0.78578 | 0 | 0 | 1.5874 | 0 | 1.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.0499 | 17.79% | CZ 4A | 0 | 0 | 0 | 0.16669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16669 | 17.79% | CZ 4A | 71.2159 | 11.8993 | 8.2263 | 18.2192 | 0 | 16.6181 | 0 | 12.0919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 154.8383 | 17.79%
CZ 4B | 0.72311 | 0.12053 | 0.082754 | 0.033835 | 0 | 0.16448 | 0 | 0.19919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4921 | 0.4638% | CZ 4B | 23.2103 | 3.8689 | 2.6562 | 3.4526 | 0 | 5.2796 | 0 | 6.3936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 50.2608 | 0.4638% | CZ 4B | 6.8025 | 1.1339 | 0.77849 | 0 | 0 | 1.5474 | 0 | 1.8739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.7187 | 0.4638% | CZ 4B | 0 | 0 | 0 | 0.034526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034526 | 0.4638% | CZ 4B | 71.2159 | 11.8708 | 8.15 | 3.7737 | 0 | 16.1992 | 0 | 19.6175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 147.3948 | 0.4638%
CZ 4C | 0.72311 | 0.12081 | 0.084158 | 0.09635 | 0 | 0.047993 | 0 | 0.2176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4582 | 2.358% | CZ 4C | 23.2103 | 3.8777 | 2.7013 | 9.8316 | 0 | 1.5405 | 0 | 6.9844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 53.5454 | 2.358% | CZ 4C | 6.8025 | 1.1365 | 0.79171 | 0 | 0 | 0.45149 | 0 | 2.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.8118 | 2.358% | CZ 4C | 0 | 0 | 0 | 0.098316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.098316 | 2.358% | CZ 4C | 71.2159 | 11.898 | 8.2884 | 10.7459 | 0 | 4.7266 | 0 | 21.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 144.8725 | 2.358%
CZ 5A | 0.72311 | 0.12063 | 0.085366 | 0.25221 | 0 | 0.093203 | 0 | 0.1533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.596 | 16.36% | CZ 5A | 23.2103 | 3.8718 | 2.7401 | 25.7356 | 0 | 2.9916 | 0 | 4.9206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 68.8696 | 16.36% | CZ 5A | 6.8025 | 1.1348 | 0.80307 | 0 | 0 | 0.87679 | 0 | 1.4421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.6419 | 16.36% | CZ 5A | 0 | 0 | 0 | 0.25736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25736 | 16.36% | CZ 5A | 71.2159 | 11.8799 | 8.4073 | 28.129 | 0 | 9.1791 | 0 | 15.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 160.4766 | 16.36%
CZ 5B | 0.72311 | 0.12076 | 0.084723 | 0.12005 | 0 | 0.11772 | 0 | 0.19478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5294 | 3.359% | CZ 5B | 23.2103 | 3.876 | 2.7194 | 12.25 | 0 | 3.7787 | 0 | 6.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 57.4862 | 3.359% | CZ 5B | 6.8025 | 1.136 | 0.79702 | 0 | 0 | 1.1075 | 0 | 1.8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.258 | 3.359% | CZ 5B | 0 | 0 | 0 | 0.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1225 | 3.359% | CZ 5B | 71.2159 | 11.8928 | 8.344 | 13.3893 | 0 | 11.5942 | 0 | 19.1831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 152.1869 | 3.359%
CZ 5C | 0.72311 | 0.12074 | 0.085209 | 0.11898 | 0 | 0.024863 | 0 | 0.21401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.4551 | 0.05591% | CZ 5C | 23.2103 | 3.8756 | 2.735 | 12.1409 | 0 | 0.79804 | 0 | 6.8693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 55.0289 | 0.05591% | CZ 5C | 6.8025 | 1.1359 | 0.80159 | 0 | 0 | 0.23389 | 0 | 2.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.5697 | 0.05591% | CZ 5C | 0 | 0 | 0 | 0.12141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12141 | 0.05591% | CZ 5C | 71.2159 | 11.8915 | 8.3918 | 13.27 | 0 | 2.4486 | 0 | 21.0771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 144.8626 | 0.05591%
CZ 6A | 0.72311 | 0.12069 | 0.086692 | 0.36016 | 0 | 0.10938 | 0 | 0.12974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.698 | 1.584% | CZ 6A | 23.2103 | 3.8739 | 2.7826 | 36.7509 | 0 | 3.5107 | 0 | 4.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 79.6923 | 1.584% | CZ 6A | 6.8025 | 1.1354 | 0.81554 | 0 | 0 | 1.0289 | 0 | 1.2205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.5854 | 1.584% | CZ 6A | 0 | 0 | 0 | 0.36751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36751 | 1.584% | CZ 6A | 71.2159 | 11.8863 | 8.5379 | 40.1687 | 0 | 10.7719 | 0 | 12.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 171.9255 | 1.584%
CZ 6B | 0.72311 | 0.12055 | 0.086298 | 0.22331 | 0 | 0.06918 | 0 | 0.24851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.6392 | 0.2227% | CZ 6B | 23.2103 | 3.8693 | 2.77 | 22.7864 | 0 | 2.2205 | 0 | 7.9767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 68.2328 | 0.2227% | CZ 6B | 6.8025 | 1.134 | 0.81184 | 0 | 0 | 0.6508 | 0 | 2.3378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.3196 | 0.2227% | CZ 6B | 0 | 0 | 0 | 0.22786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22786 | 0.2227% | CZ 6B | 71.2159 | 11.8721 | 8.4991 | 24.9055 | 0 | 6.8132 | 0 | 24.4747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 164.3482 | 0.2227%
CZ 7 | 0.72311 | 0.12076 | 0.088228 | 0.43407 | 0 | 0.073788 | 0 | 0.13335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7415 | 0.2165% | CZ 7 | 23.2103 | 3.876 | 2.8319 | 44.293 | 0 | 2.3684 | 0 | 4.2801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 86.2594 | 0.2165% | CZ 7 | 6.8025 | 1.136 | 0.82999 | 0 | 0 | 0.69415 | 0 | 1.2544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.2997 | 0.2165% | CZ 7 | 0 | 0 | 0 | 0.44293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44293 | 0.2165% | CZ 7 | 71.2159 | 11.8928 | 8.6892 | 48.4122 | 0 | 7.267 | 0 | 13.1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 177.1774 | 0.2165%
CZ 8 | 0.72311 | 0.12158 | 0.090276 | 0.51392 | 0 | 0.023353 | 0 | 0.23777 | 0.012038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.8903 | 0.02488% | CZ 8 | 23.2103 | 3.9026 | 2.8977 | 52.4408 | 0 | 0.74959 | 0 | 7.632 | 0.38638 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 96.619 | 0.02488% | CZ 8 | 6.8025 | 1.1438 | 0.84925 | 0 | 0 | 0.21969 | 0 | 2.2368 | 0.11324 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 12.9479 | 0.02488% | CZ 8 | 0 | 0 | 0 | 0.52441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52441 | 0.02488% | CZ 8 | 71.2159 | 11.9742 | 8.8908 | 57.3178 | 0 | 2.3 | 0 | 23.4171 | 1.1855 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 192.8691 | 0.02488%
US Weighted | 0.72311 | 0.12064 | 0.08182 | 0.099421 | 0 | 0.2584 | 0 | 0.14059 | 2.9948e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5922 | 100% | US Weighted | 23.2103 | 3.8724 | 2.6262 | 10.145 | 0 | 8.294 | 0 | 4.5128 | 9.6128e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.0605 | 100% | US Weighted | 6.8025 | 1.1349 | 0.7697 | 0 | 0 | 2.4308 | 0 | 1.3226 | 2.8174e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.0432 | 100% | US Weighted | 0 | 0 | 0 | 0.10145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10145 | 100% | US Weighted | 71.2159 | 11.8817 | 8.058 | 11.0885 | 0 | 25.4485 | 0 | 13.8465 | 0.00029495 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 158.1071 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.80123 | 0.12074 | 0.075836 | 0 | 0 | 1.1131 | 0 | 0.33993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 2.619 | 0% | CZ 0A | 25.7178 | 3.8756 | 2.4342 | 0 | 0 | 35.7266 | 0 | 10.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 84.0648 | 0% | CZ 0A | 7.5374 | 1.1359 | 0.71341 | 0 | 0 | 10.4709 | 0 | 3.1978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 24.638 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 78.9096 | 11.8915 | 7.4687 | 0 | 0 | 109.6196 | 0 | 33.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 257.935 | 0%
CZ 0B | 0.80123 | 0.12072 | 0.075403 | 0 | 0 | 0.90142 | 0 | 0.33816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 2.4051 | 0% | CZ 0B | 25.7178 | 3.8748 | 2.4203 | 0 | 0 | 28.9336 | 0 | 10.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 77.2001 | 0% | CZ 0B | 7.5374 | 1.1356 | 0.70934 | 0 | 0 | 8.4799 | 0 | 3.1812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 22.6261 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 78.9096 | 11.8889 | 7.4261 | 0 | 0 | 88.7765 | 0 | 33.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 236.8722 | 0%
CZ 1A | 0.80123 | 0.12073 | 0.077122 | 0 | 0 | 0.71124 | 0 | 0.28905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 2.1676 | 4.208% | CZ 1A | 25.7178 | 3.8752 | 2.4755 | 0 | 0 | 22.8294 | 0 | 9.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 69.5753 | 4.208% | CZ 1A | 7.5374 | 1.1358 | 0.72551 | 0 | 0 | 6.6909 | 0 | 2.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 20.3913 | 4.208% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.208% | CZ 1A | 78.9096 | 11.8902 | 7.5954 | 0 | 0 | 70.0472 | 0 | 28.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 213.477 | 4.208%
CZ 1B | 0.80123 | 0.12055 | 0.076925 | 0.0014284 | 0 | 0.72505 | 0 | 0.34507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 2.2385 | 0% | CZ 1B | 25.7178 | 3.8693 | 2.4691 | 0.14575 | 0 | 23.2727 | 0 | 11.0761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 71.9504 | 0% | CZ 1B | 7.5374 | 1.134 | 0.72366 | 0 | 0 | 6.8208 | 0 | 3.2462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 21.0447 | 0% | CZ 1B | 0 | 0 | 0 | 0.0014575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014575 | 0% | CZ 1B | 78.9096 | 11.8721 | 7.576 | 0.15931 | 0 | 71.4072 | 0 | 33.9848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 220.4767 | 0%
CZ 2A | 0.80123 | 0.12051 | 0.078671 | 0.0041696 | 0 | 0.5631 | 0 | 0.29186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 2.0278 | 17.06% | CZ 2A | 25.7178 | 3.868 | 2.5252 | 0.42546 | 0 | 18.0744 | 0 | 9.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 65.3785 | 17.06% | CZ 2A | 7.5374 | 1.1337 | 0.74009 | 0 | 0 | 5.2973 | 0 | 2.7456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 19.0366 | 17.06% | CZ 2A | 0 | 0 | 0 | 0.0042546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0042546 | 17.06% | CZ 2A | 78.9096 | 11.8682 | 7.748 | 0.46503 | 0 | 55.4575 | 0 | 28.7436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 199.7596 | 17.06%
CZ 2B | 0.80123 | 0.12061 | 0.078553 | 0.0006275 | 0 | 0.4262 | 0 | 0.33214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.9276 | 3.729% | CZ 2B | 25.7178 | 3.8714 | 2.5214 | 0.06403 | 0 | 13.6801 | 0 | 10.6611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 61.9155 | 3.729% | CZ 2B | 7.5374 | 1.1346 | 0.73898 | 0 | 0 | 4.0094 | 0 | 3.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 18.1276 | 3.729% | CZ 2B | 0 | 0 | 0 | 0.0006403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0006403 | 3.729% | CZ 2B | 78.9096 | 11.8786 | 7.7363 | 0.069985 | 0 | 41.9745 | 0 | 32.7113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 189.848 | 3.729%
CZ 3A | 0.80123 | 0.12059 | 0.081415 | 0.059022 | 0 | 0.28796 | 0 | 0.25598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7744 | 18.76% | CZ 3A | 25.7178 | 3.8706 | 2.6132 | 6.0226 | 0 | 9.2428 | 0 | 8.2164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 61.0831 | 18.76% | CZ 3A | 7.5374 | 1.1344 | 0.7659 | 0 | 0 | 2.7089 | 0 | 2.4081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 16.1373 | 18.76% | CZ 3A | 0 | 0 | 0 | 0.060226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.060226 | 18.76% | CZ 3A | 78.9096 | 11.876 | 8.0182 | 6.5827 | 0 | 28.3597 | 0 | 25.2103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 175.5241 | 18.76%
CZ 3B | 0.80123 | 0.12057 | 0.080535 | 0.010779 | 0 | 0.26626 | 0 | 0.28813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7357 | 11.42% | CZ 3B | 25.7178 | 3.8701 | 2.585 | 1.0999 | 0 | 8.5463 | 0 | 9.2483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 56.4671 | 11.42% | CZ 3B | 7.5374 | 1.1343 | 0.75762 | 0 | 0 | 2.5048 | 0 | 2.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 16.2272 | 11.42% | CZ 3B | 0 | 0 | 0 | 0.010999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010999 | 11.42% | CZ 3B | 78.9096 | 11.8747 | 7.9316 | 1.2022 | 0 | 26.2226 | 0 | 28.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 171.0847 | 11.42%
CZ 3C | 0.80123 | 0.12078 | 0.081494 | 0.001061 | 0 | 0.10629 | 0 | 0.28817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5673 | 2.391% | CZ 3C | 25.7178 | 3.8769 | 2.6158 | 0.10826 | 0 | 3.4117 | 0 | 9.2496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 50.3796 | 2.391% | CZ 3C | 7.5374 | 1.1362 | 0.76664 | 0 | 0 | 0.99991 | 0 | 2.7109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.7337 | 2.391% | CZ 3C | 0 | 0 | 0 | 0.0010826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010826 | 2.391% | CZ 3C | 78.9096 | 11.8954 | 8.0259 | 0.11833 | 0 | 10.4681 | 0 | 28.3803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 154.3653 | 2.391%
CZ 4A | 0.80123 | 0.12082 | 0.083633 | 0.15929 | 0 | 0.18347 | 0 | 0.24904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7657 | 17.79% | CZ 4A | 25.7178 | 3.8781 | 2.6844 | 16.254 | 0 | 5.8888 | 0 | 7.9935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 67.8164 | 17.79% | CZ 4A | 7.5374 | 1.1366 | 0.78677 | 0 | 0 | 1.7259 | 0 | 2.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 15.1121 | 17.79% | CZ 4A | 0 | 0 | 0 | 0.16254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16254 | 17.79% | CZ 4A | 78.9096 | 11.8993 | 8.2367 | 17.7656 | 0 | 18.0687 | 0 | 24.5264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 175.9739 | 17.79%
CZ 4B | 0.80123 | 0.12053 | 0.082885 | 0.035454 | 0 | 0.18705 | 0 | 0.30613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7015 | 0.4638% | CZ 4B | 25.7178 | 3.8689 | 2.6604 | 3.6177 | 0 | 6.0039 | 0 | 9.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 57.0943 | 0.4638% | CZ 4B | 7.5374 | 1.1339 | 0.77973 | 0 | 0 | 1.7596 | 0 | 2.8798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 15.6731 | 0.4638% | CZ 4B | 0 | 0 | 0 | 0.036177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036177 | 0.4638% | CZ 4B | 78.9096 | 11.8708 | 8.163 | 3.9542 | 0 | 18.4216 | 0 | 30.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 168.0358 | 0.4638%
CZ 4C | 0.80123 | 0.12081 | 0.084237 | 0.098018 | 0 | 0.052062 | 0 | 0.28963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.6142 | 2.358% | CZ 4C | 25.7178 | 3.8777 | 2.7038 | 10.0018 | 0 | 1.6711 | 0 | 9.2963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 58.6682 | 2.358% | CZ 4C | 7.5374 | 1.1365 | 0.79245 | 0 | 0 | 0.48977 | 0 | 2.7246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.2633 | 2.358% | CZ 4C | 0 | 0 | 0 | 0.10002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10002 | 2.358% | CZ 4C | 78.9096 | 11.898 | 8.2961 | 10.932 | 0 | 5.1274 | 0 | 28.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 160.2545 | 2.358%
CZ 5A | 0.80123 | 0.12063 | 0.085458 | 0.26335 | 0 | 0.10036 | 0 | 0.23511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7744 | 16.36% | CZ 5A | 25.7178 | 3.8718 | 2.743 | 26.8725 | 0 | 3.2213 | 0 | 7.5465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 75.3725 | 16.36% | CZ 5A | 7.5374 | 1.1348 | 0.80393 | 0 | 0 | 0.9441 | 0 | 2.2117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.2145 | 16.36% | CZ 5A | 0 | 0 | 0 | 0.26873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26873 | 16.36% | CZ 5A | 78.9096 | 11.8799 | 8.4164 | 29.3717 | 0 | 9.8837 | 0 | 23.1547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 178.1836 | 16.36%
CZ 5B | 0.80123 | 0.12076 | 0.084841 | 0.12973 | 0 | 0.1281 | 0 | 0.28595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7188 | 3.359% | CZ 5B | 25.7178 | 3.876 | 2.7232 | 13.2374 | 0 | 4.1116 | 0 | 9.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 64.244 | 3.359% | CZ 5B | 7.5374 | 1.136 | 0.79813 | 0 | 0 | 1.205 | 0 | 2.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.9492 | 3.359% | CZ 5B | 0 | 0 | 0 | 0.13237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13237 | 3.359% | CZ 5B | 78.9096 | 11.8928 | 8.3556 | 14.4685 | 0 | 12.6155 | 0 | 28.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 170.9715 | 3.359%
CZ 5C | 0.80123 | 0.12074 | 0.085287 | 0.12689 | 0 | 0.019665 | 0 | 0.27463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.5967 | 0.05591% | CZ 5C | 25.7178 | 3.8756 | 2.7375 | 12.9476 | 0 | 0.63119 | 0 | 8.8152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 60.1245 | 0.05591% | CZ 5C | 7.5374 | 1.1359 | 0.80233 | 0 | 0 | 0.18499 | 0 | 2.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 13.8268 | 0.05591% | CZ 5C | 0 | 0 | 0 | 0.12948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12948 | 0.05591% | CZ 5C | 78.9096 | 11.8915 | 8.3996 | 14.1517 | 0 | 1.9367 | 0 | 27.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 158.9041 | 0.05591%
CZ 6A | 0.80123 | 0.12069 | 0.086784 | 0.37097 | 0 | 0.12027 | 0 | 0.25145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.9196 | 1.584% | CZ 6A | 25.7178 | 3.8739 | 2.7856 | 37.8546 | 0 | 3.8604 | 0 | 8.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 87.563 | 1.584% | CZ 6A | 7.5374 | 1.1354 | 0.8164 | 0 | 0 | 1.1314 | 0 | 2.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.5687 | 1.584% | CZ 6A | 0 | 0 | 0 | 0.37855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37855 | 1.584% | CZ 6A | 78.9096 | 11.8863 | 8.5469 | 41.375 | 0 | 11.845 | 0 | 24.7643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 193.8948 | 1.584%
CZ 6B | 0.80123 | 0.12055 | 0.086416 | 0.24695 | 0 | 0.081165 | 0 | 0.27827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.7828 | 0.2227% | CZ 6B | 25.7178 | 3.8693 | 2.7738 | 25.1993 | 0 | 2.6052 | 0 | 8.9319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 74.4969 | 0.2227% | CZ 6B | 7.5374 | 1.134 | 0.81295 | 0 | 0 | 0.76355 | 0 | 2.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.4483 | 0.2227% | CZ 6B | 0 | 0 | 0 | 0.25199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25199 | 0.2227% | CZ 6B | 78.9096 | 11.8721 | 8.5107 | 27.5428 | 0 | 7.9936 | 0 | 27.4055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 178.8021 | 0.2227%
CZ 7 | 0.80123 | 0.12076 | 0.088333 | 0.46017 | 0 | 0.079826 | 0 | 0.25631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.9749 | 0.2165% | CZ 7 | 25.7178 | 3.876 | 2.8353 | 46.9561 | 0 | 2.5623 | 0 | 8.2269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 95.5741 | 0.2165% | CZ 7 | 7.5374 | 1.136 | 0.83098 | 0 | 0 | 0.75095 | 0 | 2.4112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.2491 | 0.2165% | CZ 7 | 0 | 0 | 0 | 0.46956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46956 | 0.2165% | CZ 7 | 78.9096 | 11.8928 | 8.6995 | 51.323 | 0 | 7.8617 | 0 | 25.2426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 200.4969 | 0.2165%
CZ 8 | 0.80123 | 0.12158 | 0.090473 | 0.69596 | 0 | 0.026149 | 0 | 0.28794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 2.1916 | 0.02488% | CZ 8 | 25.7178 | 3.9026 | 2.904 | 71.0164 | 0 | 0.83934 | 0 | 9.2424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 119.0221 | 0.02488% | CZ 8 | 7.5374 | 1.1438 | 0.85111 | 0 | 0 | 0.246 | 0 | 2.7088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 14.0697 | 0.02488% | CZ 8 | 0 | 0 | 0 | 0.71016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71016 | 0.02488% | CZ 8 | 78.9096 | 11.9742 | 8.9102 | 77.6209 | 0 | 2.5753 | 0 | 28.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 224.9163 | 0.02488%
US Weighted | 0.80123 | 0.12064 | 0.081921 | 0.098982 | 0 | 0.28657 | 0 | 0.26815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16822 | 1.8257 | 100% | US Weighted | 25.7178 | 3.8724 | 2.6295 | 10.1002 | 0 | 9.1982 | 0 | 8.6071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3997 | 65.5249 | 100% | US Weighted | 7.5374 | 1.1349 | 0.77066 | 0 | 0 | 2.6958 | 0 | 2.5226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5825 | 16.244 | 100% | US Weighted | 0 | 0 | 0 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.101 | 100% | US Weighted | 78.9096 | 11.8817 | 8.068 | 11.0396 | 0 | 28.2227 | 0 | 26.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5677 | 181.0984 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.89433 | 0.2195 | 0.082872 | 0 | 0 | 1.4869 | 0 | 0.42808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 3.2807 | 0% | CZ 0A | 28.706 | 7.0455 | 2.66 | 0 | 0 | 47.7268 | 0 | 13.7404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 105.3023 | 0% | CZ 0A | 8.4133 | 2.0649 | 0.7796 | 0 | 0 | 13.9879 | 0 | 4.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 30.8623 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 88.0783 | 21.6175 | 8.1617 | 0 | 0 | 146.4396 | 0 | 42.1594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 323.0979 | 0%
CZ 0B | 0.89433 | 0.21954 | 0.082189 | 0 | 0 | 1.221 | 0 | 0.47455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 3.0606 | 0% | CZ 0B | 28.706 | 7.0467 | 2.6381 | 0 | 0 | 39.1927 | 0 | 15.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 98.2392 | 0% | CZ 0B | 8.4133 | 2.0653 | 0.77318 | 0 | 0 | 11.4867 | 0 | 4.4642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 28.7922 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 88.0783 | 21.6214 | 8.0944 | 0 | 0 | 120.2545 | 0 | 46.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 301.4261 | 0%
CZ 1A | 0.89433 | 0.21957 | 0.084158 | 0 | 0 | 0.99685 | 0 | 0.38469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.7486 | 4.208% | CZ 1A | 28.706 | 7.0476 | 2.7013 | 0 | 0 | 31.9968 | 0 | 12.3478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 88.2231 | 4.208% | CZ 1A | 8.4133 | 2.0655 | 0.79171 | 0 | 0 | 9.3777 | 0 | 3.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 25.8567 | 4.208% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.208% | CZ 1A | 88.0783 | 21.624 | 8.2884 | 0 | 0 | 98.1754 | 0 | 37.8866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 270.694 | 4.208%
CZ 1B | 0.89433 | 0.21929 | 0.083765 | 0.00063988 | 0 | 0.99559 | 0 | 0.45806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.8206 | 0% | CZ 1B | 28.706 | 7.0387 | 2.6887 | 0.065294 | 0 | 31.9563 | 0 | 14.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 90.5814 | 0% | CZ 1B | 8.4133 | 2.0629 | 0.788 | 0 | 0 | 9.3659 | 0 | 4.3091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 26.5288 | 0% | CZ 1B | 0 | 0 | 0 | 0.00065294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00065294 | 0% | CZ 1B | 88.0783 | 21.5968 | 8.2496 | 0.071366 | 0 | 98.0513 | 0 | 45.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 277.801 | 0%
CZ 2A | 0.89433 | 0.21921 | 0.085734 | 0.0043017 | 0 | 0.83489 | 0 | 0.38792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.5954 | 17.06% | CZ 2A | 28.706 | 7.0362 | 2.7519 | 0.43894 | 0 | 26.7981 | 0 | 12.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 83.6063 | 17.06% | CZ 2A | 8.4133 | 2.0622 | 0.80653 | 0 | 0 | 7.8541 | 0 | 3.6493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 24.3749 | 17.06% | CZ 2A | 0 | 0 | 0 | 0.0043894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043894 | 17.06% | CZ 2A | 88.0783 | 21.5891 | 8.4435 | 0.47977 | 0 | 82.2244 | 0 | 38.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 255.6611 | 17.06%
CZ 2B | 0.89433 | 0.21937 | 0.085471 | 0.0010816 | 0 | 0.65107 | 0 | 0.44644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.4667 | 3.729% | CZ 2B | 28.706 | 7.0413 | 2.7434 | 0.11037 | 0 | 20.8979 | 0 | 14.3298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 79.2525 | 3.729% | CZ 2B | 8.4133 | 2.0637 | 0.80406 | 0 | 0 | 6.1248 | 0 | 4.1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 23.1952 | 3.729% | CZ 2B | 0 | 0 | 0 | 0.0011037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011037 | 3.729% | CZ 2B | 88.0783 | 21.6046 | 8.4177 | 0.12063 | 0 | 64.1208 | 0 | 43.9681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 242.9515 | 3.729%
CZ 3A | 0.89433 | 0.21933 | 0.088608 | 0.058229 | 0 | 0.45211 | 0 | 0.34796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2295 | 18.76% | CZ 3A | 28.706 | 7.04 | 2.8441 | 5.9418 | 0 | 14.5119 | 0 | 11.1688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 75.6363 | 18.76% | CZ 3A | 8.4133 | 2.0633 | 0.83357 | 0 | 0 | 4.2532 | 0 | 3.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.4263 | 18.76% | CZ 3A | 0 | 0 | 0 | 0.059418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059418 | 18.76% | CZ 3A | 88.0783 | 21.6007 | 8.7266 | 6.4943 | 0 | 44.5266 | 0 | 34.2692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 220.3372 | 18.76%
CZ 3B | 0.89433 | 0.21933 | 0.087493 | 0.0055525 | 0 | 0.38482 | 0 | 0.40081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.1613 | 11.42% | CZ 3B | 28.706 | 7.04 | 2.8083 | 0.56658 | 0 | 12.352 | 0 | 12.8652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 69.7618 | 11.42% | CZ 3B | 8.4133 | 2.0633 | 0.82307 | 0 | 0 | 3.6202 | 0 | 3.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.28 | 11.42% | CZ 3B | 0 | 0 | 0 | 0.0056658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056658 | 11.42% | CZ 3B | 88.0783 | 21.6007 | 8.6168 | 0.61928 | 0 | 37.8995 | 0 | 39.4742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 212.9301 | 11.42%
CZ 3C | 0.89433 | 0.21929 | 0.088543 | 0.0010114 | 0 | 0.2054 | 0 | 0.31983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 1.8974 | 2.391% | CZ 3C | 28.706 | 7.0387 | 2.842 | 0.10321 | 0 | 6.5929 | 0 | 10.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 60.9725 | 2.391% | CZ 3C | 8.4133 | 2.0629 | 0.83295 | 0 | 0 | 1.9323 | 0 | 3.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.8398 | 2.391% | CZ 3C | 0 | 0 | 0 | 0.0010321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010321 | 2.391% | CZ 3C | 88.0783 | 21.5968 | 8.7202 | 0.1128 | 0 | 20.229 | 0 | 31.4987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 186.8772 | 2.391%
CZ 4A | 0.89433 | 0.219 | 0.090985 | 0.16401 | 0 | 0.28693 | 0 | 0.32477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.149 | 17.79% | CZ 4A | 28.706 | 7.0295 | 2.9204 | 16.7359 | 0 | 9.21 | 0 | 10.4243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 80.4497 | 17.79% | CZ 4A | 8.4133 | 2.0602 | 0.85592 | 0 | 0 | 2.6993 | 0 | 3.0552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 18.6735 | 17.79% | CZ 4A | 0 | 0 | 0 | 0.16736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16736 | 17.79% | CZ 4A | 88.0783 | 21.5684 | 8.9606 | 18.2924 | 0 | 28.2588 | 0 | 31.9848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 213.7847 | 17.79%
CZ 4B | 0.89433 | 0.21916 | 0.090052 | 0.027028 | 0 | 0.24914 | 0 | 0.40252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.0512 | 0.4638% | CZ 4B | 28.706 | 7.0345 | 2.8905 | 2.7579 | 0 | 7.9969 | 0 | 12.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 67.7295 | 0.4638% | CZ 4B | 8.4133 | 2.0617 | 0.84715 | 0 | 0 | 2.3438 | 0 | 3.7866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 19.0421 | 0.4638% | CZ 4B | 0 | 0 | 0 | 0.027579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027579 | 0.4638% | CZ 4B | 88.0783 | 21.5839 | 8.8689 | 3.0144 | 0 | 24.5367 | 0 | 39.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 202.3659 | 0.4638%
CZ 4C | 0.89433 | 0.21875 | 0.091562 | 0.10049 | 0 | 0.086626 | 0 | 0.30758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 1.8683 | 2.358% | CZ 4C | 28.706 | 7.0214 | 2.9389 | 10.2545 | 0 | 2.7805 | 0 | 9.8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 66.9979 | 2.358% | CZ 4C | 8.4133 | 2.0579 | 0.86136 | 0 | 0 | 0.81492 | 0 | 2.8935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 16.6305 | 2.358% | CZ 4C | 0 | 0 | 0 | 0.10255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10255 | 2.358% | CZ 4C | 88.0783 | 21.5438 | 9.0175 | 11.2082 | 0 | 8.5314 | 0 | 30.2924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 185.3132 | 2.358%
CZ 5A | 0.89433 | 0.21907 | 0.092888 | 0.27223 | 0 | 0.16836 | 0 | 0.30665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.1225 | 16.36% | CZ 5A | 28.706 | 7.0316 | 2.9815 | 27.779 | 0 | 5.4039 | 0 | 9.8428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 87.1685 | 16.36% | CZ 5A | 8.4133 | 2.0608 | 0.87383 | 0 | 0 | 1.5838 | 0 | 2.8848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.4061 | 16.36% | CZ 5A | 0 | 0 | 0 | 0.27779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27779 | 16.36% | CZ 5A | 88.0783 | 21.5749 | 9.1481 | 30.3625 | 0 | 16.5806 | 0 | 30.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 212.5865 | 16.36%
CZ 5B | 0.89433 | 0.21907 | 0.09214 | 0.12031 | 0 | 0.21049 | 0 | 0.37554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.0809 | 3.359% | CZ 5B | 28.706 | 7.0316 | 2.9575 | 12.2765 | 0 | 6.7564 | 0 | 12.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 75.2058 | 3.359% | CZ 5B | 8.4133 | 2.0608 | 0.86679 | 0 | 0 | 1.9802 | 0 | 3.5329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 18.4435 | 3.359% | CZ 5B | 0 | 0 | 0 | 0.12277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12277 | 3.359% | CZ 5B | 88.0783 | 21.5749 | 9.0744 | 13.4183 | 0 | 20.7306 | 0 | 36.9855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 206.5034 | 3.359%
CZ 5C | 0.89433 | 0.21873 | 0.092639 | 0.12286 | 0 | 0.042059 | 0 | 0.29417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 1.8338 | 0.05591% | CZ 5C | 28.706 | 7.0206 | 2.9735 | 12.5369 | 0 | 1.35 | 0 | 9.4421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 67.4528 | 0.05591% | CZ 5C | 8.4133 | 2.0576 | 0.87148 | 0 | 0 | 0.39567 | 0 | 2.7673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 16.0949 | 0.05591% | CZ 5C | 0 | 0 | 0 | 0.12537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12537 | 0.05591% | CZ 5C | 88.0783 | 21.5412 | 9.1235 | 13.7028 | 0 | 4.1422 | 0 | 28.9712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 182.2007 | 0.05591%
CZ 6A | 0.89433 | 0.21896 | 0.094253 | 0.38715 | 0 | 0.19183 | 0 | 0.32572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2812 | 1.584% | CZ 6A | 28.706 | 7.0282 | 3.0253 | 39.5046 | 0 | 6.1572 | 0 | 10.4551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 100.3001 | 1.584% | CZ 6A | 8.4133 | 2.0598 | 0.88667 | 0 | 0 | 1.8046 | 0 | 3.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.8181 | 1.584% | CZ 6A | 0 | 0 | 0 | 0.39505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39505 | 1.584% | CZ 6A | 88.0783 | 21.5645 | 9.2826 | 43.1785 | 0 | 18.8922 | 0 | 32.0791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 229.7167 | 1.584%
CZ 6B | 0.89433 | 0.2188 | 0.093833 | 0.24239 | 0 | 0.13815 | 0 | 0.35848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.115 | 0.2227% | CZ 6B | 28.706 | 7.0231 | 3.0118 | 24.7338 | 0 | 4.4343 | 0 | 11.5063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 84.8391 | 0.2227% | CZ 6B | 8.4133 | 2.0584 | 0.88272 | 0 | 0 | 1.2996 | 0 | 3.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.6159 | 0.2227% | CZ 6B | 0 | 0 | 0 | 0.24734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24734 | 0.2227% | CZ 6B | 88.0783 | 21.549 | 9.2412 | 27.0341 | 0 | 13.6058 | 0 | 35.3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 211.4546 | 0.2227%
CZ 7 | 0.89433 | 0.21867 | 0.095828 | 0.47952 | 0 | 0.14377 | 0 | 0.32722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.3283 | 0.2165% | CZ 7 | 28.706 | 7.0189 | 3.0759 | 48.931 | 0 | 4.6147 | 0 | 10.5031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 108.2732 | 0.2165% | CZ 7 | 8.4133 | 2.0571 | 0.90149 | 0 | 0 | 1.3525 | 0 | 3.0783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.3922 | 0.2165% | CZ 7 | 0 | 0 | 0 | 0.48931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48931 | 0.2165% | CZ 7 | 88.0783 | 21.5361 | 9.4377 | 53.4815 | 0 | 14.1591 | 0 | 32.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 235.5607 | 0.2165%
CZ 8 | 0.89433 | 0.21746 | 0.098047 | 0.72156 | 0 | 0.070322 | 0 | 0.35479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.5255 | 0.02488% | CZ 8 | 28.706 | 6.9802 | 3.1471 | 73.6281 | 0 | 2.2572 | 0 | 11.3879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 131.5302 | 0.02488% | CZ 8 | 8.4133 | 2.0458 | 0.92236 | 0 | 0 | 0.66155 | 0 | 3.3376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 16.9701 | 0.02488% | CZ 8 | 0 | 0 | 0 | 0.73628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73628 | 0.02488% | CZ 8 | 88.0783 | 21.4171 | 9.6562 | 80.4755 | 0 | 6.9257 | 0 | 34.9415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 258.1358 | 0.02488%
US Weighted | 0.89433 | 0.21919 | 0.089124 | 0.10056 | 0 | 0.43486 | 0 | 0.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2613 | 100% | US Weighted | 28.706 | 7.0354 | 2.8607 | 10.2616 | 0 | 13.958 | 0 | 11.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 79.6176 | 100% | US Weighted | 8.4133 | 2.062 | 0.83842 | 0 | 0 | 4.0908 | 0 | 3.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.3271 | 100% | US Weighted | 0 | 0 | 0 | 0.10262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10262 | 100% | US Weighted | 88.0783 | 21.5866 | 8.7774 | 11.2159 | 0 | 42.827 | 0 | 34.8934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 224.0201 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 22500 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.8297 | 0.2195 | 0.082872 | 0 | 0 | 1.5509 | 0 | 0.41956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 3.2715 | 0% | CZ 0A | 26.6317 | 7.0455 | 2.66 | 0 | 0 | 49.7813 | 0 | 13.4669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 105.0091 | 0% | CZ 0A | 7.8053 | 2.0649 | 0.7796 | 0 | 0 | 14.5901 | 0 | 3.9469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 30.7764 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 81.7137 | 21.6175 | 8.1617 | 0 | 0 | 152.7434 | 0 | 41.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 322.1981 | 0%
CZ 0B | 0.8297 | 0.21954 | 0.082216 | 0 | 0 | 1.267 | 0 | 0.46665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 3.034 | 0% | CZ 0B | 26.6317 | 7.0467 | 2.6389 | 0 | 0 | 40.6666 | 0 | 14.9783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 97.3859 | 0% | CZ 0B | 7.8053 | 2.0653 | 0.77343 | 0 | 0 | 11.9187 | 0 | 4.3899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 28.5422 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 81.7137 | 21.6214 | 8.097 | 0 | 0 | 124.7768 | 0 | 45.9577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 298.8081 | 0%
CZ 1A | 0.8297 | 0.21957 | 0.084158 | 0 | 0 | 1.02 | 0 | 0.37365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.6961 | 4.208% | CZ 1A | 26.6317 | 7.0476 | 2.7013 | 0 | 0 | 32.7401 | 0 | 11.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 86.5377 | 4.208% | CZ 1A | 7.8053 | 2.0655 | 0.79171 | 0 | 0 | 9.5956 | 0 | 3.5151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 25.3628 | 4.208% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.208% | CZ 1A | 81.7137 | 21.624 | 8.2884 | 0 | 0 | 100.456 | 0 | 36.7993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 265.5227 | 4.208%
CZ 1B | 0.8297 | 0.21929 | 0.083817 | 0.0016018 | 0 | 1.0238 | 0 | 0.44976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.777 | 0% | CZ 1B | 26.6317 | 7.0387 | 2.6903 | 0.16345 | 0 | 32.8618 | 0 | 14.4364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 89.2462 | 0% | CZ 1B | 7.8053 | 2.0629 | 0.7885 | 0 | 0 | 9.6313 | 0 | 4.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 26.1086 | 0% | CZ 1B | 0 | 0 | 0 | 0.0016345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016345 | 0% | CZ 1B | 81.7137 | 21.5968 | 8.2548 | 0.17865 | 0 | 100.8296 | 0 | 44.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 273.5101 | 0%
CZ 2A | 0.8297 | 0.21921 | 0.085812 | 0.010721 | 0 | 0.87196 | 0 | 0.39677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.5832 | 17.06% | CZ 2A | 26.6317 | 7.0362 | 2.7544 | 1.094 | 0 | 27.988 | 0 | 12.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 83.6634 | 17.06% | CZ 2A | 7.8053 | 2.0622 | 0.80727 | 0 | 0 | 8.2028 | 0 | 3.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 24.1997 | 17.06% | CZ 2A | 0 | 0 | 0 | 0.01094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01094 | 17.06% | CZ 2A | 81.7137 | 21.5891 | 8.4513 | 1.1957 | 0 | 85.8754 | 0 | 39.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 254.5425 | 17.06%
CZ 2B | 0.8297 | 0.21937 | 0.085589 | 0.0036824 | 0 | 0.6722 | 0 | 0.45922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.4387 | 3.729% | CZ 2B | 26.6317 | 7.0413 | 2.7472 | 0.37576 | 0 | 21.5763 | 0 | 14.7398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 78.5357 | 3.729% | CZ 2B | 7.8053 | 2.0637 | 0.80517 | 0 | 0 | 6.3236 | 0 | 4.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 22.9074 | 3.729% | CZ 2B | 0 | 0 | 0 | 0.0037576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037576 | 3.729% | CZ 2B | 81.7137 | 21.6046 | 8.4293 | 0.4107 | 0 | 66.2023 | 0 | 45.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 240.2279 | 3.729%
CZ 3A | 0.8297 | 0.21933 | 0.088766 | 0.1161 | 0 | 0.48291 | 0 | 0.38348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2893 | 18.76% | CZ 3A | 26.6317 | 7.04 | 2.8492 | 11.8473 | 0 | 15.5004 | 0 | 12.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 81.6012 | 18.76% | CZ 3A | 7.8053 | 2.0633 | 0.83505 | 0 | 0 | 4.5429 | 0 | 3.6076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.4437 | 18.76% | CZ 3A | 0 | 0 | 0 | 0.11847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11847 | 18.76% | CZ 3A | 81.7137 | 21.6007 | 8.7422 | 12.9491 | 0 | 47.5596 | 0 | 37.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 226.9742 | 18.76%
CZ 3B | 0.8297 | 0.21933 | 0.087716 | 0.025802 | 0 | 0.42213 | 0 | 0.43834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.192 | 11.42% | CZ 3B | 26.6317 | 7.04 | 2.8155 | 2.6328 | 0 | 13.5495 | 0 | 14.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 72.163 | 11.42% | CZ 3B | 7.8053 | 2.0633 | 0.82517 | 0 | 0 | 3.9711 | 0 | 4.1236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.3781 | 11.42% | CZ 3B | 0 | 0 | 0 | 0.026328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026328 | 11.42% | CZ 3B | 81.7137 | 21.6007 | 8.6387 | 2.8777 | 0 | 41.5737 | 0 | 43.1704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 216.2163 | 11.42%
CZ 3C | 0.8297 | 0.21929 | 0.088687 | 0.0037609 | 0 | 0.1683 | 0 | 0.36318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 1.8419 | 2.391% | CZ 3C | 26.6317 | 7.0387 | 2.8467 | 0.38376 | 0 | 5.4022 | 0 | 11.6572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 59.3839 | 2.391% | CZ 3C | 7.8053 | 2.0629 | 0.83431 | 0 | 0 | 1.5833 | 0 | 3.4165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.2919 | 2.391% | CZ 3C | 0 | 0 | 0 | 0.0038376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038376 | 2.391% | CZ 3C | 81.7137 | 21.5968 | 8.7344 | 0.41945 | 0 | 16.5755 | 0 | 35.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 181.4488 | 2.391%
CZ 4A | 0.8297 | 0.219 | 0.091208 | 0.31168 | 0 | 0.29325 | 0 | 0.34796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2618 | 17.79% | CZ 4A | 26.6317 | 7.0295 | 2.9276 | 31.8041 | 0 | 9.4126 | 0 | 11.1688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 94.398 | 17.79% | CZ 4A | 7.8053 | 2.0602 | 0.85802 | 0 | 0 | 2.7587 | 0 | 3.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 18.3452 | 17.79% | CZ 4A | 0 | 0 | 0 | 0.31804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31804 | 17.79% | CZ 4A | 81.7137 | 21.5684 | 8.9826 | 34.7619 | 0 | 28.8807 | 0 | 34.2692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 226.8179 | 17.79%
CZ 4B | 0.8297 | 0.21916 | 0.090381 | 0.092911 | 0 | 0.27074 | 0 | 0.43228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.1041 | 0.4638% | CZ 4B | 26.6317 | 7.0345 | 2.901 | 9.4807 | 0 | 8.69 | 0 | 13.8752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 74.0368 | 0.4638% | CZ 4B | 7.8053 | 2.0617 | 0.85024 | 0 | 0 | 2.5469 | 0 | 4.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 18.9203 | 0.4638% | CZ 4B | 0 | 0 | 0 | 0.094807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094807 | 0.4638% | CZ 4B | 81.7137 | 21.5839 | 8.9012 | 10.3624 | 0 | 26.6635 | 0 | 42.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 208.4391 | 0.4638%
CZ 4C | 0.8297 | 0.21875 | 0.09189 | 0.2273 | 0 | 0.074576 | 0 | 0.32691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 1.9381 | 2.358% | CZ 4C | 26.6317 | 7.0214 | 2.9495 | 23.1937 | 0 | 2.3937 | 0 | 10.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 78.1067 | 2.358% | CZ 4C | 7.8053 | 2.0579 | 0.86444 | 0 | 0 | 0.70156 | 0 | 3.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 16.0941 | 2.358% | CZ 4C | 0 | 0 | 0 | 0.23194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23194 | 2.358% | CZ 4C | 81.7137 | 21.5438 | 9.0499 | 25.3507 | 0 | 7.3446 | 0 | 32.1955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 193.8396 | 2.358%
CZ 5A | 0.8297 | 0.21907 | 0.093098 | 0.44598 | 0 | 0.16052 | 0 | 0.32693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2443 | 16.36% | CZ 5A | 26.6317 | 7.0316 | 2.9882 | 45.5079 | 0 | 5.1523 | 0 | 10.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 103.2292 | 16.36% | CZ 5A | 7.8053 | 2.0608 | 0.8758 | 0 | 0 | 1.5101 | 0 | 3.0756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 16.9171 | 16.36% | CZ 5A | 0 | 0 | 0 | 0.45508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45508 | 16.36% | CZ 5A | 81.7137 | 21.5749 | 9.1688 | 49.7401 | 0 | 15.8088 | 0 | 32.1981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 226.8457 | 16.36%
CZ 5B | 0.8297 | 0.21907 | 0.092376 | 0.22889 | 0 | 0.2112 | 0 | 0.40438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.1546 | 3.359% | CZ 5B | 26.6317 | 7.0316 | 2.9651 | 23.3563 | 0 | 6.7792 | 0 | 12.9798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 85.1673 | 3.359% | CZ 5B | 7.8053 | 2.0608 | 0.86901 | 0 | 0 | 1.9869 | 0 | 3.8042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 18.1158 | 3.359% | CZ 5B | 0 | 0 | 0 | 0.23356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23356 | 3.359% | CZ 5B | 81.7137 | 21.5749 | 9.0977 | 25.5285 | 0 | 20.8004 | 0 | 39.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 215.1824 | 3.359%
CZ 5C | 0.8297 | 0.21873 | 0.09298 | 0.27155 | 0 | 0.03203 | 0 | 0.28888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 1.9028 | 0.05591% | CZ 5C | 26.6317 | 7.0206 | 2.9845 | 27.7095 | 0 | 1.0281 | 0 | 9.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 80.0704 | 0.05591% | CZ 5C | 7.8053 | 2.0576 | 0.87469 | 0 | 0 | 0.30132 | 0 | 2.7176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 15.3461 | 0.05591% | CZ 5C | 0 | 0 | 0 | 0.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2771 | 0.05591% | CZ 5C | 81.7137 | 21.5412 | 9.1572 | 30.2865 | 0 | 3.1545 | 0 | 28.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 190.9447 | 0.05591%
CZ 6A | 0.8297 | 0.21896 | 0.094476 | 0.60802 | 0 | 0.19155 | 0 | 0.39317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.5049 | 1.584% | CZ 6A | 26.6317 | 7.0282 | 3.0325 | 62.0433 | 0 | 6.1484 | 0 | 12.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 122.9277 | 1.584% | CZ 6A | 7.8053 | 2.0598 | 0.88877 | 0 | 0 | 1.802 | 0 | 3.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.8442 | 1.584% | CZ 6A | 0 | 0 | 0 | 0.62043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62043 | 1.584% | CZ 6A | 81.7137 | 21.5645 | 9.3045 | 67.8133 | 0 | 18.8651 | 0 | 38.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 254.6242 | 1.584%
CZ 6B | 0.8297 | 0.2188 | 0.094109 | 0.40808 | 0 | 0.13356 | 0 | 0.41232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.2655 | 0.2227% | CZ 6B | 26.6317 | 7.0231 | 3.0207 | 41.6408 | 0 | 4.2869 | 0 | 13.2347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 101.2615 | 0.2227% | CZ 6B | 7.8053 | 2.0584 | 0.88531 | 0 | 0 | 1.2564 | 0 | 3.8789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.4739 | 0.2227% | CZ 6B | 0 | 0 | 0 | 0.41641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41641 | 0.2227% | CZ 6B | 81.7137 | 21.549 | 9.2683 | 45.5134 | 0 | 13.1533 | 0 | 40.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 228.4471 | 0.2227%
CZ 7 | 0.8297 | 0.21867 | 0.096025 | 0.71405 | 0 | 0.13848 | 0 | 0.42392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.5898 | 0.2165% | CZ 7 | 26.6317 | 7.0189 | 3.0822 | 72.8619 | 0 | 4.4449 | 0 | 13.6068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 133.07 | 0.2165% | CZ 7 | 7.8053 | 2.0571 | 0.90334 | 0 | 0 | 1.3027 | 0 | 3.9879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.646 | 0.2165% | CZ 7 | 0 | 0 | 0 | 0.72862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72862 | 0.2165% | CZ 7 | 81.7137 | 21.5361 | 9.4571 | 79.638 | 0 | 13.6381 | 0 | 41.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 264.374 | 0.2165%
CZ 8 | 0.8297 | 0.21746 | 0.098152 | 0.96076 | 0 | 0.061081 | 0 | 0.46909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.8052 | 0.02488% | CZ 8 | 26.6317 | 6.9802 | 3.1505 | 98.0367 | 0 | 1.9606 | 0 | 15.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 157.2399 | 0.02488% | CZ 8 | 7.8053 | 2.0458 | 0.92335 | 0 | 0 | 0.57461 | 0 | 4.4129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 17.3515 | 0.02488% | CZ 8 | 0 | 0 | 0 | 0.98037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98037 | 0.02488% | CZ 8 | 81.7137 | 21.4171 | 9.6665 | 107.1541 | 0 | 6.0156 | 0 | 46.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 288.8067 | 0.02488%
US Weighted | 0.8297 | 0.21919 | 0.089296 | 0.18115 | 0 | 0.45174 | 0 | 0.37824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16897 | 2.3183 | 100% | US Weighted | 26.6317 | 7.0354 | 2.8662 | 18.4843 | 0 | 14.4999 | 0 | 12.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4237 | 87.0818 | 100% | US Weighted | 7.8053 | 2.062 | 0.84004 | 0 | 0 | 4.2497 | 0 | 3.5582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5896 | 20.1048 | 100% | US Weighted | 0 | 0 | 0 | 0.18484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18484 | 100% | US Weighted | 81.7137 | 21.5866 | 8.7944 | 20.2033 | 0 | 44.4899 | 0 | 37.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6414 | 230.6802 | 100%
Building Type: | Strip Mall |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Strip Mall |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 22500 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 22500 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 22500 | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.30126 | 0.14142 | 0.0073512 | 0 | 0 | 0.6541 | 0 | 0.26888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.3738 | 0% | CZ 0A | 9.6697 | 4.5392 | 0.23596 | 0 | 0 | 20.9952 | 0 | 8.6306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 44.0947 | 0% | CZ 0A | 2.834 | 1.3304 | 0.069155 | 0 | 0 | 6.1534 | 0 | 2.5295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 12.9234 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 29.6693 | 13.9277 | 0.72399 | 0 | 0 | 64.4194 | 0 | 26.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 135.2953 | 0%
CZ 0B | 0.30126 | 0.14151 | 0.0067474 | 0 | 0 | 0.4898 | 0 | 0.28296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.223 | 0% | CZ 0B | 9.6697 | 4.5422 | 0.21658 | 0 | 0 | 15.7216 | 0 | 9.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 39.2563 | 0% | CZ 0B | 2.834 | 1.3312 | 0.063475 | 0 | 0 | 4.6077 | 0 | 2.6619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 11.5054 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 29.6693 | 13.9368 | 0.66452 | 0 | 0 | 48.2383 | 0 | 27.8671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 120.4497 | 0%
CZ 1A | 0.30126 | 0.14152 | 0.0072593 | 0 | 0 | 0.4547 | 0 | 0.2563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.1618 | 4.208% | CZ 1A | 9.6697 | 4.5426 | 0.23301 | 0 | 0 | 14.5949 | 0 | 8.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 37.2907 | 4.208% | CZ 1A | 2.834 | 1.3314 | 0.068291 | 0 | 0 | 4.2775 | 0 | 2.4111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 10.9293 | 4.208% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.208% | CZ 1A | 29.6693 | 13.9381 | 0.71494 | 0 | 0 | 44.7813 | 0 | 25.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 114.4186 | 4.208%
CZ 1B | 0.30126 | 0.14138 | 0.006813 | -0.0016637 | 0 | 0.41059 | 0 | 0.27852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.1376 | 0% | CZ 1B | 9.6697 | 4.538 | 0.21868 | -0.16976 | 0 | 13.1791 | 0 | 8.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 36.3996 | 0% | CZ 1B | 2.834 | 1.33 | 0.064092 | 0 | 0 | 3.8626 | 0 | 2.6201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 10.7179 | 0% | CZ 1B | 0 | 0 | 0 | -0.0016976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0016976 | 0% | CZ 1B | 29.6693 | 13.9238 | 0.67098 | -0.18555 | 0 | 40.4373 | 0 | 27.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 112.0197 | 0%
CZ 2A | 0.30126 | 0.14134 | 0.0072725 | 0.002254 | 0 | 0.42191 | 0 | 0.2736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.1484 | 17.06% | CZ 2A | 9.6697 | 4.5367 | 0.23343 | 0.23 | 0 | 13.5423 | 0 | 8.7819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 37.018 | 17.06% | CZ 2A | 2.834 | 1.3296 | 0.068414 | 0 | 0 | 3.969 | 0 | 2.5738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 10.782 | 17.06% | CZ 2A | 0 | 0 | 0 | 0.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023 | 17.06% | CZ 2A | 29.6693 | 13.92 | 0.71623 | 0.25139 | 0 | 41.5518 | 0 | 26.9453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 113.1276 | 17.06%
CZ 2B | 0.30126 | 0.14142 | 0.0069443 | 0.0013087 | 0 | 0.32085 | 0 | 0.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.0814 | 3.729% | CZ 2B | 9.6697 | 4.5392 | 0.2229 | 0.13354 | 0 | 10.2987 | 0 | 9.9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 34.803 | 3.729% | CZ 2B | 2.834 | 1.3304 | 0.065327 | 0 | 0 | 3.0184 | 0 | 2.9059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 10.161 | 3.729% | CZ 2B | 0 | 0 | 0 | 0.0013354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013354 | 3.729% | CZ 2B | 29.6693 | 13.9277 | 0.68391 | 0.14596 | 0 | 31.5995 | 0 | 30.4217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 106.5218 | 3.729%
CZ 3A | 0.30126 | 0.14141 | 0.0073644 | 0.037163 | 0 | 0.25534 | 0 | 0.26986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.0131 | 18.76% | CZ 3A | 9.6697 | 4.5388 | 0.23638 | 3.7921 | 0 | 8.1958 | 0 | 8.6618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 35.1185 | 18.76% | CZ 3A | 2.834 | 1.3303 | 0.069279 | 0 | 0 | 2.402 | 0 | 2.5386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 9.1812 | 18.76% | CZ 3A | 0 | 0 | 0 | 0.037921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037921 | 18.76% | CZ 3A | 29.6693 | 13.9264 | 0.72528 | 4.1448 | 0 | 25.147 | 0 | 26.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 100.2633 | 18.76%
CZ 3B | 0.30126 | 0.14141 | 0.0070756 | 0.0032613 | 0 | 0.20788 | 0 | 0.2716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.93323 | 11.42% | CZ 3B | 9.6697 | 4.5388 | 0.22711 | 0.33279 | 0 | 6.6726 | 0 | 8.7178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 30.1828 | 11.42% | CZ 3B | 2.834 | 1.3303 | 0.066562 | 0 | 0 | 1.9556 | 0 | 2.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 8.7485 | 11.42% | CZ 3B | 0 | 0 | 0 | 0.0033279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033279 | 11.42% | CZ 3B | 29.6693 | 13.9264 | 0.69684 | 0.36374 | 0 | 20.4734 | 0 | 26.7488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 91.9521 | 11.42%
CZ 3C | 0.30126 | 0.1411 | 0.0071412 | -0.00016513 | 0 | 0.084303 | 0 | 0.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.70109 | 2.391% | CZ 3C | 9.6697 | 4.5291 | 0.22922 | -0.01685 | 0 | 2.7059 | 0 | 5.3508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 22.4919 | 2.391% | CZ 3C | 2.834 | 1.3274 | 0.06718 | 0 | 0 | 0.79306 | 0 | 1.5682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 6.5969 | 2.391% | CZ 3C | 0 | 0 | 0 | -0.0001685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0001685 | 2.391% | CZ 3C | 29.6693 | 13.8967 | 0.7033 | -0.018417 | 0 | 8.3026 | 0 | 16.4177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 69.0449 | 2.391%
CZ 4A | 0.30126 | 0.14067 | 0.0076006 | 0.12448 | 0 | 0.15163 | 0 | 0.21337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.93975 | 17.79% | CZ 4A | 9.6697 | 4.5152 | 0.24396 | 12.7016 | 0 | 4.8671 | 0 | 6.8487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 38.8702 | 17.79% | CZ 4A | 2.834 | 1.3233 | 0.071502 | 0 | 0 | 1.4265 | 0 | 2.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 7.6696 | 17.79% | CZ 4A | 0 | 0 | 0 | 0.12702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12702 | 17.79% | CZ 4A | 29.6693 | 13.854 | 0.74855 | 13.8828 | 0 | 14.9336 | 0 | 21.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 94.1757 | 17.79%
CZ 4B | 0.30126 | 0.14124 | 0.007535 | 0.044383 | 0 | 0.13373 | 0 | 0.18839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.81727 | 0.4638% | CZ 4B | 9.6697 | 4.5333 | 0.24186 | 4.5289 | 0 | 4.2923 | 0 | 6.0469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 29.337 | 0.4638% | CZ 4B | 2.834 | 1.3286 | 0.070884 | 0 | 0 | 1.258 | 0 | 1.7722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 7.2708 | 0.4638% | CZ 4B | 0 | 0 | 0 | 0.045289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045289 | 0.4638% | CZ 4B | 29.6693 | 13.9096 | 0.74209 | 4.9501 | 0 | 13.1701 | 0 | 18.5535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 81.0684 | 0.4638%
CZ 4C | 0.30126 | 0.14037 | 0.0076138 | 0.10053 | 0 | 0.035181 | 0 | 0.12873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.71442 | 2.358% | CZ 4C | 9.6697 | 4.5055 | 0.24439 | 10.2579 | 0 | 1.1292 | 0 | 4.1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 29.9625 | 2.358% | CZ 4C | 2.834 | 1.3205 | 0.071625 | 0 | 0 | 0.33096 | 0 | 1.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 5.7751 | 2.358% | CZ 4C | 0 | 0 | 0 | 0.10258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10258 | 2.358% | CZ 4C | 29.6693 | 13.8243 | 0.74984 | 11.2119 | 0 | 3.4648 | 0 | 12.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 71.6714 | 2.358%
CZ 5A | 0.30126 | 0.14101 | 0.0076531 | 0.16777 | 0 | 0.086692 | 0 | 0.16408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.86921 | 16.36% | CZ 5A | 9.6697 | 4.5262 | 0.24565 | 17.1193 | 0 | 2.7826 | 0 | 5.2665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 39.6339 | 16.36% | CZ 5A | 2.834 | 1.3265 | 0.071996 | 0 | 0 | 0.81554 | 0 | 1.5435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 6.5987 | 16.36% | CZ 5A | 0 | 0 | 0 | 0.17119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17119 | 16.36% | CZ 5A | 29.6693 | 13.8876 | 0.75372 | 18.7114 | 0 | 8.5379 | 0 | 16.1592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 87.7928 | 16.36%
CZ 5B | 0.30126 | 0.14084 | 0.0075744 | 0.090781 | 0 | 0.11124 | 0 | 0.16947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.82191 | 3.359% | CZ 5B | 9.6697 | 4.5207 | 0.24312 | 9.2633 | 0 | 3.5706 | 0 | 5.4397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 32.7311 | 3.359% | CZ 5B | 2.834 | 1.3249 | 0.071255 | 0 | 0 | 1.0465 | 0 | 1.5943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 6.878 | 3.359% | CZ 5B | 0 | 0 | 0 | 0.092633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092633 | 3.359% | CZ 5B | 29.6693 | 13.8708 | 0.74597 | 10.1248 | 0 | 10.9555 | 0 | 16.6905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 82.1306 | 3.359%
CZ 5C | 0.30126 | 0.14042 | 0.00764 | 0.11593 | 0 | 0.010502 | 0 | 0.099018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.67552 | 0.05591% | CZ 5C | 9.6697 | 4.5072 | 0.24523 | 11.83 | 0 | 0.33708 | 0 | 3.1783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 29.7915 | 0.05591% | CZ 5C | 2.834 | 1.321 | 0.071872 | 0 | 0 | 0.098793 | 0 | 0.9315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 5.2642 | 0.05591% | CZ 5C | 0 | 0 | 0 | 0.1183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1183 | 0.05591% | CZ 5C | 29.6693 | 13.8295 | 0.75243 | 12.9302 | 0 | 1.0343 | 0 | 9.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 68.0412 | 0.05591%
CZ 6A | 0.30126 | 0.14079 | 0.0076925 | 0.22125 | 0 | 0.10108 | 0 | 0.2687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.0415 | 1.584% | CZ 6A | 9.6697 | 4.519 | 0.24691 | 22.5762 | 0 | 3.2444 | 0 | 8.6247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 48.9049 | 1.584% | CZ 6A | 2.834 | 1.3245 | 0.072366 | 0 | 0 | 0.95089 | 0 | 2.5278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 7.7165 | 1.584% | CZ 6A | 0 | 0 | 0 | 0.22576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22576 | 1.584% | CZ 6A | 29.6693 | 13.8657 | 0.7576 | 24.6757 | 0 | 9.9548 | 0 | 26.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 105.4599 | 1.584%
CZ 6B | 0.30126 | 0.14076 | 0.0077188 | 0.1558 | 0 | 0.073158 | 0 | 0.17909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.85853 | 0.2227% | CZ 6B | 9.6697 | 4.5182 | 0.24776 | 15.8976 | 0 | 2.3482 | 0 | 5.7485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 38.454 | 0.2227% | CZ 6B | 2.834 | 1.3242 | 0.072613 | 0 | 0 | 0.68822 | 0 | 1.6848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 6.6109 | 0.2227% | CZ 6B | 0 | 0 | 0 | 0.15898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15898 | 0.2227% | CZ 6B | 29.6693 | 13.8631 | 0.76019 | 17.3761 | 0 | 7.205 | 0 | 17.6382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 86.5855 | 0.2227%
CZ 7 | 0.30126 | 0.14034 | 0.0077319 | 0.25959 | 0 | 0.083213 | 0 | 0.25376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.0466 | 0.2165% | CZ 7 | 9.6697 | 4.5047 | 0.24818 | 26.4883 | 0 | 2.671 | 0 | 8.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 51.751 | 0.2165% | CZ 7 | 2.834 | 1.3203 | 0.072737 | 0 | 0 | 0.78281 | 0 | 2.3872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 7.4041 | 0.2165% | CZ 7 | 0 | 0 | 0 | 0.26488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26488 | 0.2165% | CZ 7 | 29.6693 | 13.8217 | 0.76148 | 28.9517 | 0 | 8.1953 | 0 | 24.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 106.465 | 0.2165%
CZ 8 | 0.30126 | 0.13692 | 0.0078107 | 0.42816 | 0 | 0.044081 | 0 | 0.22291 | -0.012812 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 1.1291 | 0.02488% | CZ 8 | 9.6697 | 4.3947 | 0.25071 | 43.6893 | 0 | 1.4149 | 0 | 7.155 | -0.41124 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 66.1871 | 0.02488% | CZ 8 | 2.834 | 1.288 | 0.073478 | 0 | 0 | 0.41469 | 0 | 2.097 | -0.12053 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 6.5937 | 0.02488% | CZ 8 | 0 | 0 | 0 | 0.43689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43689 | 0.02488% | CZ 8 | 29.6693 | 13.4843 | 0.76924 | 47.7524 | 0 | 4.3413 | 0 | 21.9537 | -1.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 116.7821 | 0.02488%
US Weighted | 0.30126 | 0.14114 | 0.0074003 | 0.067574 | 0 | 0.22502 | 0 | 0.23432 | -3.1875e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00074825 | 0.97745 | 100% | US Weighted | 9.6697 | 4.5302 | 0.23753 | 6.8953 | 0 | 7.2227 | 0 | 7.5211 | -0.00010231 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024017 | 36.1005 | 100% | US Weighted | 2.834 | 1.3277 | 0.069617 | 0 | 0 | 2.1169 | 0 | 2.2043 | -2.9986e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007039 | 8.5596 | 100% | US Weighted | 0 | 0 | 0 | 0.068953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068953 | 100% | US Weighted | 29.6693 | 13.9001 | 0.72882 | 7.5366 | 0 | 22.1614 | 0 | 23.0769 | -0.00031393 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073692 | 97.1465 | 100%
Building Type: | Strip Mall |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Strip Mall |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Strip Mall |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Strip Mall |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 22500 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 22500 | [17 empty] | Prototype Floor Area: | 22500 | Building Type: | Strip Mall | [15 empty] | Prototype Floor Area: | 22500 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 36.31% | 64.43% | 8.871% |  |  | 42.17% |  | 64.09% | [7 empty] | 0.4428% | 41.99% | 0% | CZ 0A | 36.31% | 64.43% | 8.871% |  |  | 42.17% |  | 64.09% | [7 empty] | 0.4428% | 41.99% | 0% | CZ 0A | 36.31% | 64.43% | 8.871% |  |  | 42.17% |  | 64.09% | [7 empty] | 0.4428% | 41.99% | 0% | CZ 0A | [16 empty] | 0% | 0% | CZ 0A | 36.31% | 64.43% | 8.871% |  |  | 42.17% |  | 64.09% | [7 empty] | 0.4428% | 41.99% | 0%
CZ 0B | 36.31% | 64.46% | 8.207% |  |  | 38.66% |  | 60.64% | [7 empty] | 0.4428% | 40.31% | 0% | CZ 0B | 36.31% | 64.46% | 8.207% |  |  | 38.66% |  | 60.64% | [7 empty] | 0.4428% | 40.31% | 0% | CZ 0B | 36.31% | 64.46% | 8.207% |  |  | 38.66% |  | 60.64% | [7 empty] | 0.4428% | 40.31% | 0% | CZ 0B | [16 empty] | 0% | 0% | CZ 0B | 36.31% | 64.46% | 8.207% |  |  | 38.66% |  | 60.64% | [7 empty] | 0.4428% | 40.31% | 0%
CZ 1A | 36.31% | 64.46% | 8.626% |  |  | 44.58% |  | 68.59% | [7 empty] | 0.4428% | 43.09% | 4.208% | CZ 1A | 36.31% | 64.46% | 8.626% |  |  | 44.58% |  | 68.59% | [7 empty] | 0.4428% | 43.09% | 4.208% | CZ 1A | 36.31% | 64.46% | 8.626% |  |  | 44.58% |  | 68.59% | [7 empty] | 0.4428% | 43.09% | 4.208% | CZ 1A | [16 empty] | 0% | 4.208% | CZ 1A | 36.31% | 64.46% | 8.626% |  |  | 44.58% |  | 68.59% | [7 empty] | 0.4428% | 43.09% | 4.208%
CZ 1B | 36.31% | 64.47% | 8.128% | -103.9% |  | 40.1% |  | 61.93% | [7 empty] | 0.4428% | 40.97% | 0% | CZ 1B | 36.31% | 64.47% | 8.128% | -103.9% |  | 40.1% |  | 61.93% | [7 empty] | 0.4428% | 40.79% | 0% | CZ 1B | 36.31% | 64.47% | 8.128% |  |  | 40.1% |  | 61.93% | [7 empty] | 0.4428% | 41.05% | 0% | CZ 1B |  |  |  | -103.9% | [12 empty] | -103.9% | 0% | CZ 1B | 36.31% | 64.47% | 8.128% | -103.9% |  | 40.1% |  | 61.93% | [7 empty] | 0.4428% | 40.96% | 0%
CZ 2A | 36.31% | 64.48% | 8.475% | 21.02% |  | 48.39% |  | 68.96% | [7 empty] | 0.4428% | 44.46% | 17.06% | CZ 2A | 36.31% | 64.48% | 8.475% | 21.02% |  | 48.39% |  | 68.96% | [7 empty] | 0.4428% | 44.25% | 17.06% | CZ 2A | 36.31% | 64.48% | 8.475% |  |  | 48.39% |  | 68.96% | [7 empty] | 0.4428% | 44.55% | 17.06% | CZ 2A |  |  |  | 21.02% | [12 empty] | 21.02% | 17.06% | CZ 2A | 36.31% | 64.48% | 8.475% | 21.02% |  | 48.39% |  | 68.96% | [7 empty] | 0.4428% | 44.44% | 17.06%
CZ 2B | 36.31% | 64.47% | 8.113% | 35.54% |  | 47.73% |  | 67.27% | [7 empty] | 0.4428% | 44.34% | 3.729% | CZ 2B | 36.31% | 64.47% | 8.113% | 35.54% |  | 47.73% |  | 67.27% | [7 empty] | 0.4428% | 44.31% | 3.729% | CZ 2B | 36.31% | 64.47% | 8.113% |  |  | 47.73% |  | 67.27% | [7 empty] | 0.4428% | 44.36% | 3.729% | CZ 2B |  |  |  | 35.54% | [12 empty] | 35.54% | 3.729% | CZ 2B | 36.31% | 64.47% | 8.113% | 35.54% |  | 47.73% |  | 67.27% | [7 empty] | 0.4428% | 44.34% | 3.729%
CZ 3A | 36.31% | 64.47% | 8.296% | 32.01% |  | 52.87% |  | 70.37% | [7 empty] | 0.4428% | 44.26% | 18.76% | CZ 3A | 36.31% | 64.47% | 8.296% | 32.01% |  | 52.87% |  | 70.37% | [7 empty] | 0.4428% | 43.04% | 18.76% | CZ 3A | 36.31% | 64.47% | 8.296% |  |  | 52.87% |  | 70.37% | [7 empty] | 0.4428% | 44.91% | 18.76% | CZ 3A |  |  |  | 32.01% | [12 empty] | 32.01% | 18.76% | CZ 3A | 36.31% | 64.47% | 8.296% | 32.01% |  | 52.87% |  | 70.37% | [7 empty] | 0.4428% | 44.17% | 18.76%
CZ 3B | 36.31% | 64.47% | 8.066% | 12.64% |  | 49.25% |  | 61.96% | [7 empty] | 0.4428% | 42.57% | 11.42% | CZ 3B | 36.31% | 64.47% | 8.066% | 12.64% |  | 49.25% |  | 61.96% | [7 empty] | 0.4428% | 41.83% | 11.42% | CZ 3B | 36.31% | 64.47% | 8.066% |  |  | 49.25% |  | 61.96% | [7 empty] | 0.4428% | 42.93% | 11.42% | CZ 3B |  |  |  | 12.64% | [12 empty] | 12.64% | 11.42% | CZ 3B | 36.31% | 64.47% | 8.066% | 12.64% |  | 49.25% |  | 61.96% | [7 empty] | 0.4428% | 42.53% | 11.42%
CZ 3C | 36.31% | 64.35% | 8.052% | -4.391% |  | 50.09% |  | 45.9% | [7 empty] | 0.4428% | 38.06% | 2.391% | CZ 3C | 36.31% | 64.35% | 8.052% | -4.391% |  | 50.09% |  | 45.9% | [7 empty] | 0.4428% | 37.88% | 2.391% | CZ 3C | 36.31% | 64.35% | 8.052% |  |  | 50.09% |  | 45.9% | [7 empty] | 0.4428% | 38.15% | 2.391% | CZ 3C |  |  |  | -4.391% | [12 empty] | -4.391% | 2.391% | CZ 3C | 36.31% | 64.35% | 8.052% | -4.391% |  | 50.09% |  | 45.9% | [7 empty] | 0.4428% | 38.05% | 2.391%
CZ 4A | 36.31% | 64.23% | 8.333% | 39.94% |  | 51.71% |  | 61.32% | [7 empty] | 0.4428% | 41.55% | 17.79% | CZ 4A | 36.31% | 64.23% | 8.333% | 39.94% |  | 51.71% |  | 61.32% | [7 empty] | 0.4428% | 41.18% | 17.79% | CZ 4A | 36.31% | 64.23% | 8.333% |  |  | 51.71% |  | 61.32% | [7 empty] | 0.4428% | 41.81% | 17.79% | CZ 4A |  |  |  | 39.94% | [12 empty] | 39.94% | 17.79% | CZ 4A | 36.31% | 64.23% | 8.333% | 39.94% |  | 51.71% |  | 61.32% | [7 empty] | 0.4428% | 41.52% | 17.79%
CZ 4B | 36.31% | 64.44% | 8.337% | 47.77% |  | 49.39% |  | 43.58% | [7 empty] | 0.4428% | 38.84% | 0.4638% | CZ 4B | 36.31% | 64.44% | 8.337% | 47.77% |  | 49.39% |  | 43.58% | [7 empty] | 0.4428% | 39.62% | 0.4638% | CZ 4B | 36.31% | 64.44% | 8.337% |  |  | 49.39% |  | 43.58% | [7 empty] | 0.4428% | 38.43% | 0.4638% | CZ 4B |  |  |  | 47.77% | [12 empty] | 47.77% | 0.4638% | CZ 4B | 36.31% | 64.44% | 8.337% | 47.77% |  | 49.39% |  | 43.58% | [7 empty] | 0.4428% | 38.89% | 0.4638%
CZ 4C | 36.31% | 64.17% | 8.286% | 44.23% |  | 47.17% |  | 39.38% | [7 empty] | 0.4428% | 36.86% | 2.358% | CZ 4C | 36.31% | 64.17% | 8.286% | 44.23% |  | 47.17% |  | 39.38% | [7 empty] | 0.4428% | 38.36% | 2.358% | CZ 4C | 36.31% | 64.17% | 8.286% |  |  | 47.17% |  | 39.38% | [7 empty] | 0.4428% | 35.88% | 2.358% | CZ 4C |  |  |  | 44.23% | [12 empty] | 44.23% | 2.358% | CZ 4C | 36.31% | 64.17% | 8.286% | 44.23% |  | 47.17% |  | 39.38% | [7 empty] | 0.4428% | 36.97% | 2.358%
CZ 5A | 36.31% | 64.37% | 8.221% | 37.62% |  | 54.01% |  | 50.19% | [7 empty] | 0.4428% | 38.73% | 16.36% | CZ 5A | 36.31% | 64.37% | 8.221% | 37.62% |  | 54.01% |  | 50.19% | [7 empty] | 0.4428% | 38.39% | 16.36% | CZ 5A | 36.31% | 64.37% | 8.221% |  |  | 54.01% |  | 50.19% | [7 empty] | 0.4428% | 39.01% | 16.36% | CZ 5A |  |  |  | 37.62% | [12 empty] | 37.62% | 16.36% | CZ 5A | 36.31% | 64.37% | 8.221% | 37.62% |  | 54.01% |  | 50.19% | [7 empty] | 0.4428% | 38.7% | 16.36%
CZ 5B | 36.31% | 64.29% | 8.2% | 39.66% |  | 52.67% |  | 41.91% | [7 empty] | 0.4428% | 38.15% | 3.359% | CZ 5B | 36.31% | 64.29% | 8.2% | 39.66% |  | 52.67% |  | 41.91% | [7 empty] | 0.4428% | 38.43% | 3.359% | CZ 5B | 36.31% | 64.29% | 8.2% |  |  | 52.67% |  | 41.91% | [7 empty] | 0.4428% | 37.97% | 3.359% | CZ 5B |  |  |  | 39.66% | [12 empty] | 39.66% | 3.359% | CZ 5B | 36.31% | 64.29% | 8.2% | 39.66% |  | 52.67% |  | 41.91% | [7 empty] | 0.4428% | 38.17% | 3.359%
CZ 5C | 36.31% | 64.2% | 8.217% | 42.69% |  | 32.79% |  | 34.28% | [7 empty] | 0.4428% | 35.5% | 0.05591% | CZ 5C | 36.31% | 64.2% | 8.217% | 42.69% |  | 32.79% |  | 34.28% | [7 empty] | 0.4428% | 37.21% | 0.05591% | CZ 5C | 36.31% | 64.2% | 8.217% |  |  | 32.79% |  | 34.28% | [7 empty] | 0.4428% | 34.3% | 0.05591% | CZ 5C |  |  |  | 42.69% | [12 empty] | 42.69% | 0.05591% | CZ 5C | 36.31% | 64.2% | 8.217% | 42.69% |  | 32.79% |  | 34.28% | [7 empty] | 0.4428% | 35.63% | 0.05591%
CZ 6A | 36.31% | 64.3% | 8.142% | 36.39% |  | 52.77% |  | 68.34% | [7 empty] | 0.4428% | 41.58% | 1.584% | CZ 6A | 36.31% | 64.3% | 8.142% | 36.39% |  | 52.77% |  | 68.34% | [7 empty] | 0.4428% | 39.78% | 1.584% | CZ 6A | 36.31% | 64.3% | 8.142% |  |  | 52.77% |  | 68.34% | [7 empty] | 0.4428% | 43.24% | 1.584% | CZ 6A |  |  |  | 36.39% | [12 empty] | 36.39% | 1.584% | CZ 6A | 36.31% | 64.3% | 8.142% | 36.39% |  | 52.77% |  | 68.34% | [7 empty] | 0.4428% | 41.42% | 1.584%
CZ 6B | 36.31% | 64.33% | 8.202% | 38.18% |  | 54.78% |  | 43.44% | [7 empty] | 0.4428% | 37.9% | 0.2227% | CZ 6B | 36.31% | 64.33% | 8.202% | 38.18% |  | 54.78% |  | 43.44% | [7 empty] | 0.4428% | 37.97% | 0.2227% | CZ 6B | 36.31% | 64.33% | 8.202% |  |  | 54.78% |  | 43.44% | [7 empty] | 0.4428% | 37.83% | 0.2227% | CZ 6B |  |  |  | 38.18% | [12 empty] | 38.18% | 0.2227% | CZ 6B | 36.31% | 64.33% | 8.202% | 38.18% |  | 54.78% |  | 43.44% | [7 empty] | 0.4428% | 37.9% | 0.2227%
CZ 7 | 36.31% | 64.18% | 8.052% | 36.35% |  | 60.09% |  | 59.86% | [7 empty] | 0.4428% | 40.41% | 0.2165% | CZ 7 | 36.31% | 64.18% | 8.052% | 36.35% |  | 60.09% |  | 59.86% | [7 empty] | 0.4428% | 38.89% | 0.2165% | CZ 7 | 36.31% | 64.18% | 8.052% |  |  | 60.09% |  | 59.86% | [7 empty] | 0.4428% | 41.96% | 0.2165% | CZ 7 |  |  |  | 36.35% | [12 empty] | 36.35% | 0.2165% | CZ 7 | 36.31% | 64.18% | 8.052% | 36.35% |  | 60.09% |  | 59.86% | [7 empty] | 0.4428% | 40.27% | 0.2165%
CZ 8 | 36.31% | 62.96% | 7.958% | 44.56% |  | 72.17% |  | 47.52% | [7 empty] | 0.4428% | 40.25% | 0.02488% | CZ 8 | 36.31% | 62.96% | 7.958% | 44.56% |  | 72.17% |  | 47.52% | [7 empty] | 0.4428% | 42.09% | 0.02488% | CZ 8 | 36.31% | 62.96% | 7.958% |  |  | 72.17% |  | 47.52% | [7 empty] | 0.4428% | 38% | 0.02488% | CZ 8 |  |  |  | 44.56% | [12 empty] | 44.56% | 0.02488% | CZ 8 | 36.31% | 62.96% | 7.958% | 44.56% |  | 72.17% |  | 47.52% | [7 empty] | 0.4428% | 40.44% | 0.02488%
US Weighted | 36.31% | 64.39% | 8.289% | 28.89% | 0% | 50.92% | 0% | 61.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 42.04% | 100% | US Weighted | 36.31% | 64.39% | 8.289% | 28.89% | 0% | 50.92% | 0% | 61.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 41.58% | 100% | US Weighted | 36.31% | 64.39% | 8.289% | 0% | 0% | 50.92% | 0% | 61.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 42.31% | 100% | US Weighted | 0% | 0% | 0% | 28.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 28.89% | 100% | US Weighted | 36.31% | 64.39% | 8.289% | 28.89% | 0% | 50.92% | 0% | 61.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4428% | 42.01% | 100%

## SchPri
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Primary School |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 73959 |  | Building Type: | Primary School |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 |  | Building Type: | Primary School |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Primary School |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Primary School | [14 empty] | Prototype Floor Area: | 73959 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.11461 | 0.010236 | 0.024644 | 0.037767 | 0 | 0.20435 | 0 | 0.1231 | 0.026866 | 0.00079789 | 0.028908 | 0 | 0.0068195 | 0.10513 | 0 | 0.37841 | 1.0616 |  | STD2019 | 3.6786 | 0.32856 | 1.793 | 3.8538 | 0 | 6.5593 | 0 | 3.9513 | 0.86235 | 0.025611 | 0.92788 | 0 | 0.21889 | 6.5458 | 0 | 12.1461 | 40.8912 |  | STD2019 | 1.0781 | 0.096296 | 0.097071 | 0 | 0 | 1.9224 | 0 | 1.1581 | 0.25274 | 0.007506 | 0.27195 | 0 | 0.064153 | 0.56245 | 0 | 3.5598 | 9.0706 |  | STD2019 | 0 | 0 | 0.014618 | 0.038538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.099423 |  | STD2019 | 11.2871 | 1.0081 | 2.614 | 4.2122 | 0 | 20.1258 | 0 | 12.1238 | 2.6459 | 0.078581 | 2.847 | 0 | 0.67162 | 10.9453 | 0 | 37.2677 | 105.8271
STD2016 | 0.14164 | 0.010236 | 0.024676 | 0.043249 | 0 | 0.22228 | 0 | 0.14016 | 0.026486 | 0.00081245 | 0.044061 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.1441 |  | STD2016 | 4.5463 | 0.32856 | 1.7962 | 4.4132 | 0 | 7.1347 | 0 | 4.499 | 0.85014 | 0.026078 | 1.4143 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 43.9226 |  | STD2016 | 1.3324 | 0.096296 | 0.097071 | 0 | 0 | 2.0911 | 0 | 1.3186 | 0.24916 | 0.007643 | 0.4145 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 9.7942 |  | STD2016 | 0 | 0 | 0.01465 | 0.044132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10505 |  | STD2016 | 13.9494 | 1.0081 | 2.6175 | 4.8236 | 0 | 21.8915 | 0 | 13.8041 | 2.6085 | 0.080014 | 4.3394 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 114.017
STD2013 | 0.27555 | 0.01772 | 0.024715 | 0.035459 | 0 | 0.24093 | 0 | 0.14919 | 0.024277 | 0.00064175 | 0.044047 | 0 | 0.0096614 | 0.10513 | 0 | 0.37841 | 1.3057 |  | STD2013 | 8.8446 | 0.56877 | 1.8002 | 3.6183 | 0 | 7.7333 | 0 | 4.7886 | 0.77925 | 0.020599 | 1.4138 | 0 | 0.31011 | 6.5458 | 0 | 12.1461 | 48.5694 |  | STD2013 | 2.5922 | 0.1667 | 0.097071 | 0 | 0 | 2.2665 | 0 | 1.4035 | 0.22838 | 0.0060372 | 0.41437 | 0 | 0.090888 | 0.56245 | 0 | 3.5598 | 11.3879 |  | STD2013 | 0 | 0 | 0.01469 | 0.036183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.09714 |  | STD2013 | 27.1379 | 1.7451 | 2.6218 | 3.9548 | 0 | 23.7279 | 0 | 14.6928 | 2.3909 | 0.063203 | 4.338 | 0 | 0.9515 | 10.9453 | 0 | 37.2677 | 129.837
STD2010 | 0.3124 | 0.01772 | 0.02471 | 0.053437 | 0 | 0.29549 | 0 | 0.19713 | 0.032522 | 0.00092123 | 0.054609 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.5381 |  | STD2010 | 10.0273 | 0.56877 | 1.7997 | 5.4528 | 0 | 9.4846 | 0 | 6.3273 | 1.0439 | 0.029569 | 1.7528 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 57.2856 |  | STD2010 | 2.9388 | 0.1667 | 0.097071 | 0 | 0 | 2.7798 | 0 | 1.8544 | 0.30595 | 0.0086663 | 0.51372 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 13.4049 |  | STD2010 | 0 | 0 | 0.014685 | 0.054528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11548 |  | STD2010 | 30.7666 | 1.7451 | 2.6213 | 5.9599 | 0 | 29.1014 | 0 | 19.414 | 3.203 | 0.090728 | 5.3782 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 152.958
STD2007 | 0.48336 | 0.033243 | 0.02567 | 0.098193 | 0 | 0.41951 | 0 | 0.21848 | 0.044844 | 0.0013744 | 0.054371 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9413 |  | STD2007 | 15.5148 | 1.067 | 1.8379 | 10.0197 | 0 | 13.4655 | 0 | 7.0128 | 1.4394 | 0.044114 | 1.7452 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 73.3654 |  | STD2007 | 4.5471 | 0.31273 | 0.10511 | 0 | 0 | 3.9465 | 0 | 2.0553 | 0.42187 | 0.012929 | 0.51149 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 16.776 |  | STD2007 | 0 | 0 | 0.014792 | 0.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16126 |  | STD2007 | 47.6039 | 3.274 | 2.7172 | 10.9515 | 0 | 41.316 | 0 | 21.5172 | 4.4165 | 0.13536 | 5.3548 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 193.2535
STD2004 | 0.48336 | 0.033243 | 0.025689 | 0.12787 | 0 | 0.44626 | 0 | 0.24699 | 0.058845 | 0.0017805 | 0.054373 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.0407 |  | STD2004 | 15.5148 | 1.067 | 1.8396 | 13.0476 | 0 | 14.3241 | 0 | 7.9278 | 1.8888 | 0.05715 | 1.7453 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 78.6312 |  | STD2004 | 4.5471 | 0.31273 | 0.10514 | 0 | 0 | 4.1981 | 0 | 2.3235 | 0.55357 | 0.01675 | 0.51151 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 17.4314 |  | STD2004 | 0 | 0 | 0.014809 | 0.13048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19155 |  | STD2004 | 47.6039 | 3.274 | 2.7193 | 14.2611 | 0 | 43.9504 | 0 | 24.3247 | 5.7953 | 0.17535 | 5.355 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 203.4261
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 1.8881e-05 | 0.029674 | 0 | 0.02675 | 0 | 0.028507 | 0.014 | 0.00040611 | 2.3664e-06 | 0 | 0 | 0 | 0 | 0 | 0.099358 |  | 2004-2007 | 0 | 0 | 0.0017334 | 3.0279 | 0 | 0.8586 | 0 | 0.91503 | 0.44938 | 0.013035 | 7.5956e-05 | 0 | 0 | 0 | 0 | 0 | 5.2658 |  | 2004-2007 | 0 | 0 | 2.5984e-05 | 0 | 0 | 0.25164 | 0 | 0.26818 | 0.13171 | 0.0038204 | 2.2262e-05 | 0 | 0 | 0 | 0 | 0 | 0.6554 |  | 2004-2007 | 0 | 0 | 1.6448e-05 | 0.030279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030296 |  | 2004-2007 | 0 | 0 | 0.0020698 | 3.3095 | 0 | 2.6344 | 0 | 2.8076 | 1.3788 | 0.039996 | 0.00023306 | 0 | 0 | 0 | 0 | 0 | 10.1727
2007-2010 | 0.17096 | 0.015523 | 0.00096011 | 0.044756 | 0 | 0.12402 | 0 | 0.021355 | 0.012322 | 0.00045315 | -0.00023759 | 0 | 0.0083506 | 0 | 0 | 0.0047404 | 0.40321 |  | 2007-2010 | 5.4875 | 0.49827 | 0.038193 | 4.5669 | 0 | 3.9809 | 0 | 0.68544 | 0.39552 | 0.014545 | -0.0076262 | 0 | 0.26804 | 0 | 0 | 0.15216 | 16.0799 |  | 2007-2010 | 1.6083 | 0.14603 | 0.0080402 | 0 | 0 | 1.1667 | 0 | 0.20089 | 0.11592 | 0.0042629 | -0.0022351 | 0 | 0.078557 | 0 | 0 | 0.044594 | 3.3711 |  | 2007-2010 | 0 | 0 | 0.00010759 | 0.045669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045777 |  | 2007-2010 | 16.8373 | 1.5288 | 0.095933 | 4.9916 | 0 | 12.2145 | 0 | 2.1031 | 1.2136 | 0.044628 | -0.023399 | 0 | 0.82241 | 0 | 0 | 0.46686 | 40.2954
2010-2013 | 0.036845 | 0 | -5.0507e-06 | 0.017978 | 0 | 0.054562 | 0 | 0.047939 | 0.008245 | 0.00027948 | 0.010562 | 0 | 0.0011692 | 0 | 0 | 0.054812 | 0.23239 |  | 2010-2013 | 1.1826 | 0 | -0.00051545 | 1.8345 | 0 | 1.7513 | 0 | 1.5387 | 0.26465 | 0.0089706 | 0.339 | 0 | 0.037529 | 0 | 0 | 1.7593 | 8.7162 |  | 2010-2013 | 0.34661 | 0 | 1.0249e-08 | 0 | 0 | 0.51328 | 0 | 0.45097 | 0.077563 | 0.0026291 | 0.099356 | 0 | 0.010999 | 0 | 0 | 0.51563 | 2.017 |  | 2010-2013 | 0 | 0 | -5.1549e-06 | 0.018345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01834 |  | 2010-2013 | 3.6287 | 0 | -0.00056332 | 2.0051 | 0 | 5.3735 | 0 | 4.7213 | 0.81201 | 0.027524 | 1.0402 | 0 | 0.11515 | 0 | 0 | 5.3982 | 23.1211
2013-2016 | 0.13391 | 0.0074835 | 3.9242e-05 | -0.00779 | 0 | 0.018647 | 0 | 0.0090235 | -0.0022087 | -0.00017069 | -1.3968e-05 | 0 | 0.0027365 | 0 | 0 | 0 | 0.16166 |  | 2013-2016 | 4.2983 | 0.2402 | 0.0040043 | -0.7949 | 0 | 0.59853 | 0 | 0.28963 | -0.070893 | -0.0054789 | -0.00044836 | 0 | 0.087835 | 0 | 0 | 0 | 4.6468 |  | 2013-2016 | 1.2598 | 0.0704 | 0 | 0 | 0 | 0.17542 | 0 | 0.084887 | -0.020778 | -0.0016058 | -0.00013141 | 0 | 0.025743 | 0 | 0 | 0 | 1.5937 |  | 2013-2016 | 0 | 0 | 4.0043e-05 | -0.007949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.007909 |  | 2013-2016 | 13.1885 | 0.73702 | 0.0043767 | -0.86883 | 0 | 1.8364 | 0 | 0.88868 | -0.21752 | -0.016811 | -0.0013757 | 0 | 0.2695 | 0 | 0 | 0 | 15.82
2016-2019 | 0.027033 | 0 | 3.1328e-05 | 0.0054819 | 0 | 0.017928 | 0 | 0.017061 | -0.00038031 | 1.4554e-05 | 0.015153 | 0 | 0.00010542 | 0 | 0 | 0 | 0.082427 |  | 2016-2019 | 0.86769 | 0 | 0.0031996 | 0.55937 | 0 | 0.57544 | 0 | 0.54761 | -0.012207 | 0.00046716 | 0.48639 | 0 | 0.0033836 | 0 | 0 | 0 | 3.0314 |  | 2016-2019 | 0.25431 | 0 | -3.7804e-07 | 0 | 0 | 0.16865 | 0 | 0.1605 | -0.0035777 | 0.00013692 | 0.14255 | 0 | 0.00099168 | 0 | 0 | 0 | 0.72356 |  | 2016-2019 | 0 | 0 | 3.2008e-05 | 0.0055937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056257 |  | 2016-2019 | 2.6623 | 0 | 0.0034946 | 0.61139 | 0 | 1.7656 | 0 | 1.6802 | -0.037455 | 0.0014334 | 1.4924 | 0 | 0.010382 | 0 | 0 | 0 | 8.1898
2004-2019 | 0.36875 | 0.023007 | 0.0010445 | 0.0901 | 0 | 0.24191 | 0 | 0.12389 | 0.031979 | 0.0009826 | 0.025466 | 0 | 0.012362 | 0 | 0 | 0.059552 | 0.97904 |  | 2004-2019 | 11.8362 | 0.73847 | 0.046614 | 9.1938 | 0 | 7.7648 | 0 | 3.9764 | 1.0264 | 0.031539 | 0.81739 | 0 | 0.39678 | 0 | 0 | 1.9115 | 37.74 |  | 2004-2019 | 3.469 | 0.21643 | 0.0080658 | 0 | 0 | 2.2757 | 0 | 1.1654 | 0.30083 | 0.0092436 | 0.23956 | 0 | 0.11629 | 0 | 0 | 0.56023 | 8.3608 |  | 2004-2019 | 0 | 0 | 0.00019094 | 0.091938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092129 |  | 2004-2019 | 36.3168 | 2.2658 | 0.10531 | 10.0489 | 0 | 23.8246 | 0 | 12.2009 | 3.1494 | 0.096772 | 2.508 | 0 | 1.2175 | 0 | 0 | 5.865 | 97.599
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.0735% | 23.21% |  | 5.994% |  | 11.54% | 23.79% | 22.81% | 0.004352% |  | 0% | 0% |  | 0% | 4.869% |  | 2004-2007 | 0% | 0% | 0.09423% | 23.21% |  | 5.994% |  | 11.54% | 23.79% | 22.81% | 0.004352% |  | 0% | 0% |  | 0% | 6.697% |  | 2004-2007 | 0% | 0% | 0.02471% |  |  | 5.994% |  | 11.54% | 23.79% | 22.81% | 0.004352% |  | 0% | 0% |  | 0% | 3.76% |  | 2004-2007 |  |  | 0.1111% | 23.21% | [9 empty] | 0% |  |  | 15.82% |  | 2004-2007 | 0% | 0% | 0.07611% | 23.21% |  | 5.994% |  | 11.54% | 23.79% | 22.81% | 0.004352% |  | 0% | 0% |  | 0% | 5.001%
2007-2010 | 35.37% | 46.7% | 3.74% | 45.58% |  | 29.56% |  | 9.774% | 27.48% | 32.97% | -0.437% |  | 43.54% | 0% |  | 1.082% | 20.77% |  | 2007-2010 | 35.37% | 46.7% | 2.078% | 45.58% |  | 29.56% |  | 9.774% | 27.48% | 32.97% | -0.437% |  | 43.54% | 0% |  | 1.082% | 21.92% |  | 2007-2010 | 35.37% | 46.7% | 7.649% |  |  | 29.56% |  | 9.774% | 27.48% | 32.97% | -0.437% |  | 43.54% | 0% |  | 1.082% | 20.09% |  | 2007-2010 |  |  | 0.7274% | 45.58% | [9 empty] | 0% |  |  | 28.39% |  | 2007-2010 | 35.37% | 46.7% | 3.531% | 45.58% |  | 29.56% |  | 9.774% | 27.48% | 32.97% | -0.437% |  | 43.54% | 0% |  | 1.082% | 20.85%
2010-2013 | 11.79% | 0% | -0.02044% | 33.64% |  | 18.46% |  | 24.32% | 25.35% | 30.34% | 19.34% |  | 10.8% | 0% |  | 12.65% | 15.11% |  | 2010-2013 | 11.79% | 0% | -0.02864% | 33.64% |  | 18.46% |  | 24.32% | 25.35% | 30.34% | 19.34% |  | 10.8% | 0% |  | 12.65% | 15.22% |  | 2010-2013 | 11.79% | 0% | 1.056e-05% |  |  | 18.46% |  | 24.32% | 25.35% | 30.34% | 19.34% |  | 10.8% | 0% |  | 12.65% | 15.05% |  | 2010-2013 |  |  | -0.0351% | 33.64% | [9 empty] | 0% |  |  | 15.88% |  | 2010-2013 | 11.79% | 0% | -0.02149% | 33.64% |  | 18.46% |  | 24.32% | 25.35% | 30.34% | 19.34% |  | 10.8% | 0% |  | 12.65% | 15.12%
2013-2016 | 48.6% | 42.23% | 0.1588% | -21.97% |  | 7.74% |  | 6.048% | -9.098% | -26.6% | -0.03171% |  | 28.32% | 0% |  | 0% | 12.38% |  | 2013-2016 | 48.6% | 42.23% | 0.2224% | -21.97% |  | 7.74% |  | 6.048% | -9.098% | -26.6% | -0.03171% |  | 28.32% | 0% |  | 0% | 9.567% |  | 2013-2016 | 48.6% | 42.23% | 0% |  |  | 7.74% |  | 6.048% | -9.098% | -26.6% | -0.03171% |  | 28.32% | 0% |  | 0% | 13.99% |  | 2013-2016 |  |  | 0.2726% | -21.97% | [9 empty] | 0% |  |  | -8.142% |  | 2013-2016 | 48.6% | 42.23% | 0.1669% | -21.97% |  | 7.74% |  | 6.048% | -9.098% | -26.6% | -0.03171% |  | 28.32% | 0% |  | 0% | 12.18%
2016-2019 | 19.09% | 0% | 0.127% | 12.68% |  | 8.065% |  | 12.17% | -1.436% | 1.791% | 34.39% |  | 1.522% | 0% |  | 0% | 7.205% |  | 2016-2019 | 19.09% | 0% | 0.1781% | 12.68% |  | 8.065% |  | 12.17% | -1.436% | 1.791% | 34.39% |  | 1.522% | 0% |  | 0% | 6.902% |  | 2016-2019 | 19.09% | 0% | -0.0003894% |  |  | 8.065% |  | 12.17% | -1.436% | 1.791% | 34.39% |  | 1.522% | 0% |  | 0% | 7.388% |  | 2016-2019 |  |  | 0.2185% | 12.68% | [9 empty] | 0% |  |  | 5.355% |  | 2016-2019 | 19.09% | 0% | 0.1335% | 12.68% |  | 8.065% |  | 12.17% | -1.436% | 1.791% | 34.39% |  | 1.522% | 0% |  | 0% | 7.183%
2004-2019 | 76.29% | 69.21% | 4.066% | 70.46% |  | 54.21% |  | 50.16% | 54.34% | 55.19% | 46.83% |  | 64.45% | 0% |  | 13.6% | 47.98% |  | 2004-2019 | 76.29% | 69.21% | 2.534% | 70.46% |  | 54.21% |  | 50.16% | 54.34% | 55.19% | 46.83% |  | 64.45% | 0% |  | 13.6% | 48% |  | 2004-2019 | 76.29% | 69.21% | 7.672% |  |  | 54.21% |  | 50.16% | 54.34% | 55.19% | 46.83% |  | 64.45% | 0% |  | 13.6% | 47.96% |  | 2004-2019 |  |  | 1.289% | 70.46% | [9 empty] | 0% |  |  | 48.1% |  | 2004-2019 | 76.29% | 69.21% | 3.873% | 70.46% |  | 54.21% |  | 50.16% | 54.34% | 55.19% | 46.83% |  | 64.45% | 0% |  | 13.6% | 47.98%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.11297 | 0.01016 | 0.020657 | 0.00072215 | 0 | 0.69654 | 0 | 0.16494 | 0.04333 | 6.7891e-05 | 0.029185 | 0 | 0.0068171 | 0.10513 | 0 | 0.37841 | 1.5689 | 0% | CZ 0A | 3.6262 | 0.3261 | 1.3863 | 0.073689 | 0 | 22.3575 | 0 | 5.2943 | 1.3908 | 0.0021792 | 0.93678 | 0 | 0.21881 | 6.5458 | 0 | 12.1461 | 54.3046 | 0% | CZ 0A | 1.0628 | 0.095576 | 0.097041 | 0 | 0 | 6.5526 | 0 | 1.5517 | 0.40762 | 0.00063867 | 0.27455 | 0 | 0.06413 | 0.56245 | 0 | 3.5598 | 14.2289 | 0% | CZ 0A | 0 | 0 | 0.010552 | 0.00073689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057557 | 0% | CZ 0A | 11.1263 | 1.0006 | 2.1693 | 0.080542 | 0 | 68.5992 | 0 | 16.2445 | 4.2674 | 0.0066863 | 2.8743 | 0 | 0.67138 | 10.9453 | 0 | 37.2677 | 155.2532 | 0%
CZ 0B | 0.11238 | 0.010216 | 0.020909 | 0.00027128 | 0 | 0.61825 | 0 | 0.18196 | 0.039812 | 6.3897e-05 | 0.029097 | 0 | 0.0068171 | 0.10513 | 0 | 0.37841 | 1.5033 | 0% | CZ 0B | 3.607 | 0.3279 | 1.4121 | 0.027681 | 0 | 19.8445 | 0 | 5.8405 | 1.2779 | 0.002051 | 0.93396 | 0 | 0.21881 | 6.5458 | 0 | 12.1461 | 52.1843 | 0% | CZ 0B | 1.0572 | 0.096102 | 0.097041 | 0 | 0 | 5.8161 | 0 | 1.7118 | 0.37453 | 0.0006011 | 0.27373 | 0 | 0.06413 | 0.56245 | 0 | 3.5598 | 13.6134 | 0% | CZ 0B | 0 | 0 | 0.01081 | 0.00027681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057354 | 0% | CZ 0B | 11.0674 | 1.0061 | 2.1974 | 0.030256 | 0 | 60.8887 | 0 | 17.9204 | 3.9209 | 0.006293 | 2.8657 | 0 | 0.67138 | 10.9453 | 0 | 37.2677 | 148.7874 | 0%
CZ 1A | 0.11524 | 0.01024 | 0.021469 | 1.8839e-05 | 0 | 0.44302 | 0 | 0.14901 | 0.042592 | 5.9904e-05 | 0.029049 | 0 | 0.0068171 | 0.10513 | 0 | 0.37841 | 1.3011 | 2.71% | CZ 1A | 3.699 | 0.32867 | 1.4692 | 0.0019223 | 0 | 14.2201 | 0 | 4.7829 | 1.3671 | 0.0019228 | 0.93242 | 0 | 0.21881 | 6.5458 | 0 | 12.1461 | 45.714 | 2.71% | CZ 1A | 1.0841 | 0.096327 | 0.097041 | 0 | 0 | 4.1677 | 0 | 1.4018 | 0.40067 | 0.00056354 | 0.27328 | 0 | 0.06413 | 0.56245 | 0 | 3.5598 | 11.7079 | 2.71% | CZ 1A | 0 | 0 | 0.011381 | 1.9223e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057668 | 2.71% | CZ 1A | 11.3497 | 1.0084 | 2.2599 | 0.0021011 | 0 | 43.6315 | 0 | 14.6752 | 4.1947 | 0.0058997 | 2.8609 | 0 | 0.67138 | 10.9453 | 0 | 37.2677 | 128.8727 | 2.71%
CZ 1B | 0.11404 | 0.010208 | 0.02185 | 0.0059329 | 0 | 0.51683 | 0 | 0.16235 | 0.036853 | 0.00013578 | 0.029025 | 0 | 0.0068171 | 0.10513 | 0 | 0.37841 | 1.3876 | 0% | CZ 1B | 3.6606 | 0.32764 | 1.5081 | 0.6054 | 0 | 16.589 | 0 | 5.211 | 1.1829 | 0.0043583 | 0.93165 | 0 | 0.21881 | 6.5458 | 0 | 12.1461 | 48.9313 | 0% | CZ 1B | 1.0729 | 0.096026 | 0.097041 | 0 | 0 | 4.862 | 0 | 1.5273 | 0.34669 | 0.0012773 | 0.27305 | 0 | 0.06413 | 0.56245 | 0 | 3.5598 | 12.4625 | 0% | CZ 1B | 0 | 0 | 0.01177 | 0.006054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.064091 | 0% | CZ 1B | 11.2318 | 1.0053 | 2.3023 | 0.6617 | 0 | 50.8998 | 0 | 15.9888 | 3.6295 | 0.013373 | 2.8586 | 0 | 0.67138 | 10.9453 | 0 | 37.2677 | 137.4755 | 0%
CZ 2A | 0.11337 | 0.01022 | 0.022576 | 0.0040315 | 0 | 0.36873 | 0 | 0.14133 | 0.035763 | 0.00013978 | 0.029021 | 0 | 0.0068171 | 0.10513 | 0 | 0.37841 | 1.2155 | 20.22% | CZ 2A | 3.6391 | 0.32803 | 1.5821 | 0.41138 | 0 | 11.8355 | 0 | 4.5364 | 1.1479 | 0.0044865 | 0.93152 | 0 | 0.21881 | 6.5458 | 0 | 12.1461 | 43.3271 | 20.22% | CZ 2A | 1.0665 | 0.096139 | 0.097041 | 0 | 0 | 3.4688 | 0 | 1.3295 | 0.33643 | 0.0013149 | 0.27301 | 0 | 0.06413 | 0.56245 | 0 | 3.5598 | 10.8552 | 20.22% | CZ 2A | 0 | 0 | 0.01251 | 0.0041138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.062892 | 20.22% | CZ 2A | 11.1657 | 1.0065 | 2.3833 | 0.44963 | 0 | 36.3147 | 0 | 13.9188 | 3.5221 | 0.013766 | 2.8582 | 0 | 0.67138 | 10.9453 | 0 | 37.2677 | 120.5171 | 20.22%
CZ 2B | 0.11528 | 0.010224 | 0.022749 | 0.0036221 | 0 | 0.29226 | 0 | 0.13825 | 0.022903 | 0.00013179 | 0.02879 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 1.1246 | 2.485% | CZ 2B | 3.7002 | 0.32815 | 1.5996 | 0.3696 | 0 | 9.381 | 0 | 4.4375 | 0.73514 | 0.0042301 | 0.92409 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 40.3904 | 2.485% | CZ 2B | 1.0845 | 0.096177 | 0.097078 | 0 | 0 | 2.7494 | 0 | 1.3006 | 0.21546 | 0.0012398 | 0.27084 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 10.0017 | 2.485% | CZ 2B | 0 | 0 | 0.012683 | 0.003696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.062647 | 2.485% | CZ 2B | 11.3533 | 1.0069 | 2.4026 | 0.40397 | 0 | 28.7836 | 0 | 13.6156 | 2.2556 | 0.012979 | 2.8354 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 111.5547 | 2.485%
CZ 3A | 0.1146 | 0.010252 | 0.024275 | 0.028259 | 0 | 0.20894 | 0 | 0.11662 | 0.035507 | 0.00058306 | 0.028918 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 1.0583 | 19.44% | CZ 3A | 3.6784 | 0.32905 | 1.7553 | 2.8836 | 0 | 6.7065 | 0 | 3.7431 | 1.1397 | 0.018715 | 0.92819 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 40.0935 | 19.44% | CZ 3A | 1.0781 | 0.09644 | 0.097078 | 0 | 0 | 1.9656 | 0 | 1.0971 | 0.33403 | 0.0054851 | 0.27204 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 9.1322 | 19.44% | CZ 3A | 0 | 0 | 0.014241 | 0.028836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.089344 | 19.44% | CZ 3A | 11.2864 | 1.0096 | 2.5728 | 3.1518 | 0 | 20.5776 | 0 | 11.485 | 3.4969 | 0.057423 | 2.848 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 105.3703 | 19.44%
CZ 3B | 0.1161 | 0.010188 | 0.023854 | 0.01749 | 0 | 0.2145 | 0 | 0.12595 | 0 | 0.00034345 | 0.028778 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 1.0276 | 7.425% | CZ 3B | 3.7266 | 0.327 | 1.7124 | 1.7847 | 0 | 6.8851 | 0 | 4.0426 | 0 | 0.011024 | 0.9237 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 38.3239 | 7.425% | CZ 3B | 1.0922 | 0.095839 | 0.097078 | 0 | 0 | 2.0179 | 0 | 1.1848 | 0 | 0.0032309 | 0.27072 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 8.9482 | 7.425% | CZ 3B | 0 | 0 | 0.013811 | 0.017847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.077926 | 7.425% | CZ 3B | 11.4343 | 1.0033 | 2.5259 | 1.9507 | 0 | 21.1255 | 0 | 12.4038 | 0 | 0.033825 | 2.8342 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 102.1962 | 7.425%
CZ 3C | 0.11661 | 0.010196 | 0.024147 | 0.0059405 | 0 | 0.1427 | 0 | 0.10577 | 0 | 0.00015974 | 0.028894 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 0.92478 | 0.9093% | CZ 3C | 3.743 | 0.32726 | 1.7422 | 0.60617 | 0 | 4.5803 | 0 | 3.395 | 0 | 0.0051274 | 0.92742 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 34.2374 | 0.9093% | CZ 3C | 1.097 | 0.095914 | 0.097078 | 0 | 0 | 1.3424 | 0 | 0.99502 | 0 | 0.0015028 | 0.27181 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 8.0872 | 0.9093% | CZ 3C | 0 | 0 | 0.01411 | 0.0060617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.066439 | 0.9093% | CZ 3C | 11.4847 | 1.0041 | 2.5585 | 0.66254 | 0 | 14.0538 | 0 | 10.4168 | 0 | 0.015732 | 2.8456 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 91.9265 | 0.9093%
CZ 4A | 0.11535 | 0.010244 | 0.025501 | 0.038494 | 0 | 0.14563 | 0 | 0.11445 | 0.028794 | 0.0010104 | 0.028906 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 0.99874 | 18.26% | CZ 4A | 3.7025 | 0.3288 | 1.8804 | 3.9279 | 0 | 4.6745 | 0 | 3.6735 | 0.92422 | 0.032431 | 0.92781 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 38.983 | 18.26% | CZ 4A | 1.0851 | 0.096365 | 0.097078 | 0 | 0 | 1.37 | 0 | 1.0767 | 0.27087 | 0.009505 | 0.27192 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 8.464 | 18.26% | CZ 4A | 0 | 0 | 0.015491 | 0.039279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10104 | 18.26% | CZ 4A | 11.3604 | 1.0088 | 2.7095 | 4.2932 | 0 | 14.3428 | 0 | 11.2715 | 2.8358 | 0.099507 | 2.8468 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 99.6531 | 18.26%
CZ 4B | 0.11386 | 0.010196 | 0.025122 | 0.032651 | 0 | 0.14893 | 0 | 0.12451 | 0 | 0.00059904 | 0.028766 | 0 | 0.0068171 | 0.10513 | 0 | 0.37841 | 0.97499 | 0.672% | CZ 4B | 3.6546 | 0.32726 | 1.8417 | 3.3318 | 0 | 4.7804 | 0 | 3.9966 | 0 | 0.019228 | 0.92332 | 0 | 0.21881 | 6.5458 | 0 | 12.1461 | 37.7855 | 0.672% | CZ 4B | 1.0711 | 0.095914 | 0.097078 | 0 | 0 | 1.4011 | 0 | 1.1713 | 0 | 0.0056354 | 0.27061 | 0 | 0.06413 | 0.56245 | 0 | 3.5598 | 8.2991 | 0.672% | CZ 4B | 0 | 0 | 0.015104 | 0.033318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.094689 | 0.672% | CZ 4B | 11.2133 | 1.0041 | 2.6672 | 3.6416 | 0 | 14.6677 | 0 | 12.2626 | 0 | 0.058997 | 2.833 | 0 | 0.67138 | 10.9453 | 0 | 37.2677 | 97.2329 | 0.672%
CZ 4C | 0.11696 | 0.010291 | 0.025684 | 0.063999 | 0 | 0.059397 | 0 | 0.1146 | 0 | 0.0011462 | 0.028886 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 0.91132 | 2.388% | CZ 4C | 3.7543 | 0.33033 | 1.8991 | 6.5305 | 0 | 1.9065 | 0 | 3.6783 | 0 | 0.036789 | 0.92717 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 37.9738 | 2.388% | CZ 4C | 1.1003 | 0.096815 | 0.097078 | 0 | 0 | 0.55876 | 0 | 1.078 | 0 | 0.010782 | 0.27174 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 7.4 | 2.388% | CZ 4C | 0 | 0 | 0.015678 | 0.065305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12725 | 2.388% | CZ 4C | 11.5193 | 1.0136 | 2.73 | 7.1378 | 0 | 5.8497 | 0 | 11.286 | 0 | 0.11288 | 2.8448 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 91.3788 | 2.388%
CZ 5A | 0.11402 | 0.010244 | 0.026516 | 0.073304 | 0 | 0.091225 | 0 | 0.11323 | 0.027372 | 0.0015735 | 0.028882 | 0 | 0.0068171 | 0.10513 | 0 | 0.37841 | 0.97673 | 16% | CZ 5A | 3.66 | 0.3288 | 1.9839 | 7.48 | 0 | 2.9281 | 0 | 3.6344 | 0.87858 | 0.050505 | 0.92704 | 0 | 0.21881 | 6.5458 | 0 | 12.1461 | 40.7821 | 16% | CZ 5A | 1.0727 | 0.096365 | 0.097078 | 0 | 0 | 0.85819 | 0 | 1.0652 | 0.2575 | 0.014802 | 0.2717 | 0 | 0.06413 | 0.56245 | 0 | 3.5598 | 7.9199 | 16% | CZ 5A | 0 | 0 | 0.016527 | 0.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13759 | 16% | CZ 5A | 11.2298 | 1.0088 | 2.8227 | 8.1756 | 0 | 8.9844 | 0 | 11.1515 | 2.6957 | 0.15496 | 2.8444 | 0 | 0.67138 | 10.9453 | 0 | 37.2677 | 97.9523 | 16%
CZ 5B | 0.11453 | 0.010232 | 0.026184 | 0.075851 | 0 | 0.10341 | 0 | 0.1213 | 0 | 0.0012819 | 0.02879 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 0.97194 | 4.803% | CZ 5B | 3.6761 | 0.32841 | 1.9501 | 7.7399 | 0 | 3.3194 | 0 | 3.8935 | 0 | 0.041148 | 0.92409 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 40.7834 | 4.803% | CZ 5B | 1.0774 | 0.096252 | 0.097078 | 0 | 0 | 0.97285 | 0 | 1.1411 | 0 | 0.01206 | 0.27084 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 7.854 | 4.803% | CZ 5B | 0 | 0 | 0.016188 | 0.077399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13985 | 4.803% | CZ 5B | 11.2793 | 1.0077 | 2.7857 | 8.4597 | 0 | 10.1848 | 0 | 11.9464 | 0 | 0.12625 | 2.8354 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 97.51 | 4.803%
CZ 5C | 0.11581 | 0.010291 | 0.026226 | 0.041139 | 0 | 0.036541 | 0 | 0.11156 | 0.028167 | 0.0010303 | 0.028894 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 0.89002 | 0.03694% | CZ 5C | 3.7173 | 0.33033 | 1.9543 | 4.1978 | 0 | 1.1729 | 0 | 3.5809 | 0.90409 | 0.033072 | 0.92742 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 35.7289 | 0.03694% | CZ 5C | 1.0895 | 0.096815 | 0.097078 | 0 | 0 | 0.34376 | 0 | 1.0495 | 0.26497 | 0.0096928 | 0.27181 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 7.4095 | 0.03694% | CZ 5C | 0 | 0 | 0.016231 | 0.041978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10448 | 0.03694% | CZ 5C | 11.4056 | 1.0136 | 2.7903 | 4.5882 | 0 | 3.5988 | 0 | 10.9871 | 2.774 | 0.10147 | 2.8456 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 88.9895 | 0.03694%
CZ 6A | 0.11468 | 0.010256 | 0.027359 | 0.13115 | 0 | 0.097212 | 0 | 0.12063 | 0.030164 | 0.0023562 | 0.02883 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 1.053 | 3.249% | CZ 6A | 3.6811 | 0.32918 | 2.0696 | 13.383 | 0 | 3.1203 | 0 | 3.872 | 0.96818 | 0.075629 | 0.92537 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 47.3353 | 3.249% | CZ 6A | 1.0789 | 0.096477 | 0.097116 | 0 | 0 | 0.9145 | 0 | 1.1348 | 0.28376 | 0.022166 | 0.27121 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 8.0853 | 3.249% | CZ 6A | 0 | 0 | 0.017383 | 0.13383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19748 | 3.249% | CZ 6A | 11.2947 | 1.01 | 2.9167 | 14.6277 | 0 | 9.574 | 0 | 11.8803 | 2.9707 | 0.23205 | 2.8393 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 106.2301 | 3.249%
CZ 6B | 0.11394 | 0.010272 | 0.027105 | 0.088881 | 0 | 0.064365 | 0 | 0.11891 | 0.027228 | 0.0016733 | 0.028778 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 0.97151 | 0.979% | CZ 6B | 3.6573 | 0.32969 | 2.0438 | 9.0695 | 0 | 2.066 | 0 | 3.8169 | 0.87397 | 0.05371 | 0.9237 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 41.7452 | 0.979% | CZ 6B | 1.0719 | 0.096628 | 0.097116 | 0 | 0 | 0.6055 | 0 | 1.1187 | 0.25615 | 0.015741 | 0.27072 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 7.7188 | 0.979% | CZ 6B | 0 | 0 | 0.017124 | 0.090695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.15409 | 0.979% | CZ 6B | 11.2215 | 1.0116 | 2.8884 | 9.9129 | 0 | 6.339 | 0 | 11.7112 | 2.6816 | 0.1648 | 2.8342 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 97.6499 | 0.979%
CZ 7 | 0.11416 | 0.010295 | 0.028243 | 0.16221 | 0 | 0.076305 | 0 | 0.12427 | 0.026949 | 0.00041134 | 0.028806 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 1.062 | 0.3956% | CZ 7 | 3.6642 | 0.33046 | 2.1599 | 16.552 | 0 | 2.4492 | 0 | 3.9887 | 0.865 | 0.013203 | 0.9246 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 49.8582 | 0.3956% | CZ 7 | 1.0739 | 0.096853 | 0.097116 | 0 | 0 | 0.71783 | 0 | 1.169 | 0.25352 | 0.0038696 | 0.27099 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 7.8695 | 0.3956% | CZ 7 | 0 | 0 | 0.018285 | 0.16552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.23007 | 0.3956% | CZ 7 | 11.2428 | 1.014 | 3.0153 | 18.0914 | 0 | 7.515 | 0 | 12.2386 | 2.6541 | 0.040511 | 2.8369 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 107.5332 | 0.3956%
CZ 8 | 0.1228 | 0.010631 | 0.029364 | 0.28871 | 0 | 0.03599 | 0 | 0.14376 | 0.030152 | 0.00097843 | 0.02869 | 0 | 0.006821 | 0.10513 | 0 | 0.37841 | 1.1814 | 0.02728% | CZ 8 | 3.9416 | 0.34123 | 2.2737 | 29.4599 | 0 | 1.1552 | 0 | 4.6143 | 0.9678 | 0.031405 | 0.92088 | 0 | 0.21894 | 6.5458 | 0 | 12.1461 | 62.6168 | 0.02728% | CZ 8 | 1.1552 | 0.10001 | 0.097191 | 0 | 0 | 0.33857 | 0 | 1.3524 | 0.28365 | 0.0092044 | 0.2699 | 0 | 0.064168 | 0.56245 | 0 | 3.5598 | 7.7925 | 0.02728% | CZ 8 | 0 | 0 | 0.019421 | 0.2946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.36029 | 0.02728% | CZ 8 | 12.0939 | 1.047 | 3.1402 | 32.1996 | 0 | 3.5445 | 0 | 14.158 | 2.9695 | 0.096361 | 2.8255 | 0 | 0.67177 | 10.9453 | 0 | 37.2677 | 120.9593 | 0.02728%
US Weighted | 0.11461 | 0.010236 | 0.024644 | 0.037767 | 0 | 0.20435 | 0 | 0.1231 | 0.026866 | 0.00079789 | 0.028908 | 0 | 0.0068195 | 0.10513 | 0 | 0.37841 | 1.0616 | 100% | US Weighted | 3.6786 | 0.32856 | 1.793 | 3.8538 | 0 | 6.5593 | 0 | 3.9513 | 0.86235 | 0.025611 | 0.92788 | 0 | 0.21889 | 6.5458 | 0 | 12.1461 | 40.8912 | 100% | US Weighted | 1.0781 | 0.096296 | 0.097071 | 0 | 0 | 1.9224 | 0 | 1.1581 | 0.25274 | 0.007506 | 0.27195 | 0 | 0.064153 | 0.56245 | 0 | 3.5598 | 9.0706 | 100% | US Weighted | 0 | 0 | 0.014618 | 0.038538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.099423 | 100% | US Weighted | 11.2871 | 1.0081 | 2.614 | 4.2122 | 0 | 20.1258 | 0 | 12.1238 | 2.6459 | 0.078581 | 2.847 | 0 | 0.67162 | 10.9453 | 0 | 37.2677 | 105.8271 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.14002 | 0.01016 | 0.020663 | 0.0015636 | 0 | 0.74549 | 0 | 0.16558 | 0.056258 | 7.5878e-05 | 0.044584 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.6749 | 0% | CZ 0A | 4.4944 | 0.3261 | 1.387 | 0.15955 | 0 | 23.9288 | 0 | 5.3148 | 1.8057 | 0.0024355 | 1.4311 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 57.7641 | 0% | CZ 0A | 1.3172 | 0.095576 | 0.097041 | 0 | 0 | 7.0131 | 0 | 1.5577 | 0.52923 | 0.00071381 | 0.41942 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 15.2174 | 0% | CZ 0A | 0 | 0 | 0.010559 | 0.0015955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.058422 | 0% | CZ 0A | 13.7902 | 1.0006 | 2.17 | 0.17439 | 0 | 73.4204 | 0 | 16.3074 | 5.5406 | 0.0074729 | 4.3909 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 165.6969 | 0%
CZ 0B | 0.13987 | 0.010216 | 0.020923 | 0.0016452 | 0 | 0.68842 | 0 | 0.20247 | 0.046206 | 7.9872e-05 | 0.044409 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.6447 | 0% | CZ 0B | 4.4894 | 0.3279 | 1.4135 | 0.16788 | 0 | 22.0969 | 0 | 6.4989 | 1.4831 | 0.0025637 | 1.4254 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 56.8197 | 0% | CZ 0B | 1.3158 | 0.096102 | 0.097041 | 0 | 0 | 6.4762 | 0 | 1.9047 | 0.43467 | 0.00075138 | 0.41777 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 14.9305 | 0% | CZ 0B | 0 | 0 | 0.010824 | 0.0016788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.05877 | 0% | CZ 0B | 13.7749 | 1.0061 | 2.199 | 0.1835 | 0 | 67.7996 | 0 | 19.9404 | 4.5506 | 0.0078662 | 4.3736 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 162.7305 | 0%
CZ 1A | 0.14183 | 0.01024 | 0.021487 | 4.7725e-05 | 0 | 0.48773 | 0 | 0.16099 | 0.04367 | 5.9904e-05 | 0.044313 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.4008 | 2.71% | CZ 1A | 4.5524 | 0.32867 | 1.471 | 0.0048699 | 0 | 15.6552 | 0 | 5.1675 | 1.4017 | 0.0019228 | 1.4223 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 48.9198 | 2.71% | CZ 1A | 1.3342 | 0.096327 | 0.097041 | 0 | 0 | 4.5883 | 0 | 1.5145 | 0.41082 | 0.00056354 | 0.41687 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 12.646 | 2.71% | CZ 1A | 0 | 0 | 0.011399 | 4.8699e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057716 | 2.71% | CZ 1A | 13.968 | 1.0084 | 2.2619 | 0.0053228 | 0 | 48.0346 | 0 | 15.8555 | 4.3008 | 0.0058997 | 4.3642 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 138.6996 | 2.71%
CZ 1B | 0.14026 | 0.010208 | 0.021864 | 0.0090011 | 0 | 0.57572 | 0 | 0.17116 | 0.044644 | 0.00017572 | 0.044273 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.5078 | 0% | CZ 1B | 4.502 | 0.32764 | 1.5095 | 0.91848 | 0 | 18.4793 | 0 | 5.4938 | 1.433 | 0.0056402 | 1.4211 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 53.0046 | 0% | CZ 1B | 1.3195 | 0.096026 | 0.097041 | 0 | 0 | 5.416 | 0 | 1.6101 | 0.41998 | 0.001653 | 0.41649 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 13.5642 | 0% | CZ 1B | 0 | 0 | 0.011784 | 0.0091848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.067236 | 0% | CZ 1B | 13.8134 | 1.0053 | 2.3039 | 1.0039 | 0 | 56.7 | 0 | 16.8565 | 4.3968 | 0.017306 | 4.3602 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 149.3523 | 0%
CZ 2A | 0.14089 | 0.01022 | 0.022607 | 0.0054833 | 0 | 0.39918 | 0 | 0.15168 | 0.036038 | 0.00016374 | 0.044277 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.301 | 20.22% | CZ 2A | 4.5223 | 0.32803 | 1.5854 | 0.55952 | 0 | 12.8129 | 0 | 4.8686 | 1.1567 | 0.0052556 | 1.4212 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 46.1741 | 20.22% | CZ 2A | 1.3254 | 0.096139 | 0.097041 | 0 | 0 | 3.7552 | 0 | 1.4269 | 0.33902 | 0.0015403 | 0.41653 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 11.6452 | 20.22% | CZ 2A | 0 | 0 | 0.012542 | 0.0055952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.064405 | 20.22% | CZ 2A | 13.8756 | 1.0065 | 2.3868 | 0.61156 | 0 | 39.3137 | 0 | 14.9383 | 3.5492 | 0.016126 | 4.3606 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 128.9534 | 20.22%
CZ 2B | 0.14348 | 0.010224 | 0.022755 | 0.0067129 | 0 | 0.3318 | 0 | 0.16458 | 0.025172 | 0.00016773 | 0.043814 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.2392 | 2.485% | CZ 2B | 4.6053 | 0.32815 | 1.6002 | 0.68499 | 0 | 10.65 | 0 | 5.2827 | 0.80795 | 0.0053838 | 1.4063 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 44.2852 | 2.485% | CZ 2B | 1.3497 | 0.096177 | 0.097078 | 0 | 0 | 3.1213 | 0 | 1.5483 | 0.2368 | 0.0015779 | 0.41217 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 11.0505 | 2.485% | CZ 2B | 0 | 0 | 0.01269 | 0.0068499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.065807 | 2.485% | CZ 2B | 14.1304 | 1.0069 | 2.4033 | 0.74869 | 0 | 32.6774 | 0 | 16.2087 | 2.479 | 0.016519 | 4.315 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 122.8809 | 2.485%
CZ 3A | 0.14253 | 0.010252 | 0.024313 | 0.035713 | 0 | 0.2286 | 0 | 0.13153 | 0.032492 | 0.00061901 | 0.044077 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.1406 | 19.44% | CZ 3A | 4.5748 | 0.32905 | 1.7591 | 3.6442 | 0 | 7.3375 | 0 | 4.2218 | 1.0429 | 0.019869 | 1.4148 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 43.2582 | 19.44% | CZ 3A | 1.3408 | 0.09644 | 0.097078 | 0 | 0 | 2.1505 | 0 | 1.2373 | 0.30566 | 0.0058232 | 0.41465 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 9.8357 | 19.44% | CZ 3A | 0 | 0 | 0.014279 | 0.036442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.096989 | 19.44% | CZ 3A | 14.0368 | 1.0096 | 2.577 | 3.9831 | 0 | 22.5135 | 0 | 12.9537 | 3.2 | 0.060963 | 4.341 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 113.5706 | 19.44%
CZ 3B | 0.1441 | 0.010188 | 0.023863 | 0.019177 | 0 | 0.23797 | 0 | 0.15154 | 0 | 0.00036342 | 0.043798 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.1215 | 7.425% | CZ 3B | 4.6254 | 0.327 | 1.7132 | 1.9568 | 0 | 7.6384 | 0 | 4.8641 | 0 | 0.011665 | 1.4058 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 41.4567 | 7.425% | CZ 3B | 1.3556 | 0.095839 | 0.097078 | 0 | 0 | 2.2387 | 0 | 1.4256 | 0 | 0.0034188 | 0.41202 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 9.8157 | 7.425% | CZ 3B | 0 | 0 | 0.01382 | 0.019568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.079656 | 7.425% | CZ 3B | 14.1922 | 1.0033 | 2.5269 | 2.1388 | 0 | 23.4369 | 0 | 14.9245 | 0 | 0.035791 | 4.3134 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 111.4669 | 7.425%
CZ 3C | 0.14405 | 0.010196 | 0.024187 | 0.0089572 | 0 | 0.15241 | 0 | 0.12109 | 0 | 0.00021565 | 0.044061 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 0.99562 | 0.9093% | CZ 3C | 4.6237 | 0.32726 | 1.7463 | 0.914 | 0 | 4.8919 | 0 | 3.8866 | 0 | 0.006922 | 1.4143 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 36.7251 | 0.9093% | CZ 3C | 1.3551 | 0.095914 | 0.097078 | 0 | 0 | 1.4337 | 0 | 1.1391 | 0 | 0.0020287 | 0.4145 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 8.7249 | 0.9093% | CZ 3C | 0 | 0 | 0.014151 | 0.00914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.069558 | 0.9093% | CZ 3C | 14.1867 | 1.0041 | 2.563 | 0.999 | 0 | 15.0099 | 0 | 11.9252 | 0 | 0.021239 | 4.3394 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 98.9435 | 0.9093%
CZ 4A | 0.14167 | 0.010244 | 0.025535 | 0.043944 | 0 | 0.15511 | 0 | 0.13026 | 0.029636 | 0.00099041 | 0.044049 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.0719 | 18.26% | CZ 4A | 4.5474 | 0.3288 | 1.8838 | 4.4841 | 0 | 4.9787 | 0 | 4.1812 | 0.95126 | 0.03179 | 1.4139 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 41.7151 | 18.26% | CZ 4A | 1.3328 | 0.096365 | 0.097078 | 0 | 0 | 1.4592 | 0 | 1.2254 | 0.2788 | 0.0093171 | 0.41439 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 9.1007 | 18.26% | CZ 4A | 0 | 0 | 0.015526 | 0.044841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10663 | 18.26% | CZ 4A | 13.9527 | 1.0088 | 2.7133 | 4.9011 | 0 | 15.2762 | 0 | 12.829 | 2.9188 | 0.097541 | 4.3382 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 106.9306 | 18.26%
CZ 4B | 0.14032 | 0.010196 | 0.02513 | 0.033775 | 0 | 0.16516 | 0 | 0.15329 | 0 | 0.00059904 | 0.043754 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.0627 | 0.672% | CZ 4B | 4.5039 | 0.32726 | 1.8426 | 3.4465 | 0 | 5.3014 | 0 | 4.9201 | 0 | 0.019228 | 1.4044 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 40.6795 | 0.672% | CZ 4B | 1.32 | 0.095914 | 0.097078 | 0 | 0 | 1.5537 | 0 | 1.442 | 0 | 0.0056354 | 0.41161 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 9.1134 | 0.672% | CZ 4B | 0 | 0 | 0.015113 | 0.034465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.095845 | 0.672% | CZ 4B | 13.8193 | 1.0041 | 2.6682 | 3.767 | 0 | 16.2661 | 0 | 15.0964 | 0 | 0.058997 | 4.3091 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 105.8843 | 0.672%
CZ 4C | 0.14414 | 0.010291 | 0.025729 | 0.079321 | 0 | 0.061837 | 0 | 0.12462 | 0 | 0.0013858 | 0.044001 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 0.98179 | 2.388% | CZ 4C | 4.6266 | 0.33033 | 1.9037 | 8.094 | 0 | 1.9848 | 0 | 4 | 0 | 0.04448 | 1.4123 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 41.3105 | 2.388% | CZ 4C | 1.356 | 0.096815 | 0.097078 | 0 | 0 | 0.58172 | 0 | 1.1723 | 0 | 0.013036 | 0.41394 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 7.9183 | 2.388% | CZ 4C | 0 | 0 | 0.015725 | 0.08094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14293 | 2.388% | CZ 4C | 14.1957 | 1.0136 | 2.735 | 8.8467 | 0 | 6.09 | 0 | 12.2732 | 0 | 0.13648 | 4.3335 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 98.5192 | 2.388%
CZ 5A | 0.14031 | 0.010244 | 0.02656 | 0.082178 | 0 | 0.096689 | 0 | 0.1318 | 0.026438 | 0.0015575 | 0.044029 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.0503 | 16% | CZ 5A | 4.5037 | 0.3288 | 1.9884 | 8.3855 | 0 | 3.1035 | 0 | 4.2305 | 0.84859 | 0.049992 | 1.4132 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 43.7664 | 16% | CZ 5A | 1.3199 | 0.096365 | 0.097078 | 0 | 0 | 0.90958 | 0 | 1.2399 | 0.24871 | 0.014652 | 0.4142 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 8.5278 | 16% | CZ 5A | 0 | 0 | 0.016572 | 0.083855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14669 | 16% | CZ 5A | 13.8186 | 1.0088 | 2.8276 | 9.1654 | 0 | 9.5224 | 0 | 12.9804 | 2.6037 | 0.15339 | 4.3362 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 105.3115 | 16%
CZ 5B | 0.14066 | 0.010232 | 0.026194 | 0.079072 | 0 | 0.1191 | 0 | 0.15488 | 0 | 0.0012819 | 0.04381 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.0657 | 4.803% | CZ 5B | 4.5148 | 0.32841 | 1.9511 | 8.0686 | 0 | 3.8229 | 0 | 4.9712 | 0 | 0.041148 | 1.4062 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 44.0185 | 4.803% | CZ 5B | 1.3232 | 0.096252 | 0.097078 | 0 | 0 | 1.1204 | 0 | 1.457 | 0 | 0.01206 | 0.41213 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 8.7055 | 4.803% | CZ 5B | 0 | 0 | 0.016199 | 0.080686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14315 | 4.803% | CZ 5B | 13.8528 | 1.0077 | 2.7868 | 8.819 | 0 | 11.7297 | 0 | 15.253 | 0 | 0.12625 | 4.3146 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 106.7847 | 4.803%
CZ 5C | 0.14232 | 0.010291 | 0.026278 | 0.056392 | 0 | 0.038239 | 0 | 0.12186 | 0.018786 | 0.0011861 | 0.044013 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 0.94984 | 0.03694% | CZ 5C | 4.5683 | 0.33033 | 1.9597 | 5.7543 | 0 | 1.2274 | 0 | 3.9116 | 0.60298 | 0.038071 | 1.4127 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 38.7195 | 0.03694% | CZ 5C | 1.3389 | 0.096815 | 0.097078 | 0 | 0 | 0.35972 | 0 | 1.1464 | 0.17672 | 0.011158 | 0.41405 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 7.8283 | 0.03694% | CZ 5C | 0 | 0 | 0.016285 | 0.057543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12009 | 0.03694% | CZ 5C | 14.0168 | 1.0136 | 2.7962 | 6.2894 | 0 | 3.7659 | 0 | 12.0019 | 1.8501 | 0.11681 | 4.3347 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 95.0804 | 0.03694%
CZ 6A | 0.14026 | 0.010256 | 0.027388 | 0.14505 | 0 | 0.10542 | 0 | 0.14375 | 0.031362 | 0.0023602 | 0.043993 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.1403 | 3.249% | CZ 6A | 4.5021 | 0.32918 | 2.0726 | 14.8008 | 0 | 3.3837 | 0 | 4.6142 | 1.0066 | 0.075758 | 1.4121 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 51.1113 | 3.249% | CZ 6A | 1.3195 | 0.096477 | 0.097116 | 0 | 0 | 0.99171 | 0 | 1.3523 | 0.29503 | 0.022203 | 0.41386 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 8.7756 | 3.249% | CZ 6A | 0 | 0 | 0.017412 | 0.14801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.21169 | 3.249% | CZ 6A | 13.8138 | 1.01 | 2.9199 | 16.1773 | 0 | 10.3822 | 0 | 14.1576 | 3.0887 | 0.23245 | 4.3327 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 115.0096 | 3.249%
CZ 6B | 0.13949 | 0.010272 | 0.027112 | 0.091083 | 0 | 0.074257 | 0 | 0.1484 | 0.027723 | 0.0016454 | 0.043818 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.0543 | 0.979% | CZ 6B | 4.4774 | 0.32969 | 2.0448 | 9.2941 | 0 | 2.3835 | 0 | 4.7632 | 0.88986 | 0.052812 | 1.4065 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 44.556 | 0.979% | CZ 6B | 1.3122 | 0.096628 | 0.097078 | 0 | 0 | 0.69856 | 0 | 1.396 | 0.2608 | 0.015478 | 0.41221 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 8.4764 | 0.979% | CZ 6B | 0 | 0 | 0.017136 | 0.092941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.15634 | 0.979% | CZ 6B | 13.7379 | 1.0116 | 2.8892 | 10.1585 | 0 | 7.3132 | 0 | 14.615 | 2.7304 | 0.16204 | 4.3154 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 105.8282 | 0.979%
CZ 7 | 0.13898 | 0.010295 | 0.028274 | 0.18186 | 0 | 0.084912 | 0 | 0.1482 | 0.031777 | 0.0004952 | 0.043957 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.1592 | 0.3956% | CZ 7 | 4.461 | 0.33046 | 2.1631 | 18.5568 | 0 | 2.7255 | 0 | 4.7568 | 1.02 | 0.015895 | 1.4109 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 54.3546 | 0.3956% | CZ 7 | 1.3074 | 0.096853 | 0.097116 | 0 | 0 | 0.79879 | 0 | 1.3941 | 0.29894 | 0.0046586 | 0.41352 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 8.5989 | 0.3956% | CZ 7 | 0 | 0 | 0.018317 | 0.18557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.25015 | 0.3956% | CZ 7 | 13.6876 | 1.014 | 3.0188 | 20.2825 | 0 | 8.3626 | 0 | 14.5953 | 3.1296 | 0.04877 | 4.3292 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 117.3632 | 0.3956%
CZ 8 | 0.14883 | 0.010631 | 0.02938 | 0.32293 | 0 | 0.039916 | 0 | 0.17053 | 0.032887 | 0.00125 | 0.043802 | 0 | 0.0069289 | 0.10513 | 0 | 0.37841 | 1.2906 | 0.02728% | CZ 8 | 4.7772 | 0.34123 | 2.2756 | 32.9516 | 0 | 1.2812 | 0 | 5.4735 | 1.0556 | 0.040122 | 1.4059 | 0 | 0.2224 | 6.5458 | 0 | 12.1461 | 68.5163 | 0.02728% | CZ 8 | 1.4001 | 0.10001 | 0.097153 | 0 | 0 | 0.3755 | 0 | 1.6042 | 0.30938 | 0.011759 | 0.41206 | 0 | 0.065182 | 0.56245 | 0 | 3.5598 | 8.4976 | 0.02728% | CZ 8 | 0 | 0 | 0.019441 | 0.32952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.39522 | 0.02728% | CZ 8 | 14.6579 | 1.047 | 3.142 | 36.0161 | 0 | 3.9311 | 0 | 16.7943 | 3.2389 | 0.12311 | 4.3138 | 0 | 0.68239 | 10.9453 | 0 | 37.2677 | 132.1596 | 0.02728%
US Weighted | 0.14164 | 0.010236 | 0.024676 | 0.043249 | 0 | 0.22228 | 0 | 0.14016 | 0.026486 | 0.00081245 | 0.044061 | 0 | 0.0069249 | 0.10513 | 0 | 0.37841 | 1.1441 | 100% | US Weighted | 4.5463 | 0.32856 | 1.7962 | 4.4132 | 0 | 7.1347 | 0 | 4.499 | 0.85014 | 0.026078 | 1.4143 | 0 | 0.22227 | 6.5458 | 0 | 12.1461 | 43.9226 | 100% | US Weighted | 1.3324 | 0.096296 | 0.097071 | 0 | 0 | 2.0911 | 0 | 1.3186 | 0.24916 | 0.007643 | 0.4145 | 0 | 0.065145 | 0.56245 | 0 | 3.5598 | 9.7942 | 100% | US Weighted | 0 | 0 | 0.01465 | 0.044132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10505 | 100% | US Weighted | 13.9494 | 1.0081 | 2.6175 | 4.8236 | 0 | 21.8915 | 0 | 13.8041 | 2.6085 | 0.080014 | 4.3394 | 0 | 0.682 | 10.9453 | 0 | 37.2677 | 114.017 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.267 | 0.017736 | 0.020724 | 0.00059405 | 0 | 0.88062 | 0 | 0.1819 | 0.060459 | 6.3897e-05 | 0.044588 | 0 | 0.0096565 | 0.10513 | 0 | 0.37841 | 1.9669 | 0% | CZ 0A | 8.5701 | 0.56927 | 1.3932 | 0.060617 | 0 | 28.2661 | 0 | 5.8386 | 1.9406 | 0.002051 | 1.4312 | 0 | 0.30995 | 6.5458 | 0 | 12.1461 | 67.0736 | 0% | CZ 0A | 2.5118 | 0.16684 | 0.097041 | 0 | 0 | 8.2843 | 0 | 1.7112 | 0.56876 | 0.0006011 | 0.41946 | 0 | 0.090842 | 0.56245 | 0 | 3.5598 | 17.9731 | 0% | CZ 0A | 0 | 0 | 0.010621 | 0.00060617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057495 | 0% | CZ 0A | 26.2955 | 1.7467 | 2.1768 | 0.066254 | 0 | 86.7284 | 0 | 17.9145 | 5.9543 | 0.006293 | 4.3913 | 0 | 0.95102 | 10.9453 | 0 | 37.2677 | 194.4441 | 0%
CZ 0B | 0.2708 | 0.017732 | 0.020984 | 0.00093691 | 0 | 0.77921 | 0 | 0.21684 | 0.051377 | 7.1885e-05 | 0.044409 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.8956 | 0% | CZ 0B | 8.6921 | 0.56914 | 1.4198 | 0.095603 | 0 | 25.0109 | 0 | 6.96 | 1.6491 | 0.0023073 | 1.4254 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 64.8263 | 0% | CZ 0B | 2.5475 | 0.16681 | 0.097041 | 0 | 0 | 7.3303 | 0 | 2.0398 | 0.48333 | 0.00067624 | 0.41777 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 17.2964 | 0% | CZ 0B | 0 | 0 | 0.010887 | 0.00095603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.05811 | 0% | CZ 0B | 26.67 | 1.7463 | 2.2058 | 0.10449 | 0 | 76.7407 | 0 | 21.3552 | 5.0599 | 0.0070796 | 4.3736 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 187.4275 | 0%
CZ 1A | 0.27574 | 0.017736 | 0.021546 | 3.2654e-05 | 0 | 0.56036 | 0 | 0.17728 | 0.048957 | 5.9904e-05 | 0.044317 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.6392 | 2.71% | CZ 1A | 8.8507 | 0.56927 | 1.4771 | 0.003332 | 0 | 17.9862 | 0 | 5.6904 | 1.5714 | 0.0019228 | 1.4225 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 56.5748 | 2.71% | CZ 1A | 2.594 | 0.16684 | 0.097041 | 0 | 0 | 5.2715 | 0 | 1.6678 | 0.46056 | 0.00056354 | 0.4169 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 14.8883 | 2.71% | CZ 1A | 0 | 0 | 0.01146 | 3.332e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.05776 | 2.71% | CZ 1A | 27.1565 | 1.7467 | 2.2685 | 0.0036419 | 0 | 55.1869 | 0 | 17.4598 | 4.8216 | 0.0058997 | 4.3646 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 162.1784 | 2.71%
CZ 1B | 0.27526 | 0.017708 | 0.02192 | 0.004736 | 0 | 0.63597 | 0 | 0.17514 | 0.046765 | 0.00011581 | 0.044269 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.7151 | 0% | CZ 1B | 8.8353 | 0.56837 | 1.5152 | 0.48327 | 0 | 20.4134 | 0 | 5.6217 | 1.5011 | 0.0037174 | 1.4209 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 59.365 | 0% | CZ 1B | 2.5895 | 0.16658 | 0.097041 | 0 | 0 | 5.9828 | 0 | 1.6476 | 0.43993 | 0.0010895 | 0.41645 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 15.5542 | 0% | CZ 1B | 0 | 0 | 0.011841 | 0.0048327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.062942 | 0% | CZ 1B | 27.1093 | 1.7439 | 2.3102 | 0.52821 | 0 | 62.6342 | 0 | 17.249 | 4.6057 | 0.011406 | 4.3598 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 169.7162 | 0%
CZ 2A | 0.27655 | 0.0177 | 0.022652 | 0.0040579 | 0 | 0.42906 | 0 | 0.16208 | 0.028638 | 0.00013978 | 0.044277 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.4784 | 20.22% | CZ 2A | 8.8767 | 0.56812 | 1.59 | 0.41407 | 0 | 13.772 | 0 | 5.2025 | 0.91922 | 0.0044865 | 1.4212 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 51.7703 | 20.22% | CZ 2A | 2.6016 | 0.16651 | 0.097041 | 0 | 0 | 4.0363 | 0 | 1.5248 | 0.26941 | 0.0013149 | 0.41653 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 13.3267 | 20.22% | CZ 2A | 0 | 0 | 0.012589 | 0.0041407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.062997 | 20.22% | CZ 2A | 27.2363 | 1.7431 | 2.3919 | 0.45258 | 0 | 42.2564 | 0 | 15.9629 | 2.8204 | 0.013766 | 4.3606 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 146.4024 | 20.22%
CZ 2B | 0.27986 | 0.017716 | 0.022811 | 0.0041998 | 0 | 0.3611 | 0 | 0.17748 | 0.022731 | 0.00014776 | 0.043822 | 0 | 0.0096645 | 0.10513 | 0 | 0.37841 | 1.4231 | 2.485% | CZ 2B | 8.9829 | 0.56863 | 1.6059 | 0.42855 | 0 | 11.5907 | 0 | 5.6967 | 0.72963 | 0.0047429 | 1.4066 | 0 | 0.31021 | 6.5458 | 0 | 12.1461 | 50.0163 | 2.485% | CZ 2B | 2.6327 | 0.16666 | 0.097078 | 0 | 0 | 3.397 | 0 | 1.6696 | 0.21384 | 0.0013901 | 0.41224 | 0 | 0.090917 | 0.56245 | 0 | 3.5598 | 12.8037 | 2.485% | CZ 2B | 0 | 0 | 0.012746 | 0.0042855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.063299 | 2.485% | CZ 2B | 27.562 | 1.7447 | 2.4095 | 0.4684 | 0 | 35.5635 | 0 | 17.4791 | 2.2387 | 0.014552 | 4.3158 | 0 | 0.95181 | 10.9453 | 0 | 37.2677 | 140.961 | 2.485%
CZ 3A | 0.27999 | 0.017712 | 0.024357 | 0.028109 | 0 | 0.24194 | 0 | 0.14079 | 0.027128 | 0.00052715 | 0.044061 | 0 | 0.0096645 | 0.10513 | 0 | 0.37841 | 1.2978 | 19.44% | CZ 3A | 8.9871 | 0.5685 | 1.7636 | 2.8682 | 0 | 7.7659 | 0 | 4.5189 | 0.87076 | 0.01692 | 1.4143 | 0 | 0.31021 | 6.5458 | 0 | 12.1461 | 47.7763 | 19.44% | CZ 3A | 2.634 | 0.16662 | 0.097078 | 0 | 0 | 2.276 | 0 | 1.3244 | 0.25521 | 0.0049591 | 0.4145 | 0 | 0.090917 | 0.56245 | 0 | 3.5598 | 11.386 | 19.44% | CZ 3A | 0 | 0 | 0.014324 | 0.028682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.089274 | 19.44% | CZ 3A | 27.575 | 1.7443 | 2.5819 | 3.135 | 0 | 23.8279 | 0 | 13.8654 | 2.6718 | 0.051917 | 4.3394 | 0 | 0.95181 | 10.9453 | 0 | 37.2677 | 128.9573 | 19.44%
CZ 3B | 0.27875 | 0.017712 | 0.023911 | 0.01412 | 0 | 0.25863 | 0 | 0.16343 | 0 | 0.00028354 | 0.043794 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.2938 | 7.425% | CZ 3B | 8.9472 | 0.5685 | 1.7181 | 1.4408 | 0 | 8.3015 | 0 | 5.2456 | 0 | 0.0091012 | 1.4057 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 46.6386 | 7.425% | CZ 3B | 2.6223 | 0.16662 | 0.097078 | 0 | 0 | 2.433 | 0 | 1.5374 | 0 | 0.0026674 | 0.41198 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 11.4842 | 7.425% | CZ 3B | 0 | 0 | 0.013869 | 0.014408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.074545 | 7.425% | CZ 3B | 27.4526 | 1.7443 | 2.5322 | 1.5748 | 0 | 25.4715 | 0 | 16.095 | 0 | 0.027925 | 4.313 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 128.3759 | 7.425%
CZ 3C | 0.27808 | 0.01774 | 0.024225 | 0.0060133 | 0 | 0.16712 | 0 | 0.12859 | 0 | 0.00017172 | 0.044057 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.1592 | 0.9093% | CZ 3C | 8.9257 | 0.5694 | 1.7502 | 0.6136 | 0 | 5.3642 | 0 | 4.1274 | 0 | 0.005512 | 1.4141 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 41.7721 | 0.9093% | CZ 3C | 2.616 | 0.16688 | 0.097078 | 0 | 0 | 1.5722 | 0 | 1.2097 | 0 | 0.0016155 | 0.41446 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 10.291 | 0.9093% | CZ 3C | 0 | 0 | 0.014189 | 0.006136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.066593 | 0.9093% | CZ 3C | 27.3866 | 1.7471 | 2.5672 | 0.67067 | 0 | 16.4588 | 0 | 12.6642 | 0 | 0.016912 | 4.339 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 115.0149 | 0.9093%
CZ 4A | 0.27188 | 0.017747 | 0.02557 | 0.033976 | 0 | 0.1698 | 0 | 0.13943 | 0.030044 | 0.00070686 | 0.044025 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.2264 | 18.26% | CZ 4A | 8.7267 | 0.56966 | 1.8874 | 3.467 | 0 | 5.4503 | 0 | 4.4755 | 0.96434 | 0.022689 | 1.4131 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 45.9787 | 18.26% | CZ 4A | 2.5577 | 0.16696 | 0.097078 | 0 | 0 | 1.5974 | 0 | 1.3117 | 0.28263 | 0.0066497 | 0.41416 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 10.6474 | 18.26% | CZ 4A | 0 | 0 | 0.015562 | 0.03467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.096499 | 18.26% | CZ 4A | 26.7762 | 1.7479 | 2.7172 | 3.7894 | 0 | 16.7231 | 0 | 13.732 | 2.9589 | 0.069616 | 4.3358 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 122.0145 | 18.26%
CZ 4B | 0.26937 | 0.017704 | 0.025172 | 0.025697 | 0 | 0.18255 | 0 | 0.16775 | 0 | 0.00046725 | 0.043746 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.2257 | 0.672% | CZ 4B | 8.6462 | 0.56825 | 1.8468 | 2.6222 | 0 | 5.8594 | 0 | 5.3844 | 0 | 0.014998 | 1.4041 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 45.3484 | 0.672% | CZ 4B | 2.5341 | 0.16654 | 0.097078 | 0 | 0 | 1.7173 | 0 | 1.5781 | 0 | 0.0043956 | 0.41153 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 10.7221 | 0.672% | CZ 4B | 0 | 0 | 0.015156 | 0.026222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.087645 | 0.672% | CZ 4B | 26.5292 | 1.7435 | 2.6728 | 2.866 | 0 | 17.9782 | 0 | 16.521 | 0 | 0.046017 | 4.3083 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 121.8295 | 0.672%
CZ 4C | 0.27753 | 0.017744 | 0.025752 | 0.070793 | 0 | 0.070091 | 0 | 0.13377 | 0 | 0.0012779 | 0.043969 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.1341 | 2.388% | CZ 4C | 8.908 | 0.56953 | 1.906 | 7.2238 | 0 | 2.2498 | 0 | 4.2938 | 0 | 0.041019 | 1.4113 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 45.6053 | 2.388% | CZ 4C | 2.6108 | 0.16692 | 0.097078 | 0 | 0 | 0.65937 | 0 | 1.2584 | 0 | 0.012022 | 0.41363 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 9.4314 | 2.388% | CZ 4C | 0 | 0 | 0.015748 | 0.072238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13425 | 2.388% | CZ 4C | 27.3323 | 1.7475 | 2.7375 | 7.8956 | 0 | 6.903 | 0 | 13.1747 | 0 | 0.12586 | 4.3303 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 113.4112 | 2.388%
CZ 5A | 0.27277 | 0.017716 | 0.026585 | 0.06787 | 0 | 0.10687 | 0 | 0.13529 | 0.027879 | 0.0011382 | 0.044001 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.1933 | 16% | CZ 5A | 8.7553 | 0.56863 | 1.991 | 6.9255 | 0 | 3.4302 | 0 | 4.3424 | 0.89486 | 0.036533 | 1.4123 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 47.3588 | 16% | CZ 5A | 2.566 | 0.16666 | 0.097078 | 0 | 0 | 1.0053 | 0 | 1.2727 | 0.26227 | 0.010707 | 0.41394 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 10.0079 | 16% | CZ 5A | 0 | 0 | 0.016597 | 0.069255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13212 | 16% | CZ 5A | 26.8639 | 1.7447 | 2.8304 | 7.5695 | 0 | 10.525 | 0 | 13.3238 | 2.7457 | 0.11209 | 4.3335 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 119.2129 | 16%
CZ 5B | 0.27107 | 0.017736 | 0.026232 | 0.064847 | 0 | 0.13285 | 0 | 0.1663 | 0 | 0.0010463 | 0.043786 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.2171 | 4.803% | CZ 5B | 8.7007 | 0.56927 | 1.9549 | 6.617 | 0 | 4.2642 | 0 | 5.338 | 0 | 0.033585 | 1.4054 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 47.8852 | 4.803% | CZ 5B | 2.55 | 0.16684 | 0.097078 | 0 | 0 | 1.2498 | 0 | 1.5645 | 0 | 0.0098431 | 0.41191 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 10.2631 | 4.803% | CZ 5B | 0 | 0 | 0.016237 | 0.06617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12867 | 4.803% | CZ 5B | 26.6963 | 1.7467 | 2.791 | 7.2324 | 0 | 13.0839 | 0 | 16.3786 | 0 | 0.10305 | 4.3123 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 121.5086 | 4.803%
CZ 5C | 0.27581 | 0.017732 | 0.026293 | 0.043786 | 0 | 0.041861 | 0 | 0.12925 | 0.021206 | 0.0010343 | 0.043977 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.0941 | 0.03694% | CZ 5C | 8.8527 | 0.56914 | 1.9612 | 4.468 | 0 | 1.3436 | 0 | 4.1486 | 0.68066 | 0.0332 | 1.4116 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 42.4708 | 0.03694% | CZ 5C | 2.5946 | 0.16681 | 0.097078 | 0 | 0 | 0.3938 | 0 | 1.2159 | 0.19949 | 0.0097304 | 0.41371 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 9.3042 | 0.03694% | CZ 5C | 0 | 0 | 0.0163 | 0.04468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10725 | 0.03694% | CZ 5C | 27.1628 | 1.7463 | 2.7979 | 4.8835 | 0 | 4.1227 | 0 | 12.7291 | 2.0885 | 0.10187 | 4.3311 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 109.1281 | 0.03694%
CZ 6A | 0.27316 | 0.017728 | 0.027423 | 0.13142 | 0 | 0.113 | 0 | 0.14997 | 0.029868 | 0.001897 | 0.043997 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.2817 | 3.249% | CZ 6A | 8.7679 | 0.56902 | 2.0762 | 13.4106 | 0 | 3.627 | 0 | 4.8136 | 0.9587 | 0.060888 | 1.4122 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 54.6981 | 3.249% | CZ 6A | 2.5697 | 0.16677 | 0.097116 | 0 | 0 | 1.063 | 0 | 1.4108 | 0.28098 | 0.017845 | 0.4139 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 10.2333 | 3.249% | CZ 6A | 0 | 0 | 0.017448 | 0.13411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19782 | 3.249% | CZ 6A | 26.9024 | 1.7459 | 2.9238 | 14.6578 | 0 | 11.1287 | 0 | 14.7696 | 2.9416 | 0.18682 | 4.3331 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 128.754 | 3.249%
CZ 6B | 0.27351 | 0.017708 | 0.027149 | 0.092499 | 0 | 0.082783 | 0 | 0.15685 | 0.027556 | 0.0015934 | 0.043802 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.2166 | 0.979% | CZ 6B | 8.779 | 0.56837 | 2.0485 | 9.4387 | 0 | 2.6572 | 0 | 5.0346 | 0.88448 | 0.051146 | 1.4059 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 49.8699 | 0.979% | CZ 6B | 2.573 | 0.16658 | 0.097078 | 0 | 0 | 0.77877 | 0 | 1.4756 | 0.25923 | 0.01499 | 0.41206 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 9.9904 | 0.979% | CZ 6B | 0 | 0 | 0.017173 | 0.094387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.15783 | 0.979% | CZ 6B | 26.9366 | 1.7439 | 2.8933 | 10.3165 | 0 | 8.1529 | 0 | 15.4476 | 2.7138 | 0.15693 | 4.3138 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 121.8399 | 0.979%
CZ 7 | 0.27139 | 0.017736 | 0.028303 | 0.16387 | 0 | 0.09236 | 0 | 0.15355 | 0.029688 | 0.0023362 | 0.043961 | 0 | 0.0096605 | 0.10513 | 0 | 0.37841 | 1.2964 | 0.3956% | CZ 7 | 8.711 | 0.56927 | 2.166 | 16.7216 | 0 | 2.9645 | 0 | 4.9287 | 0.95293 | 0.074989 | 1.4111 | 0 | 0.31008 | 6.5458 | 0 | 12.1461 | 57.5021 | 0.3956% | CZ 7 | 2.553 | 0.16684 | 0.097116 | 0 | 0 | 0.86886 | 0 | 1.4445 | 0.27929 | 0.021978 | 0.41356 | 0 | 0.090879 | 0.56245 | 0 | 3.5598 | 10.0584 | 0.3956% | CZ 7 | 0 | 0 | 0.018347 | 0.16722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.23183 | 0.3956% | CZ 7 | 26.7278 | 1.7467 | 3.022 | 18.2767 | 0 | 9.0961 | 0 | 15.1228 | 2.9239 | 0.23009 | 4.3296 | 0 | 0.95142 | 10.9453 | 0 | 37.2677 | 130.6399 | 0.3956%
CZ 8 | 0.28574 | 0.017847 | 0.029412 | 0.31197 | 0 | 0.042108 | 0 | 0.17818 | 0.033151 | 0.0042292 | 0.043814 | 0 | 0.0096685 | 0.10513 | 0 | 0.37841 | 1.4397 | 0.02728% | CZ 8 | 9.1715 | 0.57286 | 2.2789 | 31.8341 | 0 | 1.3516 | 0 | 5.7191 | 1.0641 | 0.13575 | 1.4063 | 0 | 0.31034 | 6.5458 | 0 | 12.1461 | 72.5365 | 0.02728% | CZ 8 | 2.688 | 0.1679 | 0.097153 | 0 | 0 | 0.39613 | 0 | 1.6762 | 0.31186 | 0.039786 | 0.41217 | 0 | 0.090955 | 0.56245 | 0 | 3.5598 | 10.0024 | 0.02728% | CZ 8 | 0 | 0 | 0.019474 | 0.31834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.38408 | 0.02728% | CZ 8 | 28.1409 | 1.7577 | 3.1456 | 34.7946 | 0 | 4.1471 | 0 | 17.5479 | 3.2649 | 0.41652 | 4.315 | 0 | 0.9522 | 10.9453 | 0 | 37.2677 | 146.6955 | 0.02728%
US Weighted | 0.27555 | 0.01772 | 0.024715 | 0.035459 | 0 | 0.24093 | 0 | 0.14919 | 0.024277 | 0.00064175 | 0.044047 | 0 | 0.0096614 | 0.10513 | 0 | 0.37841 | 1.3057 | 100% | US Weighted | 8.8446 | 0.56877 | 1.8002 | 3.6183 | 0 | 7.7333 | 0 | 4.7886 | 0.77925 | 0.020599 | 1.4138 | 0 | 0.31011 | 6.5458 | 0 | 12.1461 | 48.5694 | 100% | US Weighted | 2.5922 | 0.1667 | 0.097071 | 0 | 0 | 2.2665 | 0 | 1.4035 | 0.22838 | 0.0060372 | 0.41437 | 0 | 0.090888 | 0.56245 | 0 | 3.5598 | 11.3879 | 100% | US Weighted | 0 | 0 | 0.01469 | 0.036183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.09714 | 100% | US Weighted | 27.1379 | 1.7451 | 2.6218 | 3.9548 | 0 | 23.7279 | 0 | 14.6928 | 2.3909 | 0.063203 | 4.338 | 0 | 0.9515 | 10.9453 | 0 | 37.2677 | 129.837 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.30788 | 0.017736 | 0.020731 | 0.0014719 | 0 | 1.0661 | 0 | 0.20033 | 0.078722 | 7.5878e-05 | 0.055127 | 0 | 0.010827 | 0.10513 | 0 | 0.43322 | 2.2974 | 0% | CZ 0A | 9.8822 | 0.56927 | 1.3939 | 0.1502 | 0 | 34.2204 | 0 | 6.4303 | 2.5268 | 0.0024355 | 1.7695 | 0 | 0.34751 | 6.5458 | 0 | 13.9054 | 77.7437 | 0% | CZ 0A | 2.8963 | 0.16684 | 0.097041 | 0 | 0 | 10.0294 | 0 | 1.8846 | 0.74056 | 0.00071381 | 0.5186 | 0 | 0.10185 | 0.56245 | 0 | 4.0754 | 21.0738 | 0% | CZ 0A | 0 | 0 | 0.010628 | 0.001502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.058397 | 0% | CZ 0A | 30.3214 | 1.7467 | 2.1775 | 0.16417 | 0 | 104.998 | 0 | 19.73 | 7.7529 | 0.0074729 | 5.4293 | 0 | 1.0663 | 10.9453 | 0 | 42.6659 | 227.005 | 0%
CZ 0B | 0.30934 | 0.017732 | 0.020987 | 0.0014229 | 0 | 0.85469 | 0 | 0.2043 | 0.052436 | 7.5878e-05 | 0.054948 | 0 | 0.010827 | 0.10513 | 0 | 0.43322 | 2.0651 | 0% | CZ 0B | 9.9291 | 0.56914 | 1.42 | 0.1452 | 0 | 27.4336 | 0 | 6.5576 | 1.6831 | 0.0024355 | 1.7637 | 0 | 0.34751 | 6.5458 | 0 | 13.9054 | 70.3027 | 0% | CZ 0B | 2.9101 | 0.16681 | 0.097041 | 0 | 0 | 8.0403 | 0 | 1.9219 | 0.49328 | 0.00071381 | 0.51691 | 0 | 0.10185 | 0.56245 | 0 | 4.0754 | 18.8868 | 0% | CZ 0B | 0 | 0 | 0.010889 | 0.001452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.058609 | 0% | CZ 0B | 30.4654 | 1.7463 | 2.2061 | 0.1587 | 0 | 84.1742 | 0 | 20.1206 | 5.1642 | 0.0074729 | 5.4116 | 0 | 1.0663 | 10.9453 | 0 | 42.6659 | 204.1319 | 0%
CZ 1A | 0.3118 | 0.017736 | 0.021545 | 0.0034776 | 0 | 0.74708 | 0 | 0.25935 | 0.071905 | 0.00010383 | 0.05492 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 2.0371 | 2.71% | CZ 1A | 10.0082 | 0.56927 | 1.4769 | 0.35486 | 0 | 23.9798 | 0 | 8.3246 | 2.308 | 0.0033328 | 1.7628 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 69.5867 | 2.71% | CZ 1A | 2.9332 | 0.16684 | 0.097041 | 0 | 0 | 7.0281 | 0 | 2.4398 | 0.67643 | 0.00097679 | 0.51665 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 18.5988 | 2.71% | CZ 1A | 0 | 0 | 0.011458 | 0.0035486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.061274 | 2.71% | CZ 1A | 30.7081 | 1.7467 | 2.2683 | 0.38786 | 0 | 73.5769 | 0 | 25.5423 | 7.0815 | 0.010226 | 5.4088 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 201.4086 | 2.71%
CZ 1B | 0.31148 | 0.017708 | 0.021925 | 0.007062 | 0 | 0.69509 | 0 | 0.17529 | 0.049021 | 0.00014776 | 0.054812 | 0 | 0.010827 | 0.10513 | 0 | 0.43322 | 1.8817 | 0% | CZ 1B | 9.9977 | 0.56837 | 1.5158 | 0.72061 | 0 | 22.3108 | 0 | 5.6263 | 1.5735 | 0.0047429 | 1.7593 | 0 | 0.34751 | 6.5458 | 0 | 13.9054 | 64.8759 | 0% | CZ 1B | 2.9302 | 0.16658 | 0.097041 | 0 | 0 | 6.5389 | 0 | 1.649 | 0.46116 | 0.0013901 | 0.51563 | 0 | 0.10185 | 0.56245 | 0 | 4.0754 | 17.0996 | 0% | CZ 1B | 0 | 0 | 0.011847 | 0.0072061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.06532 | 0% | CZ 1B | 30.6758 | 1.7439 | 2.3108 | 0.78763 | 0 | 68.456 | 0 | 17.2632 | 4.8279 | 0.014552 | 5.3982 | 0 | 1.0663 | 10.9453 | 0 | 42.6659 | 186.1553 | 0%
CZ 2A | 0.31218 | 0.0177 | 0.022645 | 0.014216 | 0 | 0.53292 | 0 | 0.22896 | 0.036581 | 0.00027556 | 0.054856 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.7695 | 20.22% | CZ 2A | 10.0204 | 0.56812 | 1.5892 | 1.4506 | 0 | 17.1056 | 0 | 7.3493 | 1.1742 | 0.0088448 | 1.7608 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 61.8258 | 20.22% | CZ 2A | 2.9368 | 0.16651 | 0.097041 | 0 | 0 | 5.0134 | 0 | 2.1539 | 0.34413 | 0.0025923 | 0.51605 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 15.9702 | 20.22% | CZ 2A | 0 | 0 | 0.012581 | 0.014506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.073354 | 20.22% | CZ 2A | 30.7454 | 1.7431 | 2.391 | 1.5855 | 0 | 52.4849 | 0 | 22.5496 | 3.6027 | 0.027138 | 5.4025 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 175.2098 | 20.22%
CZ 2B | 0.31415 | 0.017716 | 0.022815 | 0.0081936 | 0 | 0.38974 | 0 | 0.19305 | 0.028822 | 0.00019968 | 0.054341 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.5782 | 2.485% | CZ 2B | 10.0835 | 0.56863 | 1.6062 | 0.83608 | 0 | 12.5099 | 0 | 6.1964 | 0.92511 | 0.0064093 | 1.7442 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 55.2753 | 2.485% | CZ 2B | 2.9553 | 0.16666 | 0.097078 | 0 | 0 | 3.6664 | 0 | 1.816 | 0.27114 | 0.0018785 | 0.5112 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 14.2255 | 2.485% | CZ 2B | 0 | 0 | 0.01275 | 0.0083608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.067378 | 2.485% | CZ 2B | 30.9389 | 1.7447 | 2.4099 | 0.91383 | 0 | 38.3839 | 0 | 19.0122 | 2.8385 | 0.019666 | 5.3518 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 156.2913 | 2.485%
CZ 3A | 0.31437 | 0.017712 | 0.024335 | 0.045474 | 0 | 0.3052 | 0 | 0.18767 | 0.028726 | 0.00077476 | 0.054624 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.5281 | 19.44% | CZ 3A | 10.0906 | 0.5685 | 1.7614 | 4.6402 | 0 | 9.7962 | 0 | 6.0239 | 0.92204 | 0.024868 | 1.7533 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 56.38 | 19.44% | CZ 3A | 2.9574 | 0.16662 | 0.097078 | 0 | 0 | 2.8711 | 0 | 1.7655 | 0.27023 | 0.0072884 | 0.51387 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 13.3889 | 19.44% | CZ 3A | 0 | 0 | 0.014302 | 0.046402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10697 | 19.44% | CZ 3A | 30.961 | 1.7443 | 2.5795 | 5.0718 | 0 | 30.0575 | 0 | 18.4832 | 2.8291 | 0.076302 | 5.3797 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 151.8602 | 19.44%
CZ 3B | 0.31384 | 0.017712 | 0.023916 | 0.016778 | 0 | 0.27317 | 0 | 0.19097 | 0.029133 | 0.00044728 | 0.054317 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.4695 | 7.425% | CZ 3B | 10.0737 | 0.5685 | 1.7186 | 1.712 | 0 | 8.7681 | 0 | 6.1296 | 0.93511 | 0.014357 | 1.7435 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 52.4624 | 7.425% | CZ 3B | 2.9524 | 0.16662 | 0.097078 | 0 | 0 | 2.5698 | 0 | 1.7965 | 0.27407 | 0.0042077 | 0.51098 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 13.1114 | 7.425% | CZ 3B | 0 | 0 | 0.013874 | 0.01712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.077262 | 7.425% | CZ 3B | 30.9091 | 1.7443 | 2.5327 | 1.8712 | 0 | 26.9032 | 0 | 18.8073 | 2.8692 | 0.044051 | 5.3494 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 145.7083 | 7.425%
CZ 3C | 0.3134 | 0.01774 | 0.024236 | 0.010394 | 0 | 0.19266 | 0 | 0.16789 | 0.019521 | 0.00023562 | 0.054608 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.3499 | 0.9093% | CZ 3C | 10.0594 | 0.5694 | 1.7513 | 1.0606 | 0 | 6.1841 | 0 | 5.3888 | 0.62657 | 0.0075629 | 1.7528 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 48.1993 | 0.9093% | CZ 3C | 2.9482 | 0.16688 | 0.097078 | 0 | 0 | 1.8124 | 0 | 1.5794 | 0.18364 | 0.0022166 | 0.51372 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 12.0433 | 0.9093% | CZ 3C | 0 | 0 | 0.014201 | 0.010606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.071074 | 0.9093% | CZ 3C | 30.865 | 1.7471 | 2.5685 | 1.1592 | 0 | 18.9745 | 0 | 16.5344 | 1.9225 | 0.023205 | 5.3781 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 133.8502 | 0.9093%
CZ 4A | 0.31113 | 0.017747 | 0.025567 | 0.059179 | 0 | 0.21372 | 0 | 0.18579 | 0.032184 | 0.0010543 | 0.054596 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.4502 | 18.26% | CZ 4A | 9.9865 | 0.56966 | 1.8872 | 6.0386 | 0 | 6.8601 | 0 | 5.9634 | 1.033 | 0.033841 | 1.7524 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 54.9237 | 18.26% | CZ 4A | 2.9269 | 0.16696 | 0.097078 | 0 | 0 | 2.0106 | 0 | 1.7478 | 0.30277 | 0.0099182 | 0.51361 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 12.5154 | 18.26% | CZ 4A | 0 | 0 | 0.015559 | 0.060386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12221 | 18.26% | CZ 4A | 30.6416 | 1.7479 | 2.7169 | 6.6002 | 0 | 21.0488 | 0 | 18.2976 | 3.1697 | 0.10383 | 5.3769 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 144.3813 | 18.26%
CZ 4B | 0.31023 | 0.017704 | 0.025191 | 0.02653 | 0 | 0.20327 | 0 | 0.19529 | 0.029752 | 0.00075479 | 0.054281 | 0 | 0.010827 | 0.10513 | 0 | 0.43322 | 1.4122 | 0.672% | CZ 4B | 9.9576 | 0.56825 | 1.8487 | 2.7071 | 0 | 6.5244 | 0 | 6.2683 | 0.95498 | 0.024227 | 1.7423 | 0 | 0.34751 | 6.5458 | 0 | 13.9054 | 51.3946 | 0.672% | CZ 4B | 2.9184 | 0.16654 | 0.097078 | 0 | 0 | 1.9122 | 0 | 1.8371 | 0.27989 | 0.0071005 | 0.51064 | 0 | 0.10185 | 0.56245 | 0 | 4.0754 | 12.4687 | 0.672% | CZ 4B | 0 | 0 | 0.015175 | 0.027071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.088514 | 0.672% | CZ 4B | 30.5527 | 1.7435 | 2.6749 | 2.9589 | 0 | 20.0187 | 0 | 19.2329 | 2.9302 | 0.074336 | 5.3459 | 0 | 1.0663 | 10.9453 | 0 | 42.6659 | 140.2094 | 0.672%
CZ 4C | 0.31372 | 0.017744 | 0.025746 | 0.055808 | 0 | 0.080495 | 0 | 0.17339 | 0.024281 | 0.0010343 | 0.054528 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.2959 | 2.388% | CZ 4C | 10.0697 | 0.56953 | 1.9054 | 5.6947 | 0 | 2.5837 | 0 | 5.5654 | 0.77937 | 0.0332 | 1.7502 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 49.7501 | 2.388% | CZ 4C | 2.9513 | 0.16692 | 0.097078 | 0 | 0 | 0.75724 | 0 | 1.6311 | 0.22842 | 0.0097304 | 0.51297 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 11.0945 | 2.388% | CZ 4C | 0 | 0 | 0.015741 | 0.056947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11896 | 2.388% | CZ 4C | 30.8969 | 1.7475 | 2.7368 | 6.2243 | 0 | 7.9276 | 0 | 17.0763 | 2.3913 | 0.10187 | 5.3703 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 129.1506 | 2.388%
CZ 5A | 0.31127 | 0.017716 | 0.026581 | 0.10147 | 0 | 0.13019 | 0 | 0.17886 | 0.029537 | 0.0015974 | 0.054564 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.401 | 16% | CZ 5A | 9.991 | 0.56863 | 1.9906 | 10.354 | 0 | 4.179 | 0 | 5.7412 | 0.94806 | 0.051274 | 1.7514 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 56.374 | 16% | CZ 5A | 2.9282 | 0.16666 | 0.097078 | 0 | 0 | 1.2248 | 0 | 1.6826 | 0.27786 | 0.015028 | 0.51331 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 11.6453 | 16% | CZ 5A | 0 | 0 | 0.016593 | 0.10354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.1664 | 16% | CZ 5A | 30.6554 | 1.7447 | 2.83 | 11.3169 | 0 | 12.8223 | 0 | 17.6156 | 2.9089 | 0.15732 | 5.3738 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 140.1027 | 16%
CZ 5B | 0.31113 | 0.017736 | 0.026254 | 0.066693 | 0 | 0.14825 | 0 | 0.19686 | 0.032923 | 0.0014816 | 0.054337 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.4048 | 4.803% | CZ 5B | 9.9867 | 0.56927 | 1.9573 | 6.8054 | 0 | 4.7586 | 0 | 6.3186 | 1.0568 | 0.047557 | 1.7441 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 54.0432 | 4.803% | CZ 5B | 2.9269 | 0.16684 | 0.097078 | 0 | 0 | 1.3947 | 0 | 1.8519 | 0.30972 | 0.013938 | 0.51116 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 12.012 | 4.803% | CZ 5B | 0 | 0 | 0.01626 | 0.068054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13058 | 4.803% | CZ 5B | 30.642 | 1.7467 | 2.7936 | 7.4383 | 0 | 14.6008 | 0 | 19.3874 | 3.2424 | 0.14592 | 5.3514 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 140.0264 | 4.803%
CZ 5C | 0.31314 | 0.017732 | 0.026313 | 0.073859 | 0 | 0.043798 | 0 | 0.16329 | 0.023119 | 0.0013698 | 0.054544 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.2663 | 0.03694% | CZ 5C | 10.051 | 0.56914 | 1.9633 | 7.5366 | 0 | 1.4058 | 0 | 5.2414 | 0.74207 | 0.043968 | 1.7508 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 50.1029 | 0.03694% | CZ 5C | 2.9458 | 0.16681 | 0.097078 | 0 | 0 | 0.41202 | 0 | 1.5362 | 0.21749 | 0.012886 | 0.51312 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 10.6411 | 0.03694% | CZ 5C | 0 | 0 | 0.01632 | 0.075366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13795 | 0.03694% | CZ 5C | 30.8394 | 1.7463 | 2.8001 | 8.2375 | 0 | 4.3134 | 0 | 16.0821 | 2.2769 | 0.13491 | 5.3718 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 126.4803 | 0.03694%
CZ 6A | 0.31171 | 0.017728 | 0.027418 | 0.18244 | 0 | 0.14506 | 0 | 0.19889 | 0.034704 | 0.0025958 | 0.054512 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.5242 | 3.249% | CZ 6A | 10.0051 | 0.56902 | 2.0757 | 18.6162 | 0 | 4.656 | 0 | 6.3839 | 1.1139 | 0.083321 | 1.7497 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 66.0518 | 3.249% | CZ 6A | 2.9323 | 0.16677 | 0.097116 | 0 | 0 | 1.3646 | 0 | 1.871 | 0.32647 | 0.02442 | 0.51282 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 12.0353 | 3.249% | CZ 6A | 0 | 0 | 0.017443 | 0.18616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.24987 | 3.249% | CZ 6A | 30.6986 | 1.7459 | 2.9232 | 20.3475 | 0 | 14.2858 | 0 | 19.5876 | 3.4179 | 0.25565 | 5.3687 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 153.3088 | 3.249%
CZ 6B | 0.31216 | 0.017708 | 0.027169 | 0.13654 | 0 | 0.09974 | 0 | 0.201 | 0.030355 | 0.0023562 | 0.054329 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.4305 | 0.979% | CZ 6B | 10.0197 | 0.56837 | 2.0506 | 13.9323 | 0 | 3.2014 | 0 | 6.4517 | 0.97434 | 0.075629 | 1.7438 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 59.8168 | 0.979% | CZ 6B | 2.9366 | 0.16658 | 0.097078 | 0 | 0 | 0.93829 | 0 | 1.8909 | 0.28556 | 0.022166 | 0.51109 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 11.588 | 0.979% | CZ 6B | 0 | 0 | 0.017193 | 0.13932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.20278 | 0.979% | CZ 6B | 30.7435 | 1.7439 | 2.8955 | 15.228 | 0 | 9.8229 | 0 | 19.7957 | 2.9895 | 0.23205 | 5.3506 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 143.4796 | 0.979%
CZ 7 | 0.31095 | 0.017736 | 0.028313 | 0.23208 | 0 | 0.11584 | 0 | 0.20529 | 0.032584 | 0.0033466 | 0.054453 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.5498 | 0.3956% | CZ 7 | 9.9808 | 0.56927 | 2.167 | 23.6819 | 0 | 3.7183 | 0 | 6.5894 | 1.0459 | 0.10742 | 1.7478 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 70.4066 | 0.3956% | CZ 7 | 2.9252 | 0.16684 | 0.097116 | 0 | 0 | 1.0898 | 0 | 1.9312 | 0.30653 | 0.031483 | 0.51225 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 11.8002 | 0.3956% | CZ 7 | 0 | 0 | 0.018357 | 0.23682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.30144 | 0.3956% | CZ 7 | 30.6239 | 1.7467 | 3.0231 | 25.8843 | 0 | 11.4087 | 0 | 20.2181 | 3.209 | 0.32959 | 5.3628 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 156.4841 | 0.3956%
CZ 8 | 0.32049 | 0.017847 | 0.029436 | 0.43905 | 0 | 0.048881 | 0 | 0.22601 | 0.036509 | 0.0057747 | 0.054217 | 0 | 0.010835 | 0.10513 | 0 | 0.43322 | 1.7274 | 0.02728% | CZ 8 | 10.287 | 0.57286 | 2.2811 | 44.801 | 0 | 1.569 | 0 | 7.2544 | 1.1719 | 0.18536 | 1.7402 | 0 | 0.34777 | 6.5458 | 0 | 13.9054 | 90.6618 | 0.02728% | CZ 8 | 3.015 | 0.1679 | 0.097191 | 0 | 0 | 0.45984 | 0 | 2.1261 | 0.34346 | 0.054325 | 0.51004 | 0 | 0.10192 | 0.56245 | 0 | 4.0754 | 11.5137 | 0.02728% | CZ 8 | 0 | 0 | 0.019495 | 0.44801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.51377 | 0.02728% | CZ 8 | 31.5635 | 1.7577 | 3.1483 | 48.9675 | 0 | 4.8141 | 0 | 22.2586 | 3.5956 | 0.56873 | 5.3396 | 0 | 1.0671 | 10.9453 | 0 | 42.6659 | 176.6918 | 0.02728%
US Weighted | 0.3124 | 0.01772 | 0.02471 | 0.053437 | 0 | 0.29549 | 0 | 0.19713 | 0.032522 | 0.00092123 | 0.054609 | 0 | 0.010831 | 0.10513 | 0 | 0.43322 | 1.5381 | 100% | US Weighted | 10.0273 | 0.56877 | 1.7997 | 5.4528 | 0 | 9.4846 | 0 | 6.3273 | 1.0439 | 0.029569 | 1.7528 | 0 | 0.34764 | 6.5458 | 0 | 13.9054 | 57.2856 | 100% | US Weighted | 2.9388 | 0.1667 | 0.097071 | 0 | 0 | 2.7798 | 0 | 1.8544 | 0.30595 | 0.0086663 | 0.51372 | 0 | 0.10189 | 0.56245 | 0 | 4.0754 | 13.4049 | 100% | US Weighted | 0 | 0 | 0.014685 | 0.054528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.11548 | 100% | US Weighted | 30.7666 | 1.7451 | 2.6213 | 5.9599 | 0 | 29.1014 | 0 | 19.414 | 3.203 | 0.090728 | 5.3782 | 0 | 1.0667 | 10.9453 | 0 | 42.6659 | 152.958 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.48336 | 0.033295 | 0.021664 | 5.7772e-05 | 0 | 1.7557 | 0 | 0.32235 | 0 | 5.9904e-05 | 0.055451 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 3.2342 | 0% | CZ 0A | 15.5148 | 1.0687 | 1.4313 | 0.0058951 | 0 | 56.353 | 0 | 10.3467 | 0 | 0.0019228 | 1.7799 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 107.7213 | 0% | CZ 0A | 4.5471 | 0.31321 | 0.10482 | 0 | 0 | 16.5161 | 0 | 3.0325 | 0 | 0.00056354 | 0.52165 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 29.8989 | 0% | CZ 0A | 0 | 0 | 0.010737 | 5.8951e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057063 | 0% | CZ 0A | 47.6039 | 3.279 | 2.2709 | 0.0064433 | 0 | 172.9073 | 0 | 31.7468 | 0 | 0.0058997 | 5.4611 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 319.2485 | 0%
CZ 0B | 0.48336 | 0.033303 | 0.021929 | 0.00053879 | 0 | 1.2464 | 0 | 0.27895 | 0 | 6.7891e-05 | 0.055147 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.682 | 0% | CZ 0B | 15.5148 | 1.0689 | 1.4581 | 0.054978 | 0 | 40.0062 | 0 | 8.9538 | 0 | 0.0021792 | 1.7701 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 90.0481 | 0% | CZ 0B | 4.5471 | 0.31329 | 0.10486 | 0 | 0 | 11.7251 | 0 | 2.6242 | 0 | 0.00063867 | 0.51879 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 24.697 | 0% | CZ 0B | 0 | 0 | 0.011003 | 0.00054978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057821 | 0% | CZ 0B | 47.6039 | 3.2798 | 2.3004 | 0.060091 | 0 | 122.7505 | 0 | 27.4727 | 0 | 0.0066863 | 5.4312 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 264.8724 | 0%
CZ 1A | 0.48336 | 0.033303 | 0.022499 | 0.0021891 | 0 | 0.9413 | 0 | 0.26212 | 0.06361 | 8.3865e-05 | 0.05488 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.4256 | 2.71% | CZ 1A | 15.5148 | 1.0689 | 1.5154 | 0.22337 | 0 | 30.2136 | 0 | 8.4135 | 2.0417 | 0.0026919 | 1.7615 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 81.9746 | 2.71% | CZ 1A | 4.5471 | 0.31329 | 0.10497 | 0 | 0 | 8.8551 | 0 | 2.4658 | 0.5984 | 0.00078895 | 0.51627 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 22.2647 | 2.71% | CZ 1A | 0 | 0 | 0.011572 | 0.0022337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.060074 | 2.71% | CZ 1A | 47.6039 | 3.2798 | 2.3638 | 0.24415 | 0 | 92.704 | 0 | 25.8149 | 6.2646 | 0.0082595 | 5.4049 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 239.6553 | 2.71%
CZ 1B | 0.48336 | 0.033263 | 0.022872 | 0.0069075 | 0 | 1.0335 | 0 | 0.2447 | 0 | 0.00015176 | 0.054908 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.4419 | 0% | CZ 1B | 15.5148 | 1.0677 | 1.5537 | 0.70485 | 0 | 33.1734 | 0 | 7.8544 | 0 | 0.004871 | 1.7624 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 82.8552 | 0% | CZ 1B | 4.5471 | 0.31291 | 0.10493 | 0 | 0 | 9.7226 | 0 | 2.302 | 0 | 0.0014276 | 0.51654 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 22.3704 | 0% | CZ 1B | 0 | 0 | 0.011957 | 0.0070485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.065273 | 0% | CZ 1B | 47.6039 | 3.2759 | 2.4054 | 0.7704 | 0 | 101.7855 | 0 | 24.0997 | 0 | 0.014946 | 5.4076 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 241.3304 | 0%
CZ 2A | 0.48336 | 0.033251 | 0.023606 | 0.013379 | 0 | 0.78427 | 0 | 0.23972 | 0.057428 | 0.00023562 | 0.054804 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.2523 | 20.22% | CZ 2A | 15.5148 | 1.0673 | 1.628 | 1.3652 | 0 | 25.1734 | 0 | 7.6943 | 1.8433 | 0.0075629 | 1.7591 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 77.2722 | 20.22% | CZ 2A | 4.5471 | 0.3128 | 0.10501 | 0 | 0 | 7.3779 | 0 | 2.2551 | 0.54024 | 0.0022166 | 0.51556 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 20.5189 | 20.22% | CZ 2A | 0 | 0 | 0.012698 | 0.013652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.072617 | 20.22% | CZ 2A | 47.6039 | 3.2747 | 2.4871 | 1.4922 | 0 | 77.2394 | 0 | 23.6084 | 5.6558 | 0.023205 | 5.3974 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 222.7492 | 20.22%
CZ 2B | 0.48336 | 0.033275 | 0.023764 | 0.0099833 | 0 | 0.49858 | 0 | 0.20143 | 0.036521 | 0.00021565 | 0.054273 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9037 | 2.485% | CZ 2B | 15.5148 | 1.068 | 1.6439 | 1.0187 | 0 | 16.0032 | 0 | 6.4655 | 1.1723 | 0.006922 | 1.742 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 65.8545 | 2.485% | CZ 2B | 4.5471 | 0.31303 | 0.10504 | 0 | 0 | 4.6903 | 0 | 1.8949 | 0.34357 | 0.0020287 | 0.51056 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 17.2695 | 2.485% | CZ 2B | 0 | 0 | 0.012855 | 0.010187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.06931 | 2.485% | CZ 2B | 47.6039 | 3.2771 | 2.5048 | 1.1134 | 0 | 49.1024 | 0 | 19.8382 | 3.5968 | 0.021239 | 5.3451 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 188.3699 | 2.485%
CZ 3A | 0.48336 | 0.033271 | 0.025287 | 0.059137 | 0 | 0.44205 | 0 | 0.21464 | 0.05004 | 0.00080271 | 0.054425 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9253 | 19.44% | CZ 3A | 15.5148 | 1.0679 | 1.799 | 6.0344 | 0 | 14.1889 | 0 | 6.8896 | 1.6062 | 0.025765 | 1.7469 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 70.0925 | 19.44% | CZ 3A | 4.5471 | 0.31299 | 0.10508 | 0 | 0 | 4.1585 | 0 | 2.0192 | 0.47074 | 0.0075514 | 0.51199 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 16.9961 | 19.44% | CZ 3A | 0 | 0 | 0.014405 | 0.060344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.12102 | 19.44% | CZ 3A | 47.6039 | 3.2767 | 2.6745 | 6.5956 | 0 | 43.5355 | 0 | 21.1392 | 4.9282 | 0.079055 | 5.36 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 191.1597 | 19.44%
CZ 3B | 0.48336 | 0.033267 | 0.024872 | 0.022957 | 0 | 0.34785 | 0 | 0.19136 | 0.036302 | 0.00051517 | 0.054093 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.7568 | 7.425% | CZ 3B | 15.5148 | 1.0678 | 1.7564 | 2.3425 | 0 | 11.1651 | 0 | 6.1424 | 1.1652 | 0.016536 | 1.7363 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 62.1261 | 7.425% | CZ 3B | 4.5471 | 0.31295 | 0.10512 | 0 | 0 | 3.2723 | 0 | 1.8002 | 0.3415 | 0.0048464 | 0.50887 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 15.7559 | 7.425% | CZ 3B | 0 | 0 | 0.013978 | 0.023425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.083671 | 7.425% | CZ 3B | 47.6039 | 3.2763 | 2.6283 | 2.5604 | 0 | 34.2577 | 0 | 18.8466 | 3.5752 | 0.050737 | 5.3274 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 174.0935 | 7.425%
CZ 3C | 0.48336 | 0.033263 | 0.025166 | 0.018825 | 0 | 0.31799 | 0 | 0.21444 | 0 | 0.00030751 | 0.054469 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.7101 | 0.9093% | CZ 3C | 15.5148 | 1.0677 | 1.7867 | 1.9209 | 0 | 10.2069 | 0 | 6.8829 | 0 | 0.0098703 | 1.7483 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 60.3571 | 0.9093% | CZ 3C | 4.5471 | 0.31291 | 0.10508 | 0 | 0 | 2.9915 | 0 | 2.0173 | 0 | 0.0028928 | 0.5124 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 15.3521 | 0.9093% | CZ 3C | 0 | 0 | 0.014282 | 0.019209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.079758 | 0.9093% | CZ 3C | 47.6039 | 3.2759 | 2.6611 | 2.0996 | 0 | 31.3177 | 0 | 21.1188 | 0 | 0.030285 | 5.3644 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 169.4386 | 0.9093%
CZ 4A | 0.48336 | 0.033219 | 0.026529 | 0.12885 | 0 | 0.30715 | 0 | 0.21823 | 0.048622 | 0.0016374 | 0.054297 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.8642 | 18.26% | CZ 4A | 15.5148 | 1.0662 | 1.9252 | 13.1479 | 0 | 9.859 | 0 | 7.0046 | 1.5607 | 0.052556 | 1.7428 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 73.0928 | 18.26% | CZ 4A | 4.5471 | 0.3125 | 0.10516 | 0 | 0 | 2.8895 | 0 | 2.0529 | 0.4574 | 0.015403 | 0.51079 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 15.7537 | 18.26% | CZ 4A | 0 | 0 | 0.015664 | 0.13148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19341 | 18.26% | CZ 4A | 47.6039 | 3.2716 | 2.813 | 14.3706 | 0 | 30.2503 | 0 | 21.492 | 4.7885 | 0.16126 | 5.3474 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 186.0657 | 18.26%
CZ 4B | 0.48336 | 0.033243 | 0.026152 | 0.043819 | 0 | 0.25983 | 0 | 0.19433 | 0.036046 | 0.0011022 | 0.053981 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.6941 | 0.672% | CZ 4B | 15.5148 | 1.067 | 1.8868 | 4.4713 | 0 | 8.3401 | 0 | 6.2376 | 1.157 | 0.035379 | 1.7327 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 61.6618 | 0.672% | CZ 4B | 4.5471 | 0.31272 | 0.10516 | 0 | 0 | 2.4444 | 0 | 1.8281 | 0.3391 | 0.010369 | 0.50782 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.9577 | 0.672% | CZ 4B | 0 | 0 | 0.01528 | 0.044713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.10626 | 0.672% | CZ 4B | 47.6039 | 3.2739 | 2.771 | 4.8871 | 0 | 25.5899 | 0 | 19.1389 | 3.55 | 0.10855 | 5.3164 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 168.2067 | 0.672%
CZ 4C | 0.48336 | 0.033179 | 0.026718 | 0.098781 | 0 | 0.12619 | 0 | 0.19858 | 0.036246 | 0.0013818 | 0.054125 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.6208 | 2.388% | CZ 4C | 15.5148 | 1.065 | 1.9442 | 10.0797 | 0 | 4.0504 | 0 | 6.374 | 1.1634 | 0.044352 | 1.7373 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 63.1923 | 2.388% | CZ 4C | 4.5471 | 0.31212 | 0.10519 | 0 | 0 | 1.1871 | 0 | 1.8681 | 0.34098 | 0.012999 | 0.50917 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 13.7458 | 2.388% | CZ 4C | 0 | 0 | 0.015853 | 0.1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16292 | 2.388% | CZ 4C | 47.6039 | 3.2676 | 2.834 | 11.0171 | 0 | 12.4278 | 0 | 19.5573 | 3.5697 | 0.13609 | 5.3305 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 161.7112 | 2.388%
CZ 5A | 0.48336 | 0.033227 | 0.027549 | 0.23426 | 0 | 0.18453 | 0 | 0.21652 | 0.029584 | 0.0029473 | 0.054153 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.8284 | 16% | CZ 5A | 15.5148 | 1.0665 | 2.029 | 23.9039 | 0 | 5.9229 | 0 | 6.9498 | 0.9496 | 0.094601 | 1.7382 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 79.3885 | 16% | CZ 5A | 4.5471 | 0.31257 | 0.10519 | 0 | 0 | 1.7359 | 0 | 2.0369 | 0.27831 | 0.027726 | 0.50944 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.4161 | 16% | CZ 5A | 0 | 0 | 0.016701 | 0.23904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.30201 | 16% | CZ 5A | 47.6039 | 3.2723 | 2.9267 | 26.1269 | 0 | 18.1733 | 0 | 21.3241 | 2.9136 | 0.29026 | 5.3333 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 183.9315 | 16%
CZ 5B | 0.48336 | 0.033231 | 0.02722 | 0.10306 | 0 | 0.20091 | 0 | 0.19118 | 0.036414 | 0.0021645 | 0.054029 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.6938 | 4.803% | CZ 5B | 15.5148 | 1.0666 | 1.9957 | 10.5163 | 0 | 6.4489 | 0 | 6.1365 | 1.1688 | 0.069477 | 1.7342 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 65.8704 | 4.803% | CZ 5B | 4.5471 | 0.31261 | 0.10516 | 0 | 0 | 1.8901 | 0 | 1.7985 | 0.34255 | 0.020362 | 0.50827 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.3876 | 4.803% | CZ 5B | 0 | 0 | 0.016369 | 0.10516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.1678 | 4.803% | CZ 5B | 47.6039 | 3.2727 | 2.89 | 11.4944 | 0 | 19.787 | 0 | 18.8285 | 3.5862 | 0.21317 | 5.3211 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 168.9641 | 4.803%
CZ 5C | 0.48336 | 0.033179 | 0.027264 | 0.10881 | 0 | 0.082711 | 0 | 0.1898 | 0.034616 | 0.0014257 | 0.054069 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.5775 | 0.03694% | CZ 5C | 15.5148 | 1.065 | 1.9997 | 11.1033 | 0 | 2.6548 | 0 | 6.0921 | 1.1111 | 0.045762 | 1.7355 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 62.5412 | 0.03694% | CZ 5C | 4.5471 | 0.31212 | 0.10523 | 0 | 0 | 0.77809 | 0 | 1.7855 | 0.32565 | 0.013412 | 0.50865 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 13.2387 | 0.03694% | CZ 5C | 0 | 0 | 0.016406 | 0.11103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.17371 | 0.03694% | CZ 5C | 47.6039 | 3.2676 | 2.8949 | 12.1359 | 0 | 8.1458 | 0 | 18.6925 | 3.4092 | 0.14041 | 5.325 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 157.5823 | 0.03694%
CZ 6A | 0.48336 | 0.033215 | 0.028387 | 0.29748 | 0 | 0.19524 | 0 | 0.22755 | 0.036485 | 0.0045766 | 0.054061 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9226 | 3.249% | CZ 6A | 15.5148 | 1.0661 | 2.114 | 30.3549 | 0 | 6.2667 | 0 | 7.304 | 1.1711 | 0.1469 | 1.7352 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 86.8929 | 3.249% | CZ 6A | 4.5471 | 0.31246 | 0.10527 | 0 | 0 | 1.8367 | 0 | 2.1407 | 0.34323 | 0.043054 | 0.50857 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.7 | 3.249% | CZ 6A | 0 | 0 | 0.017548 | 0.30355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.36736 | 3.249% | CZ 6A | 47.6039 | 3.2712 | 3.0201 | 33.1779 | 0 | 19.2281 | 0 | 22.4108 | 3.5933 | 0.45073 | 5.3242 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 194.0473 | 3.249%
CZ 6B | 0.48336 | 0.033191 | 0.028141 | 0.19737 | 0 | 0.13696 | 0 | 0.1915 | 0.036414 | 0.0035303 | 0.053929 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.7267 | 0.979% | CZ 6B | 15.5148 | 1.0653 | 2.0891 | 20.14 | 0 | 4.3961 | 0 | 6.1466 | 1.1688 | 0.11332 | 1.731 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 73.5842 | 0.979% | CZ 6B | 4.5471 | 0.31224 | 0.10523 | 0 | 0 | 1.2884 | 0 | 1.8015 | 0.34255 | 0.033211 | 0.50733 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 13.8005 | 0.979% | CZ 6B | 0 | 0 | 0.017301 | 0.2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.26497 | 0.979% | CZ 6B | 47.6039 | 3.2688 | 2.9926 | 22.013 | 0 | 13.4886 | 0 | 18.8596 | 3.5862 | 0.34769 | 5.3113 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 173.4387 | 0.979%
CZ 7 | 0.48336 | 0.033167 | 0.029283 | 0.3537 | 0 | 0.15987 | 0 | 0.2264 | 0.036525 | 0.0053274 | 0.053989 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9439 | 0.3956% | CZ 7 | 15.5148 | 1.0646 | 2.2051 | 36.0917 | 0 | 5.1315 | 0 | 7.2671 | 1.1724 | 0.171 | 1.7329 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 91.5703 | 0.3956% | CZ 7 | 4.5471 | 0.31201 | 0.10531 | 0 | 0 | 1.504 | 0 | 2.1299 | 0.34361 | 0.050117 | 0.5079 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.3628 | 0.3956% | CZ 7 | 0 | 0 | 0.018458 | 0.36092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.42564 | 0.3956% | CZ 7 | 47.6039 | 3.2664 | 3.1199 | 39.4483 | 0 | 15.745 | 0 | 22.2975 | 3.5972 | 0.52468 | 5.3172 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 196.8872 | 0.3956%
CZ 8 | 0.48336 | 0.032987 | 0.030401 | 0.58612 | 0 | 0.082883 | 0 | 0.22536 | 0.036465 | 0.0082308 | 0.053746 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.1018 | 0.02728% | CZ 8 | 15.5148 | 1.0588 | 2.3184 | 59.808 | 0 | 2.6604 | 0 | 7.2336 | 1.1705 | 0.26419 | 1.7251 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 112.9729 | 0.02728% | CZ 8 | 4.5471 | 0.31032 | 0.10542 | 0 | 0 | 0.77971 | 0 | 2.1201 | 0.34304 | 0.07743 | 0.5056 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 13.6516 | 0.02728% | CZ 8 | 0 | 0 | 0.019587 | 0.59808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.66393 | 0.02728% | CZ 8 | 47.6039 | 3.2487 | 3.2445 | 65.3701 | 0 | 8.1628 | 0 | 22.1949 | 3.5913 | 0.81061 | 5.2932 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 215.4871 | 0.02728%
US Weighted | 0.48336 | 0.033243 | 0.02567 | 0.098193 | 0 | 0.41951 | 0 | 0.21848 | 0.044844 | 0.0013744 | 0.054371 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9413 | 100% | US Weighted | 15.5148 | 1.067 | 1.8379 | 10.0197 | 0 | 13.4655 | 0 | 7.0128 | 1.4394 | 0.044114 | 1.7452 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 73.3654 | 100% | US Weighted | 4.5471 | 0.31273 | 0.10511 | 0 | 0 | 3.9465 | 0 | 2.0553 | 0.42187 | 0.012929 | 0.51149 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 16.776 | 100% | US Weighted | 0 | 0 | 0.014792 | 0.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.16126 | 100% | US Weighted | 47.6039 | 3.274 | 2.7172 | 10.9515 | 0 | 41.316 | 0 | 21.5172 | 4.4165 | 0.13536 | 5.3548 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 193.2535 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 73959 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.48336 | 0.033295 | 0.021664 | 4.3957e-05 | 0 | 1.8288 | 0 | 0.38151 | 0.018794 | 5.9904e-05 | 0.055455 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 3.3853 | 0% | CZ 0A | 15.5148 | 1.0687 | 1.4313 | 0.0044854 | 0 | 58.7019 | 0 | 12.2456 | 0.60324 | 0.0019228 | 1.78 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 112.571 | 0% | CZ 0A | 4.5471 | 0.31321 | 0.10482 | 0 | 0 | 17.2045 | 0 | 3.589 | 0.1768 | 0.00056354 | 0.52168 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 31.3206 | 0% | CZ 0A | 0 | 0 | 0.010737 | 4.4854e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057049 | 0% | CZ 0A | 47.6039 | 3.279 | 2.2709 | 0.0049025 | 0 | 180.1143 | 0 | 37.5729 | 1.8509 | 0.0058997 | 5.4615 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 334.1313 | 0%
CZ 0B | 0.48336 | 0.033303 | 0.021929 | 0.00064931 | 0 | 1.3071 | 0 | 0.33043 | 0.018107 | 6.7891e-05 | 0.055147 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.8124 | 0% | CZ 0B | 15.5148 | 1.0689 | 1.4581 | 0.066256 | 0 | 41.956 | 0 | 10.6059 | 0.58119 | 0.0021792 | 1.7701 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 94.2426 | 0% | CZ 0B | 4.5471 | 0.31329 | 0.10486 | 0 | 0 | 12.2966 | 0 | 3.1084 | 0.17034 | 0.00063867 | 0.51879 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 25.923 | 0% | CZ 0B | 0 | 0 | 0.011003 | 0.00066256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.057933 | 0% | CZ 0B | 47.6039 | 3.2798 | 2.3004 | 0.072418 | 0 | 128.7331 | 0 | 32.5421 | 1.7833 | 0.0066863 | 5.4312 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 277.72 | 0%
CZ 1A | 0.48336 | 0.033303 | 0.022499 | 0.0026035 | 0 | 0.99732 | 0 | 0.30997 | 0.080982 | 8.7859e-05 | 0.05488 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.5473 | 2.71% | CZ 1A | 15.5148 | 1.0689 | 1.5154 | 0.26566 | 0 | 32.0119 | 0 | 9.9492 | 2.5993 | 0.0028201 | 1.7615 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 85.9087 | 2.71% | CZ 1A | 4.5471 | 0.31329 | 0.10497 | 0 | 0 | 9.3821 | 0 | 2.916 | 0.76182 | 0.00082652 | 0.51627 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 23.4053 | 2.71% | CZ 1A | 0 | 0 | 0.011572 | 0.0026566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.060497 | 2.71% | CZ 1A | 47.6039 | 3.2798 | 2.3638 | 0.29037 | 0 | 98.2217 | 0 | 30.5271 | 7.9755 | 0.0086528 | 5.4049 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 251.6428 | 2.71%
CZ 1B | 0.48336 | 0.033263 | 0.022876 | 0.0079411 | 0 | 1.0708 | 0 | 0.27948 | 0.016785 | 0.00015974 | 0.054912 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.5319 | 0% | CZ 1B | 15.5148 | 1.0677 | 1.5541 | 0.81032 | 0 | 34.3717 | 0 | 8.9707 | 0.53876 | 0.0051274 | 1.7626 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 85.8147 | 0% | CZ 1B | 4.5471 | 0.31291 | 0.10493 | 0 | 0 | 10.0738 | 0 | 2.6292 | 0.1579 | 0.0015028 | 0.51657 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 23.2068 | 0% | CZ 1B | 0 | 0 | 0.011961 | 0.0081032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.066331 | 0% | CZ 1B | 47.6039 | 3.2759 | 2.4058 | 0.88568 | 0 | 105.4621 | 0 | 27.5246 | 1.6531 | 0.015732 | 5.408 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 250.2019 | 0%
CZ 2A | 0.48336 | 0.033251 | 0.023613 | 0.019832 | 0 | 0.84223 | 0 | 0.25906 | 0.073953 | 0.0003115 | 0.054816 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.3527 | 20.22% | CZ 2A | 15.5148 | 1.0673 | 1.6288 | 2.0237 | 0 | 27.0337 | 0 | 8.3153 | 2.3737 | 0.0099985 | 1.7595 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 80.9458 | 20.22% | CZ 2A | 4.5471 | 0.3128 | 0.10501 | 0 | 0 | 7.9231 | 0 | 2.4371 | 0.6957 | 0.0029304 | 0.51567 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 21.4024 | 20.22% | CZ 2A | 0 | 0 | 0.012705 | 0.020237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.07921 | 20.22% | CZ 2A | 47.6039 | 3.2747 | 2.488 | 2.2119 | 0 | 82.9471 | 0 | 25.5136 | 7.2833 | 0.030678 | 5.3986 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 232.7189 | 20.22%
CZ 2B | 0.48336 | 0.033275 | 0.023774 | 0.016091 | 0 | 0.59667 | 0 | 0.22814 | 0.0090175 | 0.00027556 | 0.054281 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.0072 | 2.485% | CZ 2B | 15.5148 | 1.068 | 1.6449 | 1.6419 | 0 | 19.1517 | 0 | 7.3229 | 0.28944 | 0.0088448 | 1.7423 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 69.6039 | 2.485% | CZ 2B | 4.5471 | 0.31303 | 0.10504 | 0 | 0 | 5.613 | 0 | 2.1462 | 0.084831 | 0.0025923 | 0.51064 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 18.1854 | 2.485% | CZ 2B | 0 | 0 | 0.012865 | 0.016419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.075552 | 2.485% | CZ 2B | 47.6039 | 3.2771 | 2.5059 | 1.7946 | 0 | 58.7629 | 0 | 22.4686 | 0.88809 | 0.027138 | 5.3459 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 198.6411 | 2.485%
CZ 3A | 0.48336 | 0.033271 | 0.025303 | 0.081089 | 0 | 0.46951 | 0 | 0.23983 | 0.06583 | 0.0010743 | 0.054437 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.016 | 19.44% | CZ 3A | 15.5148 | 1.0679 | 1.8004 | 8.2744 | 0 | 15.0704 | 0 | 7.6979 | 2.113 | 0.034482 | 1.7473 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 74.5397 | 19.44% | CZ 3A | 4.5471 | 0.31299 | 0.10512 | 0 | 0 | 4.4169 | 0 | 2.2561 | 0.61929 | 0.010106 | 0.5121 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 17.6427 | 19.44% | CZ 3A | 0 | 0 | 0.014417 | 0.082744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.14343 | 19.44% | CZ 3A | 47.6039 | 3.2767 | 2.6763 | 9.0439 | 0 | 46.2403 | 0 | 23.6194 | 6.4833 | 0.1058 | 5.3612 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 200.3779 | 19.44%
CZ 3B | 0.48336 | 0.033267 | 0.024887 | 0.033346 | 0 | 0.37345 | 0 | 0.21632 | 0.046489 | 0.00065495 | 0.054105 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.8282 | 7.425% | CZ 3B | 15.5148 | 1.0678 | 1.758 | 3.4026 | 0 | 11.987 | 0 | 6.9434 | 1.4922 | 0.021022 | 1.7367 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 65.1426 | 7.425% | CZ 3B | 4.5471 | 0.31295 | 0.10512 | 0 | 0 | 3.5132 | 0 | 2.035 | 0.43734 | 0.0061613 | 0.50898 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 16.3288 | 7.425% | CZ 3B | 0 | 0 | 0.013993 | 0.034026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.094287 | 7.425% | CZ 3B | 47.6039 | 3.2763 | 2.6299 | 3.7191 | 0 | 36.7796 | 0 | 21.3044 | 4.5785 | 0.064503 | 5.3286 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 181.2519 | 7.425%
CZ 3C | 0.48336 | 0.033263 | 0.025179 | 0.037351 | 0 | 0.33801 | 0 | 0.22248 | 0 | 0.00048322 | 0.054469 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.7569 | 0.9093% | CZ 3C | 15.5148 | 1.0677 | 1.788 | 3.8113 | 0 | 10.8495 | 0 | 7.1411 | 0 | 0.01551 | 1.7483 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 63.1552 | 0.9093% | CZ 3C | 4.5471 | 0.31291 | 0.10508 | 0 | 0 | 3.1798 | 0 | 2.0929 | 0 | 0.0045459 | 0.5124 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 15.6177 | 0.9093% | CZ 3C | 0 | 0 | 0.014294 | 0.038113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.098675 | 0.9093% | CZ 3C | 47.6039 | 3.2759 | 2.6625 | 4.1658 | 0 | 33.2894 | 0 | 21.9109 | 0 | 0.047591 | 5.3644 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 174.2873 | 0.9093%
CZ 4A | 0.48336 | 0.033219 | 0.026557 | 0.18862 | 0 | 0.32137 | 0 | 0.24496 | 0.065151 | 0.0023562 | 0.054309 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9822 | 18.26% | CZ 4A | 15.5148 | 1.0662 | 1.9278 | 19.2466 | 0 | 10.3152 | 0 | 7.8628 | 2.0912 | 0.075629 | 1.7432 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 81.0626 | 18.26% | CZ 4A | 4.5471 | 0.3125 | 0.10519 | 0 | 0 | 3.0232 | 0 | 2.3044 | 0.6129 | 0.022166 | 0.5109 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 16.3014 | 18.26% | CZ 4A | 0 | 0 | 0.015689 | 0.19247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.25442 | 18.26% | CZ 4A | 47.6039 | 3.2716 | 2.816 | 21.0365 | 0 | 31.65 | 0 | 24.1252 | 6.4165 | 0.23205 | 5.3486 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 198.4675 | 18.26%
CZ 4B | 0.48336 | 0.033243 | 0.026172 | 0.07152 | 0 | 0.27174 | 0 | 0.21267 | 0.046445 | 0.0014057 | 0.054009 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.7628 | 0.672% | CZ 4B | 15.5148 | 1.067 | 1.8888 | 7.298 | 0 | 8.7221 | 0 | 6.8263 | 1.4908 | 0.045121 | 1.7336 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 65.8056 | 0.672% | CZ 4B | 4.5471 | 0.31272 | 0.10516 | 0 | 0 | 2.5563 | 0 | 2.0007 | 0.43693 | 0.013224 | 0.50808 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 15.3431 | 0.672% | CZ 4B | 0 | 0 | 0.0153 | 0.07298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.13455 | 0.672% | CZ 4B | 47.6039 | 3.2739 | 2.7732 | 7.9767 | 0 | 26.762 | 0 | 20.9449 | 4.5742 | 0.13845 | 5.3191 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 175.3335 | 0.672%
CZ 4C | 0.48336 | 0.033179 | 0.026742 | 0.14434 | 0 | 0.12784 | 0 | 0.22478 | 0.04744 | 0.0021446 | 0.054169 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.7063 | 2.388% | CZ 4C | 15.5148 | 1.065 | 1.9464 | 14.7289 | 0 | 4.1035 | 0 | 7.215 | 1.5227 | 0.068836 | 1.7387 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 69.1229 | 2.388% | CZ 4C | 4.5471 | 0.31212 | 0.10523 | 0 | 0 | 1.2027 | 0 | 2.1146 | 0.44628 | 0.020175 | 0.50959 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.1207 | 2.388% | CZ 4C | 0 | 0 | 0.015873 | 0.14729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.20943 | 2.388% | CZ 4C | 47.6039 | 3.2676 | 2.8366 | 16.0987 | 0 | 12.5906 | 0 | 22.1378 | 4.6721 | 0.21121 | 5.3349 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 170.7206 | 2.388%
CZ 5A | 0.48336 | 0.033227 | 0.027576 | 0.26092 | 0 | 0.18962 | 0 | 0.26207 | 0.046557 | 0.0035822 | 0.054129 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.9233 | 16% | CZ 5A | 15.5148 | 1.0665 | 2.0315 | 26.625 | 0 | 6.0865 | 0 | 8.4119 | 1.4944 | 0.11498 | 1.7374 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 84.302 | 16% | CZ 5A | 4.5471 | 0.31257 | 0.10523 | 0 | 0 | 1.7839 | 0 | 2.4654 | 0.43798 | 0.033699 | 0.50921 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 15.058 | 16% | CZ 5A | 0 | 0 | 0.016724 | 0.26625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.32924 | 16% | CZ 5A | 47.6039 | 3.2723 | 2.9296 | 29.1011 | 0 | 18.6751 | 0 | 25.8102 | 4.5852 | 0.3528 | 5.3309 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 193.6283 | 16%
CZ 5B | 0.48336 | 0.033231 | 0.027245 | 0.14841 | 0 | 0.20378 | 0 | 0.21471 | 0.046533 | 0.0026677 | 0.054041 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.7762 | 4.803% | CZ 5B | 15.5148 | 1.0666 | 1.998 | 15.1437 | 0 | 6.5408 | 0 | 6.8916 | 1.4936 | 0.085628 | 1.7346 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 71.6886 | 4.803% | CZ 5B | 4.5471 | 0.31261 | 0.10519 | 0 | 0 | 1.917 | 0 | 2.0198 | 0.43775 | 0.025096 | 0.50838 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.7359 | 4.803% | CZ 5B | 0 | 0 | 0.016391 | 0.15144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.2141 | 4.803% | CZ 5B | 47.6039 | 3.2727 | 2.8928 | 16.5521 | 0 | 20.069 | 0 | 21.1455 | 4.5828 | 0.26273 | 5.3223 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 177.671 | 4.803%
CZ 5C | 0.48336 | 0.033179 | 0.027284 | 0.16116 | 0 | 0.083142 | 0 | 0.22694 | 0.046933 | 0.0020407 | 0.054129 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.6804 | 0.03694% | CZ 5C | 15.5148 | 1.065 | 2.0017 | 16.4446 | 0 | 2.6687 | 0 | 7.2843 | 1.5064 | 0.065503 | 1.7374 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 69.5076 | 0.03694% | CZ 5C | 4.5471 | 0.31212 | 0.10523 | 0 | 0 | 0.78215 | 0 | 2.1349 | 0.44151 | 0.019198 | 0.50921 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 13.7144 | 0.03694% | CZ 5C | 0 | 0 | 0.016427 | 0.16445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.22714 | 0.03694% | CZ 5C | 47.6039 | 3.2676 | 2.8971 | 17.974 | 0 | 8.1883 | 0 | 22.3502 | 4.6222 | 0.20098 | 5.3309 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 168.4023 | 0.03694%
CZ 6A | 0.48336 | 0.033215 | 0.028417 | 0.39175 | 0 | 0.19596 | 0 | 0.26737 | 0.046921 | 0.0055631 | 0.053973 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.0688 | 3.249% | CZ 6A | 15.5148 | 1.0661 | 2.1164 | 39.9743 | 0 | 6.2899 | 0 | 8.582 | 1.5061 | 0.17856 | 1.7324 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 98.1797 | 3.249% | CZ 6A | 4.5471 | 0.31246 | 0.10534 | 0 | 0 | 1.8435 | 0 | 2.5152 | 0.4414 | 0.052334 | 0.50775 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 15.1881 | 3.249% | CZ 6A | 0 | 0 | 0.01757 | 0.39974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.46358 | 3.249% | CZ 6A | 47.6039 | 3.2712 | 3.0232 | 43.6919 | 0 | 19.2993 | 0 | 26.3321 | 4.621 | 0.54788 | 5.3156 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 209.6732 | 3.249%
CZ 6B | 0.48336 | 0.033191 | 0.028171 | 0.27747 | 0 | 0.1337 | 0 | 0.22343 | 0.046741 | 0.0044249 | 0.053897 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 1.8467 | 0.979% | CZ 6B | 15.5148 | 1.0653 | 2.092 | 28.313 | 0 | 4.2915 | 0 | 7.1716 | 1.5003 | 0.14203 | 1.73 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 83.0396 | 0.979% | CZ 6B | 4.5471 | 0.31224 | 0.10527 | 0 | 0 | 1.2578 | 0 | 2.1019 | 0.43971 | 0.041626 | 0.50703 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.1756 | 0.979% | CZ 6B | 0 | 0 | 0.017328 | 0.28313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.34673 | 0.979% | CZ 6B | 47.6039 | 3.2688 | 2.996 | 30.9461 | 0 | 13.1676 | 0 | 22.0045 | 4.6033 | 0.43579 | 5.3081 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 186.3012 | 0.979%
CZ 7 | 0.48336 | 0.033167 | 0.029315 | 0.47399 | 0 | 0.15849 | 0 | 0.25946 | 0.046833 | 0.006825 | 0.053865 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.1076 | 0.3956% | CZ 7 | 15.5148 | 1.0646 | 2.2078 | 48.366 | 0 | 5.087 | 0 | 8.328 | 1.5032 | 0.21907 | 1.729 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 105.2385 | 0.3956% | CZ 7 | 4.5471 | 0.31201 | 0.10538 | 0 | 0 | 1.4909 | 0 | 2.4408 | 0.44057 | 0.064205 | 0.50673 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.7707 | 0.3956% | CZ 7 | 0 | 0 | 0.018482 | 0.48366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.54841 | 0.3956% | CZ 7 | 47.6039 | 3.2664 | 3.1234 | 52.864 | 0 | 15.6085 | 0 | 25.5526 | 4.6123 | 0.67217 | 5.305 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 214.5753 | 0.3956%
CZ 8 | 0.48336 | 0.032987 | 0.030409 | 0.66669 | 0 | 0.081641 | 0 | 0.27784 | 0.046989 | 0.0087899 | 0.053726 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.2447 | 0.02728% | CZ 8 | 15.5148 | 1.0588 | 2.3192 | 68.0291 | 0 | 2.6205 | 0 | 8.918 | 1.5082 | 0.28214 | 1.7245 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 123.1943 | 0.02728% | CZ 8 | 4.5471 | 0.31032 | 0.10542 | 0 | 0 | 0.76802 | 0 | 2.6137 | 0.44204 | 0.082689 | 0.50542 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 14.2377 | 0.02728% | CZ 8 | 0 | 0 | 0.019595 | 0.68029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.74615 | 0.02728% | CZ 8 | 47.6039 | 3.2487 | 3.2453 | 74.3558 | 0 | 8.0404 | 0 | 27.363 | 4.6277 | 0.86568 | 5.2912 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 230.6088 | 0.02728%
US Weighted | 0.48336 | 0.033243 | 0.025689 | 0.12787 | 0 | 0.44626 | 0 | 0.24699 | 0.058845 | 0.0017805 | 0.054373 | 0 | 0.019181 | 0.10513 | 0 | 0.43796 | 2.0407 | 100% | US Weighted | 15.5148 | 1.067 | 1.8396 | 13.0476 | 0 | 14.3241 | 0 | 7.9278 | 1.8888 | 0.05715 | 1.7453 | 0 | 0.61567 | 6.5458 | 0 | 14.0576 | 78.6312 | 100% | US Weighted | 4.5471 | 0.31273 | 0.10514 | 0 | 0 | 4.1981 | 0 | 2.3235 | 0.55357 | 0.01675 | 0.51151 | 0 | 0.18044 | 0.56245 | 0 | 4.12 | 17.4314 | 100% | US Weighted | 0 | 0 | 0.014809 | 0.13048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046268 | 0 | 0 | 0.19155 | 100% | US Weighted | 47.6039 | 3.274 | 2.7193 | 14.2611 | 0 | 43.9504 | 0 | 24.3247 | 5.7953 | 0.17535 | 5.355 | 0 | 1.8891 | 10.9453 | 0 | 43.1327 | 203.4261 | 100%
Building Type: | Primary School |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Primary School |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 73959 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 73959 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 73959 | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.37039 | 0.023135 | 0.0010075 | -0.00067819 | 0 | 1.1323 | 0 | 0.21656 | -0.024537 | -7.9872e-06 | 0.02627 | 0 | 0.012364 | 0 | 0 | 0.059552 | 1.8164 | 0% | CZ 0A | 11.8886 | 0.74258 | 0.044989 | -0.069203 | 0 | 36.3444 | 0 | 6.9512 | -0.78757 | -0.00025637 | 0.8432 | 0 | 0.39686 | 0 | 0 | 1.9115 | 58.2663 | 0% | CZ 0A | 3.4843 | 0.21764 | 0.0077768 | 0 | 0 | 10.6519 | 0 | 2.0373 | -0.23082 | -7.5138e-05 | 0.24713 | 0 | 0.11631 | 0 | 0 | 0.56023 | 17.0918 | 0% | CZ 0A | 0 | 0 | 0.00018454 | -0.00069203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00050749 | 0% | CZ 0A | 36.4775 | 2.2784 | 0.10159 | -0.075639 | 0 | 111.5152 | 0 | 21.3284 | -2.4165 | -0.00078662 | 2.5872 | 0 | 1.2177 | 0 | 0 | 5.865 | 178.8782 | 0%
CZ 0B | 0.37098 | 0.023087 | 0.0010203 | 0.00037803 | 0 | 0.68888 | 0 | 0.14847 | -0.021705 | 3.9936e-06 | 0.02605 | 0 | 0.012364 | 0 | 0 | 0.059552 | 1.3091 | 0% | CZ 0B | 11.9078 | 0.74104 | 0.046014 | 0.038574 | 0 | 22.1115 | 0 | 4.7654 | -0.69669 | 0.00012819 | 0.83615 | 0 | 0.39686 | 0 | 0 | 1.9115 | 42.0583 | 0% | CZ 0B | 3.49 | 0.21719 | 0.0078144 | 0 | 0 | 6.4805 | 0 | 1.3967 | -0.20419 | 3.7569e-05 | 0.24506 | 0 | 0.11631 | 0 | 0 | 0.56023 | 12.3096 | 0% | CZ 0B | 0 | 0 | 0.00019351 | 0.00038574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00057926 | 0% | CZ 0B | 36.5365 | 2.2737 | 0.10296 | 0.042162 | 0 | 67.8444 | 0 | 14.6217 | -2.1376 | 0.00039331 | 2.5656 | 0 | 1.2177 | 0 | 0 | 5.865 | 128.9325 | 0%
CZ 1A | 0.36812 | 0.023063 | 0.0010298 | 0.0025847 | 0 | 0.5543 | 0 | 0.16096 | 0.03839 | 2.7955e-05 | 0.025831 | 0 | 0.012364 | 0 | 0 | 0.059552 | 1.2462 | 2.71% | CZ 1A | 11.8158 | 0.74027 | 0.046142 | 0.26374 | 0 | 17.7918 | 0 | 5.1664 | 1.2322 | 0.0008973 | 0.8291 | 0 | 0.39686 | 0 | 0 | 1.9115 | 40.1947 | 2.71% | CZ 1A | 3.463 | 0.21696 | 0.0079271 | 0 | 0 | 5.2145 | 0 | 1.5142 | 0.36115 | 0.00026298 | 0.243 | 0 | 0.11631 | 0 | 0 | 0.56023 | 11.6975 | 2.71% | CZ 1A | 0 | 0 | 0.00019095 | 0.0026374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028284 | 2.71% | CZ 1A | 36.2541 | 2.2714 | 0.10386 | 0.28827 | 0 | 54.5902 | 0 | 15.852 | 3.7809 | 0.0027532 | 2.5439 | 0 | 1.2177 | 0 | 0 | 5.865 | 122.7701 | 2.71%
CZ 1B | 0.36931 | 0.023055 | 0.0010258 | 0.0020082 | 0 | 0.55401 | 0 | 0.11713 | -0.020068 | 2.3962e-05 | 0.025886 | 0 | 0.012364 | 0 | 0 | 0.059552 | 1.1443 | 0% | CZ 1B | 11.8542 | 0.74001 | 0.046014 | 0.20492 | 0 | 17.7827 | 0 | 3.7597 | -0.64413 | 0.00076911 | 0.8309 | 0 | 0.39686 | 0 | 0 | 1.9115 | 36.8834 | 0% | CZ 1B | 3.4743 | 0.21689 | 0.0078895 | 0 | 0 | 5.2118 | 0 | 1.1019 | -0.18878 | 0.00022541 | 0.24352 | 0 | 0.11631 | 0 | 0 | 0.56023 | 10.7442 | 0% | CZ 1B | 0 | 0 | 0.00019095 | 0.0020492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022401 | 0% | CZ 1B | 36.3721 | 2.2706 | 0.10347 | 0.22398 | 0 | 54.5623 | 0 | 11.5358 | -1.9764 | 0.0023599 | 2.5494 | 0 | 1.2177 | 0 | 0 | 5.865 | 112.7264 | 0%
CZ 2A | 0.36999 | 0.023031 | 0.0010375 | 0.015801 | 0 | 0.4735 | 0 | 0.11773 | 0.038191 | 0.00017172 | 0.025795 | 0 | 0.012364 | 0 | 0 | 0.059552 | 1.1372 | 20.22% | CZ 2A | 11.8757 | 0.73925 | 0.046655 | 1.6123 | 0 | 15.1982 | 0 | 3.7789 | 1.2258 | 0.005512 | 0.82795 | 0 | 0.39686 | 0 | 0 | 1.9115 | 37.6187 | 20.22% | CZ 2A | 3.4806 | 0.21666 | 0.0079646 | 0 | 0 | 4.4543 | 0 | 1.1075 | 0.35927 | 0.0016155 | 0.24266 | 0 | 0.11631 | 0 | 0 | 0.56023 | 10.5472 | 20.22% | CZ 2A | 0 | 0 | 0.00019479 | 0.016123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016318 | 20.22% | CZ 2A | 36.4382 | 2.2682 | 0.10467 | 1.7623 | 0 | 46.6324 | 0 | 11.5948 | 3.7612 | 0.016912 | 2.5404 | 0 | 1.2177 | 0 | 0 | 5.865 | 112.2018 | 20.22%
CZ 2B | 0.36808 | 0.023051 | 0.001025 | 0.012469 | 0 | 0.3044 | 0 | 0.089892 | -0.013886 | 0.00014377 | 0.025491 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.88258 | 2.485% | CZ 2B | 11.8146 | 0.73989 | 0.045373 | 1.2723 | 0 | 9.7707 | 0 | 2.8853 | -0.4457 | 0.0046147 | 0.81821 | 0 | 0.39673 | 0 | 0 | 1.9115 | 29.2135 | 2.485% | CZ 2B | 3.4627 | 0.21685 | 0.0079646 | 0 | 0 | 2.8636 | 0 | 0.84564 | -0.13063 | 0.0013525 | 0.2398 | 0 | 0.11628 | 0 | 0 | 0.56023 | 8.1838 | 2.485% | CZ 2B | 0 | 0 | 0.00018198 | 0.012723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012905 | 2.485% | CZ 2B | 36.2506 | 2.2702 | 0.10327 | 1.3906 | 0 | 29.9793 | 0 | 8.853 | -1.3675 | 0.014159 | 2.5105 | 0 | 1.2173 | 0 | 0 | 5.865 | 87.0864 | 2.485%
CZ 3A | 0.36876 | 0.023019 | 0.0010279 | 0.05283 | 0 | 0.26057 | 0 | 0.12321 | 0.030323 | 0.00049121 | 0.025519 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.95767 | 19.44% | CZ 3A | 11.8364 | 0.73886 | 0.045117 | 5.3908 | 0 | 8.3638 | 0 | 3.9548 | 0.97331 | 0.015767 | 0.81911 | 0 | 0.39673 | 0 | 0 | 1.9115 | 34.4462 | 19.44% | CZ 3A | 3.469 | 0.21655 | 0.0080398 | 0 | 0 | 2.4513 | 0 | 1.1591 | 0.28526 | 0.004621 | 0.24007 | 0 | 0.11628 | 0 | 0 | 0.56023 | 8.5105 | 19.44% | CZ 3A | 0 | 0 | 0.00017685 | 0.053908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054085 | 19.44% | CZ 3A | 36.3175 | 2.267 | 0.1035 | 5.8922 | 0 | 25.6627 | 0 | 12.1344 | 2.9864 | 0.048377 | 2.5133 | 0 | 1.2173 | 0 | 0 | 5.865 | 95.0076 | 19.44%
CZ 3B | 0.36726 | 0.023079 | 0.001033 | 0.015856 | 0 | 0.15895 | 0 | 0.090375 | 0.046489 | 0.0003115 | 0.025327 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.80059 | 7.425% | CZ 3B | 11.7882 | 0.74078 | 0.04563 | 1.6179 | 0 | 5.1019 | 0 | 2.9008 | 1.4922 | 0.0099985 | 0.81295 | 0 | 0.39673 | 0 | 0 | 1.9115 | 26.8187 | 7.425% | CZ 3B | 3.4549 | 0.21711 | 0.0080398 | 0 | 0 | 1.4953 | 0 | 0.85019 | 0.43734 | 0.0029304 | 0.23826 | 0 | 0.11628 | 0 | 0 | 0.56023 | 7.3806 | 7.425% | CZ 3B | 0 | 0 | 0.00018198 | 0.016179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016361 | 7.425% | CZ 3B | 36.1696 | 2.2729 | 0.10406 | 1.7684 | 0 | 15.6541 | 0 | 8.9006 | 4.5785 | 0.030678 | 2.4944 | 0 | 1.2173 | 0 | 0 | 5.865 | 79.0556 | 7.425%
CZ 3C | 0.36675 | 0.023067 | 0.0010315 | 0.03141 | 0 | 0.19531 | 0 | 0.11671 | 0 | 0.00032348 | 0.025575 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.83209 | 0.9093% | CZ 3C | 11.7718 | 0.7404 | 0.045758 | 3.2051 | 0 | 6.2692 | 0 | 3.7461 | 0 | 0.010383 | 0.8209 | 0 | 0.39673 | 0 | 0 | 1.9115 | 28.9179 | 0.9093% | CZ 3C | 3.4501 | 0.217 | 0.0080022 | 0 | 0 | 1.8374 | 0 | 1.0979 | 0 | 0.0030431 | 0.24059 | 0 | 0.11628 | 0 | 0 | 0.56023 | 7.5306 | 0.9093% | CZ 3C | 0 | 0 | 0.00018454 | 0.032051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032236 | 0.9093% | CZ 3C | 36.1192 | 2.2718 | 0.10395 | 3.5032 | 0 | 19.2356 | 0 | 11.4941 | 0 | 0.031858 | 2.5188 | 0 | 1.2173 | 0 | 0 | 5.865 | 82.3608 | 0.9093%
CZ 4A | 0.36801 | 0.022975 | 0.001056 | 0.15012 | 0 | 0.17573 | 0 | 0.13051 | 0.036358 | 0.0013458 | 0.025403 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.98343 | 18.26% | CZ 4A | 11.8123 | 0.73745 | 0.047424 | 15.3187 | 0 | 5.6407 | 0 | 4.1892 | 1.167 | 0.043199 | 0.81539 | 0 | 0.39673 | 0 | 0 | 1.9115 | 42.0796 | 18.26% | CZ 4A | 3.462 | 0.21613 | 0.0081149 | 0 | 0 | 1.6532 | 0 | 1.2278 | 0.34203 | 0.012661 | 0.23898 | 0 | 0.11628 | 0 | 0 | 0.56023 | 7.8374 | 18.26% | CZ 4A | 0 | 0 | 0.00019736 | 0.15319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15338 | 18.26% | CZ 4A | 36.2435 | 2.2627 | 0.10653 | 16.7433 | 0 | 17.3072 | 0 | 12.8538 | 3.5807 | 0.13255 | 2.5018 | 0 | 1.2173 | 0 | 0 | 5.865 | 98.8145 | 18.26%
CZ 4B | 0.3695 | 0.023047 | 0.0010508 | 0.038869 | 0 | 0.1228 | 0 | 0.088158 | 0.046445 | 0.0008067 | 0.025243 | 0 | 0.012364 | 0 | 0 | 0.059552 | 0.78784 | 0.672% | CZ 4B | 11.8602 | 0.73976 | 0.047168 | 3.9663 | 0 | 3.9417 | 0 | 2.8297 | 1.4908 | 0.025893 | 0.81026 | 0 | 0.39686 | 0 | 0 | 1.9115 | 28.0201 | 0.672% | CZ 4B | 3.476 | 0.21681 | 0.0080773 | 0 | 0 | 1.1552 | 0 | 0.82934 | 0.43693 | 0.0075889 | 0.23747 | 0 | 0.11631 | 0 | 0 | 0.56023 | 7.044 | 0.672% | CZ 4B | 0 | 0 | 0.00019608 | 0.039663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039859 | 0.672% | CZ 4B | 36.3906 | 2.2698 | 0.10599 | 4.3351 | 0 | 12.0943 | 0 | 8.6823 | 4.5742 | 0.079449 | 2.4861 | 0 | 1.2177 | 0 | 0 | 5.865 | 78.1006 | 0.672%
CZ 4C | 0.3664 | 0.022887 | 0.0010575 | 0.080345 | 0 | 0.068446 | 0 | 0.11019 | 0.04744 | 0.0009984 | 0.025283 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.79495 | 2.388% | CZ 4C | 11.7605 | 0.73463 | 0.047296 | 8.1984 | 0 | 2.197 | 0 | 3.5368 | 1.5227 | 0.032046 | 0.81154 | 0 | 0.39673 | 0 | 0 | 1.9115 | 31.1491 | 2.388% | CZ 4C | 3.4468 | 0.21531 | 0.0081525 | 0 | 0 | 0.6439 | 0 | 1.0366 | 0.44628 | 0.0093923 | 0.23785 | 0 | 0.11628 | 0 | 0 | 0.56023 | 6.7208 | 2.388% | CZ 4C | 0 | 0 | 0.00019479 | 0.081984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082179 | 2.388% | CZ 4C | 36.0846 | 2.2541 | 0.10664 | 8.9609 | 0 | 6.7409 | 0 | 10.8518 | 4.6721 | 0.098328 | 2.49 | 0 | 1.2173 | 0 | 0 | 5.865 | 79.3418 | 2.388%
CZ 5A | 0.36933 | 0.022983 | 0.00106 | 0.18762 | 0 | 0.098398 | 0 | 0.14884 | 0.019185 | 0.0020088 | 0.025247 | 0 | 0.012364 | 0 | 0 | 0.059552 | 0.9466 | 16% | CZ 5A | 11.8548 | 0.73771 | 0.047552 | 19.145 | 0 | 3.1584 | 0 | 4.7775 | 0.6158 | 0.064477 | 0.81039 | 0 | 0.39686 | 0 | 0 | 1.9115 | 43.52 | 16% | CZ 5A | 3.4745 | 0.21621 | 0.0081525 | 0 | 0 | 0.92566 | 0 | 1.4002 | 0.18048 | 0.018897 | 0.23751 | 0 | 0.11631 | 0 | 0 | 0.56023 | 7.1381 | 16% | CZ 5A | 0 | 0 | 0.00019736 | 0.19145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19165 | 16% | CZ 5A | 36.3741 | 2.2635 | 0.10692 | 20.9255 | 0 | 9.6908 | 0 | 14.6587 | 1.8895 | 0.19783 | 2.4865 | 0 | 1.2177 | 0 | 0 | 5.865 | 95.6759 | 16%
CZ 5B | 0.36883 | 0.022999 | 0.001061 | 0.072558 | 0 | 0.10036 | 0 | 0.093406 | 0.046533 | 0.0013858 | 0.025251 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.8043 | 4.803% | CZ 5B | 11.8387 | 0.73822 | 0.047936 | 7.4039 | 0 | 3.2214 | 0 | 2.9981 | 1.4936 | 0.04448 | 0.81052 | 0 | 0.39673 | 0 | 0 | 1.9115 | 30.9051 | 4.803% | CZ 5B | 3.4697 | 0.21636 | 0.0081149 | 0 | 0 | 0.94415 | 0 | 0.8787 | 0.43775 | 0.013036 | 0.23755 | 0 | 0.11628 | 0 | 0 | 0.56023 | 6.8819 | 4.803% | CZ 5B | 0 | 0 | 0.00020248 | 0.074039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074241 | 4.803% | CZ 5B | 36.3245 | 2.2651 | 0.10709 | 8.0924 | 0 | 9.8843 | 0 | 9.1991 | 4.5828 | 0.13648 | 2.4869 | 0 | 1.2173 | 0 | 0 | 5.865 | 80.1611 | 4.803%
CZ 5C | 0.36755 | 0.022887 | 0.0010588 | 0.12002 | 0 | 0.046601 | 0 | 0.11538 | 0.018766 | 0.0010104 | 0.025235 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.79042 | 0.03694% | CZ 5C | 11.7976 | 0.73463 | 0.047424 | 12.2468 | 0 | 1.4958 | 0 | 3.7034 | 0.60234 | 0.032431 | 0.81 | 0 | 0.39673 | 0 | 0 | 1.9115 | 33.7786 | 0.03694% | CZ 5C | 3.4577 | 0.21531 | 0.0081525 | 0 | 0 | 0.43839 | 0 | 1.0854 | 0.17654 | 0.009505 | 0.2374 | 0 | 0.11628 | 0 | 0 | 0.56023 | 6.3049 | 0.03694% | CZ 5C | 0 | 0 | 0.00019608 | 0.12247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12266 | 0.03694% | CZ 5C | 36.1983 | 2.2541 | 0.10678 | 13.3858 | 0 | 4.5895 | 0 | 11.3631 | 1.8482 | 0.099507 | 2.4853 | 0 | 1.2173 | 0 | 0 | 5.865 | 79.4129 | 0.03694%
CZ 6A | 0.36868 | 0.022959 | 0.001058 | 0.26059 | 0 | 0.098749 | 0 | 0.14674 | 0.016757 | 0.0032068 | 0.025144 | 0 | 0.01236 | 0 | 0 | 0.059552 | 1.0158 | 3.249% | CZ 6A | 11.8337 | 0.73694 | 0.046783 | 26.5913 | 0 | 3.1696 | 0 | 4.71 | 0.53787 | 0.10293 | 0.80706 | 0 | 0.39673 | 0 | 0 | 1.9115 | 50.8445 | 3.249% | CZ 6A | 3.4683 | 0.21598 | 0.0082276 | 0 | 0 | 0.92897 | 0 | 1.3804 | 0.15764 | 0.030168 | 0.23653 | 0 | 0.11628 | 0 | 0 | 0.56023 | 7.1027 | 3.249% | CZ 6A | 0 | 0 | 0.00018711 | 0.26591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2661 | 3.249% | CZ 6A | 36.3092 | 2.2611 | 0.10659 | 29.0643 | 0 | 9.7254 | 0 | 14.4518 | 1.6503 | 0.31583 | 2.4763 | 0 | 1.2173 | 0 | 0 | 5.865 | 103.4431 | 3.249%
CZ 6B | 0.36942 | 0.022919 | 0.0010663 | 0.18859 | 0 | 0.069337 | 0 | 0.10452 | 0.019513 | 0.0027516 | 0.02512 | 0 | 0.01236 | 0 | 0 | 0.059552 | 0.87514 | 0.979% | CZ 6B | 11.8575 | 0.73566 | 0.048193 | 19.2435 | 0 | 2.2256 | 0 | 3.3547 | 0.62631 | 0.08832 | 0.80629 | 0 | 0.39673 | 0 | 0 | 1.9115 | 41.2944 | 0.979% | CZ 6B | 3.4752 | 0.21561 | 0.0081525 | 0 | 0 | 0.65227 | 0 | 0.98322 | 0.18356 | 0.025885 | 0.23631 | 0 | 0.11628 | 0 | 0 | 0.56023 | 6.4568 | 0.979% | CZ 6B | 0 | 0 | 0.00020377 | 0.19244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19264 | 0.979% | CZ 6B | 36.3824 | 2.2572 | 0.10762 | 21.0332 | 0 | 6.8286 | 0 | 10.2933 | 1.9217 | 0.27099 | 2.4739 | 0 | 1.2173 | 0 | 0 | 5.865 | 88.6513 | 0.979%
CZ 7 | 0.3692 | 0.022871 | 0.001072 | 0.31178 | 0 | 0.08218 | 0 | 0.13519 | 0.019884 | 0.0064137 | 0.02506 | 0 | 0.01236 | 0 | 0 | 0.059552 | 1.0456 | 0.3956% | CZ 7 | 11.8506 | 0.73412 | 0.047937 | 31.8139 | 0 | 2.6378 | 0 | 4.3392 | 0.63824 | 0.20587 | 0.80436 | 0 | 0.39673 | 0 | 0 | 1.9115 | 55.3803 | 0.3956% | CZ 7 | 3.4732 | 0.21516 | 0.0082652 | 0 | 0 | 0.7731 | 0 | 1.2717 | 0.18706 | 0.060336 | 0.23575 | 0 | 0.11628 | 0 | 0 | 0.56023 | 6.9011 | 0.3956% | CZ 7 | 0 | 0 | 0.00019736 | 0.31814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31834 | 0.3956% | CZ 7 | 36.3611 | 2.2525 | 0.1081 | 34.7726 | 0 | 8.0935 | 0 | 13.3139 | 1.9583 | 0.63166 | 2.468 | 0 | 1.2173 | 0 | 0 | 5.865 | 107.0421 | 0.3956%
CZ 8 | 0.36056 | 0.022356 | 0.0010454 | 0.37798 | 0 | 0.045651 | 0 | 0.13408 | 0.016837 | 0.0078115 | 0.025036 | 0 | 0.01236 | 0 | 0 | 0.059552 | 1.0633 | 0.02728% | CZ 8 | 11.5732 | 0.71758 | 0.045502 | 38.5692 | 0 | 1.4653 | 0 | 4.3037 | 0.54043 | 0.25073 | 0.80359 | 0 | 0.39673 | 0 | 0 | 1.9115 | 60.5775 | 0.02728% | CZ 8 | 3.3919 | 0.21031 | 0.0082276 | 0 | 0 | 0.42945 | 0 | 1.2613 | 0.15839 | 0.073485 | 0.23552 | 0 | 0.11628 | 0 | 0 | 0.56023 | 6.4452 | 0.02728% | CZ 8 | 0 | 0 | 0.00017429 | 0.38569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38587 | 0.02728% | CZ 8 | 35.51 | 2.2017 | 0.10518 | 42.1562 | 0 | 4.4959 | 0 | 13.205 | 1.6582 | 0.76931 | 2.4657 | 0 | 1.2173 | 0 | 0 | 5.865 | 109.6495 | 0.02728%
US Weighted | 0.36875 | 0.023007 | 0.0010445 | 0.0901 | 0 | 0.24191 | 0 | 0.12389 | 0.031979 | 0.0009826 | 0.025466 | 0 | 0.012362 | 0 | 0 | 0.059552 | 0.97904 | 100% | US Weighted | 11.8362 | 0.73847 | 0.046614 | 9.1938 | 0 | 7.7648 | 0 | 3.9764 | 1.0264 | 0.031539 | 0.81739 | 0 | 0.39678 | 0 | 0 | 1.9115 | 37.74 | 100% | US Weighted | 3.469 | 0.21643 | 0.0080658 | 0 | 0 | 2.2757 | 0 | 1.1654 | 0.30083 | 0.0092436 | 0.23956 | 0 | 0.11629 | 0 | 0 | 0.56023 | 8.3608 | 100% | US Weighted | 0 | 0 | 0.00019094 | 0.091938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092129 | 100% | US Weighted | 36.3168 | 2.2658 | 0.10531 | 10.0489 | 0 | 23.8246 | 0 | 12.2009 | 3.1494 | 0.096772 | 2.508 | 0 | 1.2175 | 0 | 0 | 5.865 | 97.599 | 100%
Building Type: | Primary School |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Primary School |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Primary School |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Primary School |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 73959 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 73959 | [17 empty] | Prototype Floor Area: | 73959 | Building Type: | Primary School | [15 empty] | Prototype Floor Area: | 73959 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 76.63% | 69.49% | 4.651% | -1543% |  | 61.91% |  | 56.77% | -130.6% | -13.33% | 47.37% |  | 64.46% | 0% |  | 13.6% | 53.65% | 0% | CZ 0A | 76.63% | 69.49% | 3.143% | -1543% |  | 61.91% |  | 56.77% | -130.6% | -13.33% | 47.37% |  | 64.46% | 0% |  | 13.6% | 51.76% | 0% | CZ 0A | 76.63% | 69.49% | 7.419% |  |  | 61.91% |  | 56.77% | -130.6% | -13.33% | 47.37% |  | 64.46% | 0% |  | 13.6% | 54.57% | 0% | CZ 0A |  |  | 1.719% | -1543% | [9 empty] | 0% |  |  | -0.8896% | 0% | CZ 0A | 76.63% | 69.49% | 4.473% | -1543% |  | 61.91% |  | 56.77% | -130.6% | -13.33% | 47.37% |  | 64.46% | 0% |  | 13.6% | 53.54% | 0%
CZ 0B | 76.75% | 69.32% | 4.653% | 58.22% |  | 52.7% |  | 44.93% | -119.9% | 5.882% | 47.24% |  | 64.46% | 0% |  | 13.6% | 46.55% | 0% | CZ 0B | 76.75% | 69.32% | 3.156% | 58.22% |  | 52.7% |  | 44.93% | -119.9% | 5.882% | 47.24% |  | 64.46% | 0% |  | 13.6% | 44.63% | 0% | CZ 0B | 76.75% | 69.32% | 7.453% |  |  | 52.7% |  | 44.93% | -119.9% | 5.882% | 47.24% |  | 64.46% | 0% |  | 13.6% | 47.49% | 0% | CZ 0B |  |  | 1.759% | 58.22% | [9 empty] | 0% |  |  | 0.9999% | 0% | CZ 0B | 76.75% | 69.32% | 4.476% | 58.22% |  | 52.7% |  | 44.93% | -119.9% | 5.882% | 47.24% |  | 64.46% | 0% |  | 13.6% | 46.43% | 0%
CZ 1A | 76.16% | 69.25% | 4.577% | 99.28% |  | 55.58% |  | 51.93% | 47.41% | 31.82% | 47.07% |  | 64.46% | 0% |  | 13.6% | 48.92% | 2.71% | CZ 1A | 76.16% | 69.25% | 3.045% | 99.28% |  | 55.58% |  | 51.93% | 47.41% | 31.82% | 47.07% |  | 64.46% | 0% |  | 13.6% | 46.79% | 2.71% | CZ 1A | 76.16% | 69.25% | 7.552% |  |  | 55.58% |  | 51.93% | 47.41% | 31.82% | 47.07% |  | 64.46% | 0% |  | 13.6% | 49.98% | 2.71% | CZ 1A |  |  | 1.65% | 99.28% | [9 empty] | 0% |  |  | 4.675% | 2.71% | CZ 1A | 76.16% | 69.25% | 4.394% | 99.28% |  | 55.58% |  | 51.93% | 47.41% | 31.82% | 47.07% |  | 64.46% | 0% |  | 13.6% | 48.79% | 2.71%
CZ 1B | 76.41% | 69.31% | 4.484% | 25.29% |  | 51.74% |  | 41.91% | -119.6% | 15% | 47.14% |  | 64.46% | 0% |  | 13.6% | 45.2% | 0% | CZ 1B | 76.41% | 69.31% | 2.961% | 25.29% |  | 51.74% |  | 41.91% | -119.6% | 15% | 47.14% |  | 64.46% | 0% |  | 13.6% | 42.98% | 0% | CZ 1B | 76.41% | 69.31% | 7.519% |  |  | 51.74% |  | 41.91% | -119.6% | 15% | 47.14% |  | 64.46% | 0% |  | 13.6% | 46.3% | 0% | CZ 1B |  |  | 1.596% | 25.29% | [9 empty] | 0% |  |  | 3.377% | 0% | CZ 1B | 76.41% | 69.31% | 4.301% | 25.29% |  | 51.74% |  | 41.91% | -119.6% | 15% | 47.14% |  | 64.46% | 0% |  | 13.6% | 45.05% | 0%
CZ 2A | 76.54% | 69.26% | 4.394% | 79.67% |  | 56.22% |  | 45.45% | 51.64% | 55.13% | 47.06% |  | 64.46% | 0% |  | 13.6% | 48.33% | 20.22% | CZ 2A | 76.54% | 69.26% | 2.864% | 79.67% |  | 56.22% |  | 45.45% | 51.64% | 55.13% | 47.06% |  | 64.46% | 0% |  | 13.6% | 46.47% | 20.22% | CZ 2A | 76.54% | 69.26% | 7.585% |  |  | 56.22% |  | 45.45% | 51.64% | 55.13% | 47.06% |  | 64.46% | 0% |  | 13.6% | 49.28% | 20.22% | CZ 2A |  |  | 1.533% | 79.67% | [9 empty] | 0% |  |  | 20.6% | 20.22% | CZ 2A | 76.54% | 69.26% | 4.207% | 79.67% |  | 56.22% |  | 45.45% | 51.64% | 55.13% | 47.06% |  | 64.46% | 0% |  | 13.6% | 48.21% | 20.22%
CZ 2B | 76.15% | 69.28% | 4.311% | 77.49% |  | 51.02% |  | 39.4% | -154% | 52.17% | 46.96% |  | 64.44% | 0% |  | 13.6% | 43.97% | 2.485% | CZ 2B | 76.15% | 69.28% | 2.758% | 77.49% |  | 51.02% |  | 39.4% | -154% | 52.17% | 46.96% |  | 64.44% | 0% |  | 13.6% | 41.97% | 2.485% | CZ 2B | 76.15% | 69.28% | 7.582% |  |  | 51.02% |  | 39.4% | -154% | 52.17% | 46.96% |  | 64.44% | 0% |  | 13.6% | 45% | 2.485% | CZ 2B |  |  | 1.414% | 77.49% | [9 empty] | 0% |  |  | 17.08% | 2.485% | CZ 2B | 76.15% | 69.28% | 4.121% | 77.49% |  | 51.02% |  | 39.4% | -154% | 52.17% | 46.96% |  | 64.44% | 0% |  | 13.6% | 43.84% | 2.485%
CZ 3A | 76.29% | 69.19% | 4.063% | 65.15% |  | 55.5% |  | 51.37% | 46.06% | 45.72% | 46.88% |  | 64.44% | 0% |  | 13.6% | 47.5% | 19.44% | CZ 3A | 76.29% | 69.19% | 2.506% | 65.15% |  | 55.5% |  | 51.37% | 46.06% | 45.72% | 46.88% |  | 64.44% | 0% |  | 13.6% | 46.21% | 19.44% | CZ 3A | 76.29% | 69.19% | 7.648% |  |  | 55.5% |  | 51.37% | 46.06% | 45.72% | 46.88% |  | 64.44% | 0% |  | 13.6% | 48.24% | 19.44% | CZ 3A |  |  | 1.227% | 65.15% | [9 empty] | 0% |  |  | 37.71% | 19.44% | CZ 3A | 76.29% | 69.19% | 3.867% | 65.15% |  | 55.5% |  | 51.37% | 46.06% | 45.72% | 46.88% |  | 64.44% | 0% |  | 13.6% | 47.41% | 19.44%
CZ 3B | 75.98% | 69.38% | 4.151% | 47.55% |  | 42.56% |  | 41.78% | 100% | 47.56% | 46.81% |  | 64.44% | 0% |  | 13.6% | 43.79% | 7.425% | CZ 3B | 75.98% | 69.38% | 2.596% | 47.55% |  | 42.56% |  | 41.78% | 100% | 47.56% | 46.81% |  | 64.44% | 0% |  | 13.6% | 41.17% | 7.425% | CZ 3B | 75.98% | 69.38% | 7.648% |  |  | 42.56% |  | 41.78% | 100% | 47.56% | 46.81% |  | 64.44% | 0% |  | 13.6% | 45.2% | 7.425% | CZ 3B |  |  | 1.3% | 47.55% | [9 empty] | 0% |  |  | 17.35% | 7.425% | CZ 3B | 75.98% | 69.38% | 3.957% | 47.55% |  | 42.56% |  | 41.78% | 100% | 47.56% | 46.81% |  | 64.44% | 0% |  | 13.6% | 43.62% | 7.425%
CZ 3C | 75.87% | 69.35% | 4.097% | 84.1% |  | 57.78% |  | 52.46% |  | 66.94% | 46.95% |  | 64.44% | 0% |  | 13.6% | 47.36% | 0.9093% | CZ 3C | 75.87% | 69.35% | 2.559% | 84.1% |  | 57.78% |  | 52.46% |  | 66.94% | 46.95% |  | 64.44% | 0% |  | 13.6% | 45.79% | 0.9093% | CZ 3C | 75.87% | 69.35% | 7.615% |  |  | 57.78% |  | 52.46% |  | 66.94% | 46.95% |  | 64.44% | 0% |  | 13.6% | 48.22% | 0.9093% | CZ 3C |  |  | 1.291% | 84.1% | [9 empty] | 0% |  |  | 32.67% | 0.9093% | CZ 3C | 75.87% | 69.35% | 3.904% | 84.1% |  | 57.78% |  | 52.46% |  | 66.94% | 46.95% |  | 64.44% | 0% |  | 13.6% | 47.26% | 0.9093%
CZ 4A | 76.14% | 69.16% | 3.976% | 79.59% |  | 54.68% |  | 53.28% | 55.8% | 57.12% | 46.78% |  | 64.44% | 0% |  | 13.6% | 49.61% | 18.26% | CZ 4A | 76.14% | 69.16% | 2.46% | 79.59% |  | 54.68% |  | 53.28% | 55.8% | 57.12% | 46.78% |  | 64.44% | 0% |  | 13.6% | 51.91% | 18.26% | CZ 4A | 76.14% | 69.16% | 7.714% |  |  | 54.68% |  | 53.28% | 55.8% | 57.12% | 46.78% |  | 64.44% | 0% |  | 13.6% | 48.08% | 18.26% | CZ 4A |  |  | 1.258% | 79.59% | [9 empty] | 0% |  |  | 60.29% | 18.26% | CZ 4A | 76.14% | 69.16% | 3.783% | 79.59% |  | 54.68% |  | 53.28% | 55.8% | 57.12% | 46.78% |  | 64.44% | 0% |  | 13.6% | 49.79% | 18.26%
CZ 4B | 76.44% | 69.33% | 4.015% | 54.35% |  | 45.19% |  | 41.45% | 100% | 57.39% | 46.74% |  | 64.46% | 0% |  | 13.6% | 44.69% | 0.672% | CZ 4B | 76.44% | 69.33% | 2.497% | 54.35% |  | 45.19% |  | 41.45% | 100% | 57.39% | 46.74% |  | 64.46% | 0% |  | 13.6% | 42.58% | 0.672% | CZ 4B | 76.44% | 69.33% | 7.681% |  |  | 45.19% |  | 41.45% | 100% | 57.39% | 46.74% |  | 64.46% | 0% |  | 13.6% | 45.91% | 0.672% | CZ 4B |  |  | 1.282% | 54.35% | [9 empty] | 0% |  |  | 29.62% | 0.672% | CZ 4B | 76.44% | 69.33% | 3.822% | 54.35% |  | 45.19% |  | 41.45% | 100% | 57.39% | 46.74% |  | 64.46% | 0% |  | 13.6% | 44.54% | 0.672%
CZ 4C | 75.8% | 68.98% | 3.955% | 55.66% |  | 53.54% |  | 49.02% | 100% | 46.55% | 46.68% |  | 64.44% | 0% |  | 13.6% | 46.59% | 2.388% | CZ 4C | 75.8% | 68.98% | 2.43% | 55.66% |  | 53.54% |  | 49.02% | 100% | 46.55% | 46.68% |  | 64.44% | 0% |  | 13.6% | 45.06% | 2.388% | CZ 4C | 75.8% | 68.98% | 7.747% |  |  | 53.54% |  | 49.02% | 100% | 46.55% | 46.68% |  | 64.44% | 0% |  | 13.6% | 47.59% | 2.388% | CZ 4C |  |  | 1.227% | 55.66% | [9 empty] | 0% |  |  | 39.24% | 2.388% | CZ 4C | 75.8% | 68.98% | 3.759% | 55.66% |  | 53.54% |  | 49.02% | 100% | 46.55% | 46.68% |  | 64.44% | 0% |  | 13.6% | 46.47% | 2.388%
CZ 5A | 76.41% | 69.17% | 3.844% | 71.91% |  | 51.89% |  | 56.79% | 41.21% | 56.08% | 46.64% |  | 64.46% | 0% |  | 13.6% | 49.22% | 16% | CZ 5A | 76.41% | 69.17% | 2.341% | 71.91% |  | 51.89% |  | 56.79% | 41.21% | 56.08% | 46.64% |  | 64.46% | 0% |  | 13.6% | 51.62% | 16% | CZ 5A | 76.41% | 69.17% | 7.747% |  |  | 51.89% |  | 56.79% | 41.21% | 56.08% | 46.64% |  | 64.46% | 0% |  | 13.6% | 47.4% | 16% | CZ 5A |  |  | 1.18% | 71.91% | [9 empty] | 0% |  |  | 58.21% | 16% | CZ 5A | 76.41% | 69.17% | 3.65% | 71.91% |  | 51.89% |  | 56.79% | 41.21% | 56.08% | 46.64% |  | 64.46% | 0% |  | 13.6% | 49.41% | 16%
CZ 5B | 76.31% | 69.21% | 3.894% | 48.89% |  | 49.25% |  | 43.5% | 100% | 51.95% | 46.73% |  | 64.44% | 0% |  | 13.6% | 45.28% | 4.803% | CZ 5B | 76.31% | 69.21% | 2.399% | 48.89% |  | 49.25% |  | 43.5% | 100% | 51.95% | 46.73% |  | 64.44% | 0% |  | 13.6% | 43.11% | 4.803% | CZ 5B | 76.31% | 69.21% | 7.714% |  |  | 49.25% |  | 43.5% | 100% | 51.95% | 46.73% |  | 64.44% | 0% |  | 13.6% | 46.7% | 4.803% | CZ 5B |  |  | 1.235% | 48.89% | [9 empty] | 0% |  |  | 34.68% | 4.803% | CZ 5B | 76.31% | 69.21% | 3.702% | 48.89% |  | 49.25% |  | 43.5% | 100% | 51.95% | 46.73% |  | 64.44% | 0% |  | 13.6% | 45.12% | 4.803%
CZ 5C | 76.04% | 68.98% | 3.88% | 74.47% |  | 56.05% |  | 50.84% | 39.98% | 49.51% | 46.62% |  | 64.44% | 0% |  | 13.6% | 47.04% | 0.03694% | CZ 5C | 76.04% | 68.98% | 2.369% | 74.47% |  | 56.05% |  | 50.84% | 39.98% | 49.51% | 46.62% |  | 64.44% | 0% |  | 13.6% | 48.6% | 0.03694% | CZ 5C | 76.04% | 68.98% | 7.747% |  |  | 56.05% |  | 50.84% | 39.98% | 49.51% | 46.62% |  | 64.44% | 0% |  | 13.6% | 45.97% | 0.03694% | CZ 5C |  |  | 1.194% | 74.47% | [9 empty] | 0% |  |  | 54% | 0.03694% | CZ 5C | 76.04% | 68.98% | 3.686% | 74.47% |  | 56.05% |  | 50.84% | 39.98% | 49.51% | 46.62% |  | 64.44% | 0% |  | 13.6% | 47.16% | 0.03694%
CZ 6A | 76.27% | 69.12% | 3.723% | 66.52% |  | 50.39% |  | 54.88% | 35.71% | 57.65% | 46.59% |  | 64.44% | 0% |  | 13.6% | 49.1% | 3.249% | CZ 6A | 76.27% | 69.12% | 2.21% | 66.52% |  | 50.39% |  | 54.88% | 35.71% | 57.65% | 46.59% |  | 64.44% | 0% |  | 13.6% | 51.79% | 3.249% | CZ 6A | 76.27% | 69.12% | 7.81% |  |  | 50.39% |  | 54.88% | 35.71% | 57.65% | 46.59% |  | 64.44% | 0% |  | 13.6% | 46.77% | 3.249% | CZ 6A |  |  | 1.065% | 66.52% | [9 empty] | 0% |  |  | 57.4% | 3.249% | CZ 6A | 76.27% | 69.12% | 3.526% | 66.52% |  | 50.39% |  | 54.88% | 35.71% | 57.65% | 46.59% |  | 64.44% | 0% |  | 13.6% | 49.34% | 3.249%
CZ 6B | 76.43% | 69.05% | 3.785% | 67.97% |  | 51.86% |  | 46.78% | 41.75% | 62.18% | 46.61% |  | 64.44% | 0% |  | 13.6% | 47.39% | 0.979% | CZ 6B | 76.43% | 69.05% | 2.304% | 67.97% |  | 51.86% |  | 46.78% | 41.75% | 62.18% | 46.61% |  | 64.44% | 0% |  | 13.6% | 49.73% | 0.979% | CZ 6B | 76.43% | 69.05% | 7.744% |  |  | 51.86% |  | 46.78% | 41.75% | 62.18% | 46.61% |  | 64.44% | 0% |  | 13.6% | 45.55% | 0.979% | CZ 6B |  |  | 1.176% | 67.97% | [9 empty] | 0% |  |  | 55.56% | 0.979% | CZ 6B | 76.43% | 69.05% | 3.592% | 67.97% |  | 51.86% |  | 46.78% | 41.75% | 62.18% | 46.61% |  | 64.44% | 0% |  | 13.6% | 47.58% | 0.979%
CZ 7 | 76.38% | 68.96% | 3.657% | 65.78% |  | 51.85% |  | 52.1% | 42.46% | 93.97% | 46.52% |  | 64.44% | 0% |  | 13.6% | 49.61% | 0.3956% | CZ 7 | 76.38% | 68.96% | 2.171% | 65.78% |  | 51.85% |  | 52.1% | 42.46% | 93.97% | 46.52% |  | 64.44% | 0% |  | 13.6% | 52.62% | 0.3956% | CZ 7 | 76.38% | 68.96% | 7.843% |  |  | 51.85% |  | 52.1% | 42.46% | 93.97% | 46.52% |  | 64.44% | 0% |  | 13.6% | 46.72% | 0.3956% | CZ 7 |  |  | 1.068% | 65.78% | [9 empty] | 0% |  |  | 58.05% | 0.3956% | CZ 7 | 76.38% | 68.96% | 3.461% | 65.78% |  | 51.85% |  | 52.1% | 42.46% | 93.97% | 46.52% |  | 64.44% | 0% |  | 13.6% | 49.89% | 0.3956%
CZ 8 | 74.59% | 67.77% | 3.438% | 56.7% |  | 55.92% |  | 48.26% | 35.83% | 88.87% | 46.6% |  | 64.44% | 0% |  | 13.6% | 47.37% | 0.02728% | CZ 8 | 74.59% | 67.77% | 1.962% | 56.7% |  | 55.92% |  | 48.26% | 35.83% | 88.87% | 46.6% |  | 64.44% | 0% |  | 13.6% | 49.17% | 0.02728% | CZ 8 | 74.59% | 67.77% | 7.805% |  |  | 55.92% |  | 48.26% | 35.83% | 88.87% | 46.6% |  | 64.44% | 0% |  | 13.6% | 45.27% | 0.02728% | CZ 8 |  |  | 0.8895% | 56.7% | [9 empty] | 0% |  |  | 51.71% | 0.02728% | CZ 8 | 74.59% | 67.77% | 3.241% | 56.7% |  | 55.92% |  | 48.26% | 35.83% | 88.87% | 46.6% |  | 64.44% | 0% |  | 13.6% | 47.55% | 0.02728%
US Weighted | 76.29% | 69.21% | 4.079% | 70.9% | 0% | 53.24% | 0% | 49.98% | 50.69% | 52.63% | 46.83% | 0% | 64.45% | 0% | 0% | 13.6% | 47.92% | 100% | US Weighted | 76.29% | 69.21% | 2.552% | 70.9% | 0% | 53.24% | 0% | 49.98% | 50.69% | 52.63% | 46.83% | 0% | 64.45% | 0% | 0% | 13.6% | 47.75% | 100% | US Weighted | 76.29% | 69.21% | 7.672% | 0% | 0% | 53.24% | 0% | 49.98% | 50.69% | 52.63% | 46.83% | 0% | 64.45% | 0% | 0% | 13.6% | 47.84% | 100% | US Weighted | 0% | 0% | 1.303% | 70.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.43% | 100% | US Weighted | 76.29% | 69.21% | 3.887% | 70.9% | 0% | 53.24% | 0% | 49.98% | 50.69% | 52.63% | 46.83% | 0% | 64.45% | 0% | 0% | 13.6% | 47.92% | 100%

## SchSec
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Secondary School |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 210887 |  | Building Type: | Secondary School |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 |  | Building Type: | Secondary School |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Secondary School |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Secondary School | [14 empty] | Prototype Floor Area: | 210887 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.11484 | 0.0095301 | 0.04253 | 0.029356 | 0 | 0.23127 | 0 | 0.11076 | 0.03057 | 0.0039571 | 0.017 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.94624 |  | STD2019 | 3.6861 | 0.3059 | 2.8272 | 2.9956 | 0 | 7.4232 | 0 | 3.5552 | 0.98125 | 0.12701 | 0.54567 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 35.5649 |  | STD2019 | 1.0803 | 0.089653 | 0.20343 | 0 | 0 | 2.1756 | 0 | 1.042 | 0.28759 | 0.037226 | 0.15993 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 8.2032 |  | STD2019 | 0 | 0 | 0.021331 | 0.029956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.075757 |  | STD2019 | 11.31 | 0.93858 | 4.4612 | 3.2741 | 0 | 22.7765 | 0 | 10.9085 | 3.0107 | 0.38971 | 1.6743 | 0.90762 | 0.40595 | 7.6313 | 0 | 26.4707 | 94.1593
STD2016 | 0.1336 | 0.0095301 | 0.042548 | 0.032553 | 0 | 0.2415 | 0 | 0.12447 | 0.027737 | 0.0040832 | 0.025229 | 0.0092157 | 0.0041591 | 0.07431 | 0 | 0.26878 | 0.99771 |  | STD2016 | 4.2881 | 0.3059 | 2.8291 | 3.3218 | 0 | 7.7516 | 0 | 3.9952 | 0.8903 | 0.13106 | 0.8098 | 0.29581 | 0.1335 | 4.0625 | 0 | 8.6272 | 37.4418 |  | STD2016 | 1.2568 | 0.089653 | 0.20343 | 0 | 0 | 2.2719 | 0 | 1.1709 | 0.26093 | 0.038412 | 0.23734 | 0.086696 | 0.039126 | 0.47347 | 0 | 2.5285 | 8.6571 |  | STD2016 | 0 | 0 | 0.02135 | 0.033218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.079038 |  | STD2016 | 13.1573 | 0.93858 | 4.4633 | 3.6307 | 0 | 23.7841 | 0 | 12.2584 | 2.7317 | 0.40214 | 2.4847 | 0.90762 | 0.40961 | 7.6313 | 0 | 26.4707 | 99.27
STD2013 | 0.25157 | 0.016495 | 0.042548 | 0.025893 | 0 | 0.25848 | 0 | 0.12981 | 0.028214 | 0.0053003 | 0.025224 | 0.0092157 | 0.0057249 | 0.07431 | 0 | 0.26878 | 1.1416 |  | STD2013 | 8.0747 | 0.52947 | 2.8291 | 2.6421 | 0 | 8.2965 | 0 | 4.1667 | 0.9056 | 0.17013 | 0.80965 | 0.29581 | 0.18376 | 4.0625 | 0 | 8.6272 | 41.5932 |  | STD2013 | 2.3666 | 0.15518 | 0.20343 | 0 | 0 | 2.4316 | 0 | 1.2212 | 0.26542 | 0.049862 | 0.23729 | 0.086696 | 0.053856 | 0.47347 | 0 | 2.5285 | 10.073 |  | STD2013 | 0 | 0 | 0.02135 | 0.026421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.072242 |  | STD2013 | 24.7756 | 1.6246 | 4.4633 | 2.8878 | 0 | 25.456 | 0 | 12.7845 | 2.7786 | 0.522 | 2.4842 | 0.90762 | 0.56381 | 7.6313 | 0 | 26.4707 | 113.3502
STD2010 | 0.28949 | 0.016495 | 0.042602 | 0.034586 | 0 | 0.33387 | 0 | 0.16342 | 0.03461 | 0.007758 | 0.029703 | 0.0092395 | 0.0062098 | 0.07431 | 0 | 0.29592 | 1.3382 |  | STD2010 | 9.2919 | 0.52947 | 2.8334 | 3.5292 | 0 | 10.7163 | 0 | 5.2453 | 1.1109 | 0.24901 | 0.95339 | 0.29657 | 0.19932 | 4.0625 | 0 | 9.4984 | 48.5158 |  | STD2010 | 2.7233 | 0.15518 | 0.2036 | 0 | 0 | 3.1408 | 0 | 1.5373 | 0.32558 | 0.072982 | 0.27942 | 0.08692 | 0.058418 | 0.47347 | 0 | 2.7838 | 11.8408 |  | STD2010 | 0 | 0 | 0.021387 | 0.035292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.081149 |  | STD2010 | 28.5104 | 1.6246 | 4.4691 | 3.8574 | 0 | 32.8809 | 0 | 16.0942 | 3.4085 | 0.76405 | 2.9253 | 0.90996 | 0.61158 | 7.6313 | 0 | 29.1439 | 132.8311
STD2007 | 0.46148 | 0.030358 | 0.04263 | 0.059824 | 0 | 0.44228 | 0 | 0.21885 | 0.045335 | 0.022048 | 0.02955 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.7456 |  | STD2007 | 14.8126 | 0.97441 | 2.8362 | 6.1045 | 0 | 14.1961 | 0 | 7.0246 | 1.4551 | 0.7077 | 0.94848 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 63.3609 |  | STD2007 | 4.3413 | 0.28558 | 0.20361 | 0 | 0 | 4.1606 | 0 | 2.0588 | 0.42648 | 0.20742 | 0.27798 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 15.4361 |  | STD2007 | 0 | 0 | 0.021415 | 0.061045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10693 |  | STD2007 | 45.4494 | 2.9898 | 4.4722 | 6.6723 | 0 | 43.5578 | 0 | 21.5536 | 4.4648 | 2.1714 | 2.9102 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 173.2877
STD2004 | 0.46148 | 0.030358 | 0.042637 | 0.09296 | 0 | 0.48162 | 0 | 0.29191 | 0.074845 | 0.024008 | 0.029549 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.9227 |  | STD2004 | 14.8126 | 0.97441 | 2.837 | 9.4857 | 0 | 15.4591 | 0 | 9.3698 | 2.4024 | 0.7706 | 0.94846 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 71.361 |  | STD2004 | 4.3413 | 0.28558 | 0.20361 | 0 | 0 | 4.5308 | 0 | 2.7461 | 0.70409 | 0.22585 | 0.27798 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 16.7896 |  | STD2004 | 0 | 0 | 0.021422 | 0.094857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.14075 |  | STD2004 | 45.4494 | 2.9898 | 4.473 | 10.3679 | 0 | 47.4329 | 0 | 28.7491 | 7.3712 | 2.3644 | 2.9102 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 191.1539
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 7.082e-06 | 0.033136 | 0 | 0.039346 | 0 | 0.073061 | 0.029511 | 0.0019595 | -5.7344e-07 | 0 | 0 | 0 | 0 | 0 | 0.17702 |  | 2004-2007 | 0 | 0 | 0.00072329 | 3.3812 | 0 | 1.2629 | 0 | 2.3451 | 0.94722 | 0.062895 | -1.8406e-05 | 0 | 0 | 0 | 0 | 0 | 8 |  | 2004-2007 | 0 | 0 | -8.5759e-08 | 0 | 0 | 0.37014 | 0 | 0.68731 | 0.27762 | 0.018433 | -5.3946e-06 | 0 | 0 | 0 | 0 | 0 | 1.3535 |  | 2004-2007 | 0 | 0 | 7.2358e-06 | 0.033812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033819 |  | 2004-2007 | 0 | 0 | 0.00078998 | 3.6956 | 0 | 3.875 | 0 | 7.1955 | 2.9064 | 0.19298 | -5.6476e-05 | 0 | 0 | 0 | 0 | 0 | 17.8662
2007-2010 | 0.17199 | 0.013862 | 2.8491e-05 | 0.025238 | 0 | 0.10841 | 0 | 0.055434 | 0.010725 | 0.01429 | -0.00015282 | 0.0013698 | 0.0049051 | 0 | 0 | 0.0013347 | 0.40744 |  | 2007-2010 | 5.5207 | 0.44494 | 0.0028565 | 2.5753 | 0 | 3.4798 | 0 | 1.7793 | 0.34425 | 0.45869 | -0.0049053 | 0.043966 | 0.15744 | 0 | 0 | 0.042842 | 14.8452 |  | 2007-2010 | 1.618 | 0.13041 | 6.8281e-06 | 0 | 0 | 1.0199 | 0 | 0.52148 | 0.1009 | 0.13443 | -0.0014377 | 0.012886 | 0.046144 | 0 | 0 | 0.012556 | 3.5953 |  | 2007-2010 | 0 | 0 | 2.8332e-05 | 0.025753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025782 |  | 2007-2010 | 16.939 | 1.3652 | 0.0031681 | 2.8148 | 0 | 10.677 | 0 | 5.4594 | 1.0563 | 1.4074 | -0.015051 | 0.1349 | 0.48308 | 0 | 0 | 0.13145 | 40.4566
2010-2013 | 0.037922 | 0 | 5.4147e-05 | 0.0086934 | 0 | 0.07539 | 0 | 0.033606 | 0.0063958 | 0.0024577 | 0.0044782 | 2.381e-05 | 0.00048496 | 0 | 0 | 0.027143 | 0.19665 |  | 2010-2013 | 1.2172 | 0 | 0.0042642 | 0.88708 | 0 | 2.4199 | 0 | 1.0787 | 0.20529 | 0.078886 | 0.14374 | 0.00076424 | 0.015566 | 0 | 0 | 0.87123 | 6.9226 |  | 2010-2013 | 0.35674 | 0 | 0.0001696 | 0 | 0 | 0.70922 | 0 | 0.31614 | 0.060167 | 0.02312 | 0.042127 | 0.00022399 | 0.0045622 | 0 | 0 | 0.25534 | 1.7678 |  | 2010-2013 | 0 | 0 | 3.6856e-05 | 0.0088708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0089076 |  | 2010-2013 | 3.7347 | 0 | 0.0058038 | 0.96958 | 0 | 7.4248 | 0 | 3.3097 | 0.62989 | 0.24205 | 0.44103 | 0.0023449 | 0.047761 | 0 | 0 | 2.6732 | 19.4809
2013-2016 | 0.11797 | 0.0069653 | 1.3692e-07 | -0.0066603 | 0 | 0.016976 | 0 | 0.0053424 | 0.00047672 | 0.0012171 | -4.5721e-06 | 0 | 0.0015658 | 0 | 0 | 0 | 0.14385 |  | 2013-2016 | 3.7866 | 0.22357 | 1.403e-05 | -0.67963 | 0 | 0.5449 | 0 | 0.17148 | 0.015302 | 0.039065 | -0.00014676 | 0 | 0.050258 | 0 | 0 | 0 | 4.1514 |  | 2013-2016 | 1.1098 | 0.065525 | -7.8633e-09 | 0 | 0 | 0.1597 | 0 | 0.050258 | 0.0044846 | 0.011449 | -4.3011e-05 | 0 | 0.01473 | 0 | 0 | 0 | 1.4159 |  | 2013-2016 | 0 | 0 | 1.4056e-07 | -0.0067963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0067961 |  | 2013-2016 | 11.6184 | 0.68598 | 1.5281e-05 | -0.74283 | 0 | 1.6719 | 0 | 0.52615 | 0.04695 | 0.11986 | -0.00045029 | 0 | 0.15421 | 0 | 0 | 0 | 14.0801
2016-2019 | 0.018756 | 0 | 1.809e-05 | 0.0031968 | 0 | 0.010232 | 0 | 0.013706 | -0.0028334 | 0.00012614 | 0.0082287 | 0 | 3.7167e-05 | 0 | 0 | 0 | 0.051467 |  | 2016-2019 | 0.60203 | 0 | 0.0018726 | 0.3262 | 0 | 0.32841 | 0 | 0.43993 | -0.090946 | 0.0040489 | 0.26412 | 0 | 0.001193 | 0 | 0 | 0 | 1.8769 |  | 2016-2019 | 0.17645 | 0 | -3.5819e-06 | 0 | 0 | 0.096252 | 0 | 0.12894 | -0.026655 | 0.0011867 | 0.07741 | 0 | 0.00034964 | 0 | 0 | 0 | 0.45392 |  | 2016-2019 | 0 | 0 | 1.8848e-05 | 0.003262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0032809 |  | 2016-2019 | 1.8472 | 0 | 0.0020226 | 0.35654 | 0 | 1.0077 | 0 | 1.3498 | -0.27905 | 0.012423 | 0.81041 | 0 | 0.0036604 | 0 | 0 | 0 | 5.1107
2004-2019 | 0.34664 | 0.020827 | 0.00010795 | 0.063604 | 0 | 0.25036 | 0 | 0.18115 | 0.044275 | 0.020051 | 0.012549 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.97643 |  | 2004-2019 | 11.1265 | 0.66851 | 0.0097306 | 6.4902 | 0 | 8.0359 | 0 | 5.8145 | 1.4211 | 0.64359 | 0.40279 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 35.7961 |  | 2004-2019 | 3.261 | 0.19593 | 0.00017275 | 0 | 0 | 2.3552 | 0 | 1.7041 | 0.41651 | 0.18862 | 0.11805 | 0.01311 | 0.065785 | 0 | 0 | 0.2679 | 8.5864 |  | 2004-2019 | 0 | 0 | 9.1411e-05 | 0.064902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064993 |  | 2004-2019 | 34.1393 | 2.0512 | 0.0118 | 7.0938 | 0 | 24.6564 | 0 | 17.8406 | 4.3604 | 1.9747 | 1.2359 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 96.9946
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.01661% | 35.65% |  | 8.169% |  | 25.03% | 39.43% | 8.162% | -0.001941% | 0% | 0% | 0% |  | 0% | 9.207% |  | 2004-2007 | 0% | 0% | 0.0255% | 35.65% |  | 8.169% |  | 25.03% | 39.43% | 8.162% | -0.001941% | 0% | 0% | 0% |  | 0% | 11.21% |  | 2004-2007 | 0% | 0% | -4.212e-05% |  |  | 8.169% |  | 25.03% | 39.43% | 8.162% | -0.001941% | 0% | 0% | 0% |  | 0% | 8.062% |  | 2004-2007 |  |  | 0.03378% | 35.65% | [9 empty] | 0% |  |  | 24.03% |  | 2004-2007 | 0% | 0% | 0.01766% | 35.65% |  | 8.169% |  | 25.03% | 39.43% | 8.162% | -0.001941% | 0% | 0% | 0% |  | 0% | 9.346%
2007-2010 | 37.27% | 45.66% | 0.06683% | 42.19% |  | 24.51% |  | 25.33% | 23.66% | 64.81% | -0.5172% | 12.91% | 44.13% | 0% |  | 0.449% | 23.34% |  | 2007-2010 | 37.27% | 45.66% | 0.1007% | 42.19% |  | 24.51% |  | 25.33% | 23.66% | 64.81% | -0.5172% | 12.91% | 44.13% | 0% |  | 0.449% | 23.43% |  | 2007-2010 | 37.27% | 45.66% | 0.003354% |  |  | 24.51% |  | 25.33% | 23.66% | 64.81% | -0.5172% | 12.91% | 44.13% | 0% |  | 0.449% | 23.29% |  | 2007-2010 |  |  | 0.1323% | 42.19% | [9 empty] | 0% |  |  | 24.11% |  | 2007-2010 | 37.27% | 45.66% | 0.07084% | 42.19% |  | 24.51% |  | 25.33% | 23.66% | 64.81% | -0.5172% | 12.91% | 44.13% | 0% |  | 0.449% | 23.35%
2010-2013 | 13.1% | 0% | 0.1271% | 25.14% |  | 22.58% |  | 20.56% | 18.48% | 31.68% | 15.08% | 0.2577% | 7.81% | 0% |  | 9.172% | 14.69% |  | 2010-2013 | 13.1% | 0% | 0.1505% | 25.14% |  | 22.58% |  | 20.56% | 18.48% | 31.68% | 15.08% | 0.2577% | 7.81% | 0% |  | 9.172% | 14.27% |  | 2010-2013 | 13.1% | 0% | 0.0833% |  |  | 22.58% |  | 20.56% | 18.48% | 31.68% | 15.08% | 0.2577% | 7.81% | 0% |  | 9.172% | 14.93% |  | 2010-2013 |  |  | 0.1723% | 25.14% | [9 empty] | 0% |  |  | 10.98% |  | 2010-2013 | 13.1% | 0% | 0.1299% | 25.14% |  | 22.58% |  | 20.56% | 18.48% | 31.68% | 15.08% | 0.2577% | 7.81% | 0% |  | 9.172% | 14.67%
2013-2016 | 46.89% | 42.23% | 0.0003218% | -25.72% |  | 6.568% |  | 4.116% | 1.69% | 22.96% | -0.01813% | 0% | 27.35% | 0% |  | 0% | 12.6% |  | 2013-2016 | 46.89% | 42.23% | 0.0004959% | -25.72% |  | 6.568% |  | 4.116% | 1.69% | 22.96% | -0.01813% | 0% | 27.35% | 0% |  | 0% | 9.981% |  | 2013-2016 | 46.89% | 42.23% | -3.865e-06% |  |  | 6.568% |  | 4.116% | 1.69% | 22.96% | -0.01813% | 0% | 27.35% | 0% |  | 0% | 14.06% |  | 2013-2016 |  |  | 0.0006584% | -25.72% | [9 empty] | 0% |  |  | -9.407% |  | 2013-2016 | 46.89% | 42.23% | 0.0003424% | -25.72% |  | 6.568% |  | 4.116% | 1.69% | 22.96% | -0.01813% | 0% | 27.35% | 0% |  | 0% | 12.42%
2016-2019 | 14.04% | 0% | 0.04252% | 9.82% |  | 4.237% |  | 11.01% | -10.22% | 3.089% | 32.62% | 0% | 0.8936% | 0% |  | 0% | 5.159% |  | 2016-2019 | 14.04% | 0% | 0.06619% | 9.82% |  | 4.237% |  | 11.01% | -10.22% | 3.089% | 32.62% | 0% | 0.8936% | 0% |  | 0% | 5.013% |  | 2016-2019 | 14.04% | 0% | -0.001761% |  |  | 4.237% |  | 11.01% | -10.22% | 3.089% | 32.62% | 0% | 0.8936% | 0% |  | 0% | 5.243% |  | 2016-2019 |  |  | 0.08828% | 9.82% | [9 empty] | 0% |  |  | 4.151% |  | 2016-2019 | 14.04% | 0% | 0.04532% | 9.82% |  | 4.237% |  | 11.01% | -10.22% | 3.089% | 32.62% | 0% | 0.8936% | 0% |  | 0% | 5.148%
2004-2019 | 75.12% | 68.61% | 0.2532% | 68.42% |  | 51.98% |  | 62.06% | 59.16% | 83.52% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 50.79% |  | 2004-2019 | 75.12% | 68.61% | 0.343% | 68.42% |  | 51.98% |  | 62.06% | 59.16% | 83.52% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 50.16% |  | 2004-2019 | 75.12% | 68.61% | 0.08484% |  |  | 51.98% |  | 62.06% | 59.16% | 83.52% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 51.14% |  | 2004-2019 |  |  | 0.4267% | 68.42% | [9 empty] | 0% |  |  | 46.18% |  | 2004-2019 | 75.12% | 68.61% | 0.2638% | 68.42% |  | 51.98% |  | 62.06% | 59.16% | 83.52% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 50.74%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.11113 | 0.0095323 | 0.035909 | 0.0047847 | 0 | 0.7629 | 0 | 0.16974 | 0.046891 | 0.010153 | 0.017262 | 0.0092157 | 0.0041205 | 0.07431 | 0 | 0.26878 | 1.5247 | 0% | CZ 0A | 3.5671 | 0.30597 | 2.1517 | 0.48823 | 0 | 24.4873 | 0 | 5.4482 | 1.5051 | 0.32588 | 0.55407 | 0.29581 | 0.13226 | 4.0625 | 0 | 8.6272 | 51.9513 | 0% | CZ 0A | 1.0455 | 0.089673 | 0.20343 | 0 | 0 | 7.1768 | 0 | 1.5968 | 0.44112 | 0.09551 | 0.16239 | 0.086696 | 0.038763 | 0.47347 | 0 | 2.5285 | 13.9386 | 0% | CZ 0A | 0 | 0 | 0.014576 | 0.0048823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.043929 | 0% | CZ 0A | 10.9449 | 0.93879 | 3.7229 | 0.53364 | 0 | 75.1342 | 0 | 16.7165 | 4.6181 | 0.99989 | 1.7001 | 0.90762 | 0.40581 | 7.6313 | 0 | 26.4707 | 150.7244 | 0%
CZ 0B | 0.11063 | 0.0095267 | 0.036303 | 0.00050256 | 0 | 0.65573 | 0 | 0.1458 | 0.042696 | 0.0093502 | 0.01722 | 0.0092157 | 0.0041205 | 0.07431 | 0 | 0.26878 | 1.3842 | 0% | CZ 0B | 3.5508 | 0.30579 | 2.1919 | 0.051281 | 0 | 21.0477 | 0 | 4.6797 | 1.3705 | 0.30012 | 0.55272 | 0.29581 | 0.13226 | 4.0625 | 0 | 8.6272 | 47.1682 | 0% | CZ 0B | 1.0407 | 0.089621 | 0.20343 | 0 | 0 | 6.1687 | 0 | 1.3716 | 0.40166 | 0.08796 | 0.16199 | 0.086696 | 0.038763 | 0.47347 | 0 | 2.5285 | 12.653 | 0% | CZ 0B | 0 | 0 | 0.014978 | 0.00051281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.039961 | 0% | CZ 0B | 10.895 | 0.93824 | 3.7668 | 0.056051 | 0 | 64.5803 | 0 | 14.3588 | 4.205 | 0.92086 | 1.6959 | 0.90762 | 0.40581 | 7.6313 | 0 | 26.4707 | 136.8323 | 0%
CZ 1A | 0.11384 | 0.0095281 | 0.037228 | 0.0002929 | 0 | 0.48531 | 0 | 0.12756 | 0.045467 | 0.0065715 | 0.017184 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 1.1994 | 2.407% | CZ 1A | 3.6539 | 0.30583 | 2.2863 | 0.029888 | 0 | 15.5773 | 0 | 4.0943 | 1.4594 | 0.21093 | 0.55156 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 41.2871 | 2.407% | CZ 1A | 1.0709 | 0.089634 | 0.20343 | 0 | 0 | 4.5654 | 0 | 1.2 | 0.42772 | 0.06182 | 0.16165 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 10.908 | 2.407% | CZ 1A | 0 | 0 | 0.015922 | 0.00029888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.040691 | 2.407% | CZ 1A | 11.2111 | 0.93838 | 3.87 | 0.032668 | 0 | 47.7956 | 0 | 12.5625 | 4.4778 | 0.64719 | 1.6923 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 118.6432 | 2.407%
CZ 1B | 0.11257 | 0.0095113 | 0.037806 | 0.002755 | 0 | 0.55352 | 0 | 0.14257 | 0.035569 | 0.0076009 | 0.017135 | 0.0092157 | 0.0041205 | 0.07431 | 0 | 0.26878 | 1.2755 | 0% | CZ 1B | 3.6132 | 0.30529 | 2.3452 | 0.28113 | 0 | 17.7667 | 0 | 4.5763 | 1.1417 | 0.24397 | 0.54998 | 0.29581 | 0.13226 | 4.0625 | 0 | 8.6272 | 43.9413 | 0% | CZ 1B | 1.059 | 0.089476 | 0.20343 | 0 | 0 | 5.2071 | 0 | 1.3412 | 0.33461 | 0.071504 | 0.16119 | 0.086696 | 0.038763 | 0.47347 | 0 | 2.5285 | 11.595 | 0% | CZ 1B | 0 | 0 | 0.016511 | 0.0028113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.043793 | 0% | CZ 1B | 11.0864 | 0.93672 | 3.9344 | 0.30727 | 0 | 54.5135 | 0 | 14.0414 | 3.503 | 0.74858 | 1.6875 | 0.90762 | 0.40581 | 7.6313 | 0 | 26.4707 | 126.1743 | 0%
CZ 2A | 0.11279 | 0.0095057 | 0.038992 | 0.0030797 | 0 | 0.42295 | 0 | 0.11425 | 0.037112 | 0.0067731 | 0.017125 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 1.119 | 17.03% | CZ 2A | 3.6204 | 0.30511 | 2.4663 | 0.31425 | 0 | 13.5756 | 0 | 3.667 | 1.1912 | 0.2174 | 0.54967 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 39.0248 | 17.03% | CZ 2A | 1.0611 | 0.089423 | 0.20343 | 0 | 0 | 3.9788 | 0 | 1.0747 | 0.34913 | 0.063717 | 0.1611 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 10.1088 | 17.03% | CZ 2A | 0 | 0 | 0.017722 | 0.0031425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.045334 | 17.03% | CZ 2A | 11.1085 | 0.93617 | 4.0667 | 0.34348 | 0 | 41.6539 | 0 | 11.2515 | 3.655 | 0.66706 | 1.6865 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 110.7844 | 17.03%
CZ 2B | 0.11514 | 0.0095155 | 0.039246 | 0.0018702 | 0 | 0.31955 | 0 | 0.12233 | 0.033541 | 0.0043586 | 0.016944 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 1.0189 | 1.76% | CZ 2B | 3.6956 | 0.30543 | 2.4922 | 0.19083 | 0 | 10.2569 | 0 | 3.9267 | 1.0766 | 0.1399 | 0.54387 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 35.7457 | 1.76% | CZ 2B | 1.0831 | 0.089515 | 0.20343 | 0 | 0 | 3.0061 | 0 | 1.1508 | 0.31553 | 0.041003 | 0.1594 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 9.1764 | 1.76% | CZ 2B | 0 | 0 | 0.01798 | 0.0019083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.044359 | 1.76% | CZ 2B | 11.3391 | 0.93713 | 4.095 | 0.20858 | 0 | 31.4711 | 0 | 12.0481 | 3.3033 | 0.42926 | 1.6687 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 100.9159 | 1.76%
CZ 3A | 0.11464 | 0.0095141 | 0.041672 | 0.020175 | 0 | 0.25566 | 0 | 0.10644 | 0.034573 | 0.0044692 | 0.017003 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.96057 | 19.81% | CZ 3A | 3.6796 | 0.30538 | 2.7397 | 2.0587 | 0 | 8.206 | 0 | 3.4165 | 1.1097 | 0.14345 | 0.54576 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 35.3227 | 19.81% | CZ 3A | 1.0784 | 0.089502 | 0.20343 | 0 | 0 | 2.4051 | 0 | 1.0013 | 0.32524 | 0.042043 | 0.15995 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 8.4324 | 19.81% | CZ 3A | 0 | 0 | 0.020456 | 0.020587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.065514 | 19.81% | CZ 3A | 11.2902 | 0.937 | 4.3656 | 2.2501 | 0 | 25.1785 | 0 | 10.4828 | 3.4049 | 0.44015 | 1.6745 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 95.4394 | 19.81%
CZ 3B | 0.11589 | 0.0095127 | 0.041013 | 0.01438 | 0 | 0.23865 | 0 | 0.11581 | 0 | 0.003521 | 0.016924 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.91213 | 7.027% | CZ 3B | 3.7198 | 0.30534 | 2.6725 | 1.4673 | 0 | 7.66 | 0 | 3.7173 | 0 | 0.11302 | 0.54324 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 33.3164 | 7.027% | CZ 3B | 1.0902 | 0.089489 | 0.20343 | 0 | 0 | 2.245 | 0 | 1.0895 | 0 | 0.033124 | 0.15921 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 8.0374 | 7.027% | CZ 3B | 0 | 0 | 0.019784 | 0.014673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.058928 | 7.027% | CZ 3B | 11.4135 | 0.93686 | 4.2921 | 1.6038 | 0 | 23.5031 | 0 | 11.4059 | 0 | 0.34677 | 1.6668 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 90.5844 | 7.027%
CZ 3C | 0.11653 | 0.0095463 | 0.04151 | 0.0079837 | 0 | 0.17825 | 0 | 0.099156 | 0 | 0.0027745 | 0.016987 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.82916 | 1.237% | CZ 3C | 3.7405 | 0.30641 | 2.7232 | 0.81466 | 0 | 5.7213 | 0 | 3.1827 | 0 | 0.089056 | 0.54526 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 30.2409 | 1.237% | CZ 3C | 1.0963 | 0.089805 | 0.20343 | 0 | 0 | 1.6768 | 0 | 0.93279 | 0 | 0.026101 | 0.15981 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 7.3125 | 1.237% | CZ 3C | 0 | 0 | 0.020291 | 0.0081466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.052908 | 1.237% | CZ 3C | 11.4769 | 0.94017 | 4.3475 | 0.89042 | 0 | 17.5546 | 0 | 9.7654 | 0 | 0.27325 | 1.673 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 82.3369 | 1.237%
CZ 4A | 0.11592 | 0.0095631 | 0.04362 | 0.023867 | 0 | 0.18203 | 0 | 0.10752 | 0.037971 | 0.0036345 | 0.016978 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.89753 | 18.1% | CZ 4A | 3.7208 | 0.30695 | 2.9385 | 2.4354 | 0 | 5.8428 | 0 | 3.4513 | 1.2188 | 0.11666 | 0.54495 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 33.694 | 18.1% | CZ 4A | 1.0905 | 0.089963 | 0.20343 | 0 | 0 | 1.7124 | 0 | 1.0115 | 0.3572 | 0.034191 | 0.15971 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 7.7864 | 18.1% | CZ 4A | 0 | 0 | 0.022444 | 0.024354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.071269 | 18.1% | CZ 4A | 11.4164 | 0.94182 | 4.5829 | 2.6619 | 0 | 17.9275 | 0 | 10.5896 | 3.7396 | 0.35794 | 1.6721 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 89.3052 | 18.1%
CZ 4B | 0.11415 | 0.0095127 | 0.043041 | 0.028683 | 0 | 0.17133 | 0 | 0.11644 | 0 | 0.0028081 | 0.016902 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.85929 | 0.6509% | CZ 4B | 3.6641 | 0.30534 | 2.8794 | 2.9269 | 0 | 5.4992 | 0 | 3.7374 | 0 | 0.090135 | 0.54252 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 32.7627 | 0.6509% | CZ 4B | 1.0739 | 0.089489 | 0.20343 | 0 | 0 | 1.6117 | 0 | 1.0954 | 0 | 0.026417 | 0.159 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 7.3867 | 0.6509% | CZ 4B | 0 | 0 | 0.021853 | 0.029269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.075592 | 0.6509% | CZ 4B | 11.2424 | 0.93686 | 4.5182 | 3.1991 | 0 | 16.8731 | 0 | 11.4675 | 0 | 0.27656 | 1.6646 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 85.594 | 0.6509%
CZ 4C | 0.11844 | 0.0095701 | 0.043931 | 0.053677 | 0 | 0.082586 | 0 | 0.10238 | 0 | 0.0032717 | 0.016954 | 0.0092157 | 0.0041233 | 0.07431 | 0 | 0.26878 | 0.78724 | 2.48% | CZ 4C | 3.8016 | 0.30718 | 2.9703 | 5.4773 | 0 | 2.6508 | 0 | 3.2862 | 0 | 0.10502 | 0.54418 | 0.29581 | 0.13235 | 4.0625 | 0 | 8.6272 | 32.2604 | 2.48% | CZ 4C | 1.1142 | 0.090029 | 0.20343 | 0 | 0 | 0.77691 | 0 | 0.96314 | 0 | 0.030778 | 0.15949 | 0.086696 | 0.038789 | 0.47347 | 0 | 2.5285 | 6.4654 | 2.48% | CZ 4C | 0 | 0 | 0.022762 | 0.054773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.102 | 2.48% | CZ 4C | 11.6644 | 0.94251 | 4.6176 | 5.9867 | 0 | 8.1335 | 0 | 10.0831 | 0 | 0.32222 | 1.6697 | 0.90762 | 0.40608 | 7.6313 | 0 | 26.4707 | 78.8353 | 2.48%
CZ 5A | 0.11472 | 0.0095295 | 0.045227 | 0.050701 | 0 | 0.12253 | 0 | 0.10918 | 0.035303 | 0.0020252 | 0.016965 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.8626 | 19.94% | CZ 5A | 3.6822 | 0.30588 | 3.1024 | 5.1736 | 0 | 3.9329 | 0 | 3.5043 | 1.1331 | 0.065005 | 0.54454 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 34.5618 | 19.94% | CZ 5A | 1.0792 | 0.089647 | 0.20344 | 0 | 0 | 1.1527 | 0 | 1.0271 | 0.3321 | 0.019052 | 0.1596 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 7.1902 | 19.94% | CZ 5A | 0 | 0 | 0.024083 | 0.051736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10029 | 19.94% | CZ 5A | 11.2982 | 0.93851 | 4.7621 | 5.6547 | 0 | 12.0672 | 0 | 10.7524 | 3.4768 | 0.19945 | 1.6708 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 86.2356 | 19.94%
CZ 5B | 0.1154 | 0.0095505 | 0.04472 | 0.066964 | 0 | 0.12899 | 0 | 0.11521 | 0 | 0.0027311 | 0.016915 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.8569 | 4.639% | CZ 5B | 3.704 | 0.30655 | 3.0508 | 6.833 | 0 | 4.1402 | 0 | 3.698 | 0 | 0.087663 | 0.54292 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 35.481 | 4.639% | CZ 5B | 1.0856 | 0.089845 | 0.20343 | 0 | 0 | 1.2134 | 0 | 1.0838 | 0 | 0.025692 | 0.15912 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 6.9884 | 4.639% | CZ 5B | 0 | 0 | 0.023567 | 0.06833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11637 | 4.639% | CZ 5B | 11.3651 | 0.94058 | 4.7055 | 7.4685 | 0 | 12.7035 | 0 | 11.3466 | 0 | 0.26897 | 1.6658 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 85.8801 | 4.639%
CZ 5C | 0.11717 | 0.0095631 | 0.044786 | 0.026753 | 0 | 0.054999 | 0 | 0.097849 | 0.034909 | 0.002353 | 0.016951 | 0.0092157 | 0.0041233 | 0.07431 | 0 | 0.26878 | 0.76176 | 0.08039% | CZ 5C | 3.7608 | 0.30695 | 3.0575 | 2.7299 | 0 | 1.7653 | 0 | 3.1408 | 1.1205 | 0.075525 | 0.54409 | 0.29581 | 0.13235 | 4.0625 | 0 | 8.6272 | 29.6192 | 0.08039% | CZ 5C | 1.1022 | 0.089963 | 0.20343 | 0 | 0 | 0.51739 | 0 | 0.9205 | 0.3284 | 0.022135 | 0.15946 | 0.086696 | 0.038789 | 0.47347 | 0 | 2.5285 | 6.471 | 0.08039% | CZ 5C | 0 | 0 | 0.023634 | 0.027299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.075404 | 0.08039% | CZ 5C | 11.5393 | 0.94182 | 4.7129 | 2.9838 | 0 | 5.4166 | 0 | 9.6367 | 3.438 | 0.23173 | 1.6694 | 0.90762 | 0.40608 | 7.6313 | 0 | 26.4707 | 75.986 | 0.08039%
CZ 6A | 0.11571 | 0.0095449 | 0.046531 | 0.097801 | 0 | 0.12982 | 0 | 0.1174 | 0.036716 | 0.0023656 | 0.016954 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.92926 | 3.358% | CZ 6A | 3.7141 | 0.30637 | 3.2355 | 9.9797 | 0 | 4.1669 | 0 | 3.7682 | 1.1785 | 0.075929 | 0.54418 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 40.0871 | 3.358% | CZ 6A | 1.0885 | 0.089792 | 0.20344 | 0 | 0 | 1.2212 | 0 | 1.1044 | 0.3454 | 0.022254 | 0.15949 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 7.362 | 3.358% | CZ 6A | 0 | 0 | 0.025413 | 0.099797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.14968 | 3.358% | CZ 6A | 11.3958 | 0.94003 | 4.9075 | 10.9078 | 0 | 12.7852 | 0 | 11.5619 | 3.616 | 0.23297 | 1.6697 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 93.4326 | 3.358%
CZ 6B | 0.11527 | 0.0095351 | 0.046156 | 0.062476 | 0 | 0.0891 | 0 | 0.11508 | 0.036542 | 0.0014342 | 0.016905 | 0.0092157 | 0.0041233 | 0.07431 | 0 | 0.26878 | 0.84893 | 0.8663% | CZ 6B | 3.7 | 0.30606 | 3.1972 | 6.3751 | 0 | 2.8599 | 0 | 3.6937 | 1.1729 | 0.046034 | 0.54261 | 0.29581 | 0.13235 | 4.0625 | 0 | 8.6272 | 35.0115 | 0.8663% | CZ 6B | 1.0844 | 0.0897 | 0.20344 | 0 | 0 | 0.83819 | 0 | 1.0826 | 0.34377 | 0.013492 | 0.15903 | 0.086696 | 0.038789 | 0.47347 | 0 | 2.5285 | 6.942 | 0.8663% | CZ 6B | 0 | 0 | 0.02503 | 0.063751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11325 | 0.8663% | CZ 6B | 11.3528 | 0.93907 | 4.8657 | 6.968 | 0 | 8.775 | 0 | 11.3335 | 3.5989 | 0.14125 | 1.6649 | 0.90762 | 0.40608 | 7.6313 | 0 | 26.4707 | 85.0548 | 0.8663%
CZ 7 | 0.1131 | 0.0095673 | 0.04794 | 0.11918 | 0 | 0.10539 | 0 | 0.1203 | 0.037087 | 0.0033936 | 0.016943 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.92932 | 0.5534% | CZ 7 | 3.6303 | 0.30709 | 3.3793 | 12.1611 | 0 | 3.3827 | 0 | 3.8613 | 1.1904 | 0.10893 | 0.54382 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 41.6827 | 0.5534% | CZ 7 | 1.064 | 0.090003 | 0.20344 | 0 | 0 | 0.99143 | 0 | 1.1317 | 0.34889 | 0.031925 | 0.15939 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 7.1481 | 0.5534% | CZ 7 | 0 | 0 | 0.026851 | 0.12161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.17293 | 0.5534% | CZ 7 | 11.1387 | 0.94224 | 5.0647 | 13.2921 | 0 | 10.3792 | 0 | 11.8476 | 3.6525 | 0.33422 | 1.6686 | 0.90762 | 0.40594 | 7.6313 | 0 | 26.4707 | 93.7354 | 0.5534%
CZ 8 | 0.12393 | 0.0099328 | 0.04967 | 0.20964 | 0 | 0.050444 | 0 | 0.12481 | 0.035806 | 0.0022367 | 0.01691 | 0.0092157 | 0.0041275 | 0.07431 | 0 | 0.26878 | 0.97981 | 0.05968% | CZ 8 | 3.9779 | 0.31882 | 3.5557 | 21.3919 | 0 | 1.6192 | 0 | 4.0061 | 1.1493 | 0.071793 | 0.54279 | 0.29581 | 0.13248 | 4.0625 | 0 | 8.6272 | 49.7515 | 0.05968% | CZ 8 | 1.1659 | 0.093441 | 0.20346 | 0 | 0 | 0.47455 | 0 | 1.1741 | 0.33683 | 0.021041 | 0.15908 | 0.086696 | 0.038829 | 0.47347 | 0 | 2.5285 | 6.7559 | 0.05968% | CZ 8 | 0 | 0 | 0.028615 | 0.21392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.267 | 0.05968% | CZ 8 | 12.2054 | 0.97824 | 5.2576 | 23.3814 | 0 | 4.968 | 0 | 12.292 | 3.5263 | 0.22028 | 1.6654 | 0.90762 | 0.4065 | 7.6313 | 0 | 26.4707 | 99.9108 | 0.05968%
US Weighted | 0.11484 | 0.0095301 | 0.04253 | 0.029356 | 0 | 0.23127 | 0 | 0.11076 | 0.03057 | 0.0039571 | 0.017 | 0.0092157 | 0.0041219 | 0.07431 | 0 | 0.26878 | 0.94624 | 100% | US Weighted | 3.6861 | 0.3059 | 2.8272 | 2.9956 | 0 | 7.4232 | 0 | 3.5552 | 0.98125 | 0.12701 | 0.54567 | 0.29581 | 0.1323 | 4.0625 | 0 | 8.6272 | 35.5649 | 100% | US Weighted | 1.0803 | 0.089653 | 0.20343 | 0 | 0 | 2.1756 | 0 | 1.042 | 0.28759 | 0.037226 | 0.15993 | 0.086696 | 0.038776 | 0.47347 | 0 | 2.5285 | 8.2032 | 100% | US Weighted | 0 | 0 | 0.021331 | 0.029956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.075757 | 100% | US Weighted | 11.31 | 0.93858 | 4.4612 | 3.2741 | 0 | 22.7765 | 0 | 10.9085 | 3.0107 | 0.38971 | 1.6743 | 0.90762 | 0.40595 | 7.6313 | 0 | 26.4707 | 94.1593 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.13064 | 0.0095323 | 0.035918 | 0.010026 | 0 | 0.80316 | 0 | 0.19382 | 0.05523 | 0.011195 | 0.025685 | 0.0092157 | 0.0041569 | 0.07431 | 0 | 0.26878 | 1.6317 | 0% | CZ 0A | 4.1932 | 0.30597 | 2.1527 | 1.0231 | 0 | 25.7798 | 0 | 6.2212 | 1.7728 | 0.35933 | 0.82443 | 0.29581 | 0.13343 | 4.0625 | 0 | 8.6272 | 55.7514 | 0% | CZ 0A | 1.229 | 0.089673 | 0.20342 | 0 | 0 | 7.5556 | 0 | 1.8233 | 0.51957 | 0.10531 | 0.24163 | 0.086696 | 0.039105 | 0.47347 | 0 | 2.5285 | 14.8953 | 0% | CZ 0A | 0 | 0 | 0.014586 | 0.010231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.049287 | 0% | CZ 0A | 12.8659 | 0.93879 | 3.7239 | 1.1182 | 0 | 79.1 | 0 | 19.0885 | 5.4394 | 1.1025 | 2.5296 | 0.90762 | 0.40939 | 7.6313 | 0 | 26.4707 | 161.3257 | 0%
CZ 0B | 0.1305 | 0.0095267 | 0.036312 | 0.00082101 | 0 | 0.69074 | 0 | 0.15647 | 0.040395 | 0.010464 | 0.025562 | 0.0092157 | 0.0041583 | 0.07431 | 0 | 0.26878 | 1.4573 | 0% | CZ 0B | 4.1887 | 0.30579 | 2.1929 | 0.083776 | 0 | 22.1714 | 0 | 5.0222 | 1.2966 | 0.33586 | 0.82048 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 49.5367 | 0% | CZ 0B | 1.2277 | 0.089621 | 0.20342 | 0 | 0 | 6.4981 | 0 | 1.4719 | 0.38001 | 0.098435 | 0.24047 | 0.086696 | 0.039118 | 0.47347 | 0 | 2.5285 | 13.3374 | 0% | CZ 0B | 0 | 0 | 0.014988 | 0.00083776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.040297 | 0% | CZ 0B | 12.8523 | 0.93824 | 3.7678 | 0.091567 | 0 | 68.0283 | 0 | 15.4096 | 3.9783 | 1.0305 | 2.5175 | 0.90762 | 0.40953 | 7.6313 | 0 | 26.4707 | 144.0333 | 0%
CZ 1A | 0.13283 | 0.0095281 | 0.037235 | 0.00053912 | 0 | 0.51302 | 0 | 0.13778 | 0.043759 | 0.0070238 | 0.025496 | 0.0092157 | 0.0041583 | 0.07431 | 0 | 0.26878 | 1.2637 | 2.407% | CZ 1A | 4.2635 | 0.30583 | 2.2871 | 0.055012 | 0 | 16.467 | 0 | 4.4225 | 1.4046 | 0.22545 | 0.81836 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 43.3682 | 2.407% | CZ 1A | 1.2495 | 0.089634 | 0.20342 | 0 | 0 | 4.8262 | 0 | 1.2962 | 0.41166 | 0.066076 | 0.23985 | 0.086696 | 0.039118 | 0.47347 | 0 | 2.5285 | 11.5103 | 2.407% | CZ 1A | 0 | 0 | 0.015931 | 0.00055012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.040951 | 2.407% | CZ 1A | 13.0815 | 0.93838 | 3.8708 | 0.060128 | 0 | 50.5254 | 0 | 13.5695 | 4.3097 | 0.69175 | 2.511 | 0.90762 | 0.40953 | 7.6313 | 0 | 26.4707 | 124.9773 | 2.407%
CZ 1B | 0.13149 | 0.0095113 | 0.037824 | 0.0060849 | 0 | 0.60614 | 0 | 0.16953 | 0.037286 | 0.0093502 | 0.025416 | 0.0092157 | 0.0041583 | 0.07431 | 0 | 0.26878 | 1.3891 | 0% | CZ 1B | 4.2206 | 0.30529 | 2.3471 | 0.62091 | 0 | 19.4557 | 0 | 5.4415 | 1.1968 | 0.30012 | 0.8158 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 47.8228 | 0% | CZ 1B | 1.237 | 0.089476 | 0.20343 | 0 | 0 | 5.7021 | 0 | 1.5948 | 0.35076 | 0.08796 | 0.2391 | 0.086696 | 0.039118 | 0.47347 | 0 | 2.5285 | 12.6324 | 0% | CZ 1B | 0 | 0 | 0.01653 | 0.0062091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.04721 | 0% | CZ 1B | 12.9499 | 0.93672 | 3.9365 | 0.67865 | 0 | 59.6957 | 0 | 16.6961 | 3.6721 | 0.92086 | 2.5031 | 0.90762 | 0.40953 | 7.6313 | 0 | 26.4707 | 137.4089 | 0%
CZ 2A | 0.13252 | 0.0095057 | 0.039004 | 0.0041138 | 0 | 0.4387 | 0 | 0.12539 | 0.034804 | 0.0068138 | 0.025447 | 0.0092157 | 0.0041583 | 0.07431 | 0 | 0.26878 | 1.1728 | 17.03% | CZ 2A | 4.2537 | 0.30511 | 2.4675 | 0.41978 | 0 | 14.0815 | 0 | 4.0247 | 1.1171 | 0.21871 | 0.81679 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 40.8237 | 17.03% | CZ 2A | 1.2467 | 0.089423 | 0.20343 | 0 | 0 | 4.127 | 0 | 1.1796 | 0.32741 | 0.064099 | 0.23939 | 0.086696 | 0.039118 | 0.47347 | 0 | 2.5285 | 10.6048 | 17.03% | CZ 2A | 0 | 0 | 0.017734 | 0.0041978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.046402 | 17.03% | CZ 2A | 13.0515 | 0.93617 | 4.068 | 0.45882 | 0 | 43.206 | 0 | 12.3488 | 3.4277 | 0.67106 | 2.5062 | 0.90762 | 0.40953 | 7.6313 | 0 | 26.4707 | 116.0933 | 17.03%
CZ 2B | 0.13501 | 0.0095155 | 0.03926 | 0.0027868 | 0 | 0.33728 | 0 | 0.13682 | 0.028053 | 0.004465 | 0.025116 | 0.0092157 | 0.0041597 | 0.07431 | 0 | 0.26878 | 1.0748 | 1.76% | CZ 2B | 4.3336 | 0.30543 | 2.4936 | 0.28436 | 0 | 10.8258 | 0 | 4.3915 | 0.90045 | 0.14332 | 0.80618 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 37.6032 | 1.76% | CZ 2B | 1.2701 | 0.089515 | 0.20343 | 0 | 0 | 3.1729 | 0 | 1.2871 | 0.26391 | 0.042004 | 0.23628 | 0.086696 | 0.039132 | 0.47347 | 0 | 2.5285 | 9.6929 | 1.76% | CZ 2B | 0 | 0 | 0.017995 | 0.0028436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.045309 | 1.76% | CZ 2B | 13.2967 | 0.93713 | 4.0966 | 0.31081 | 0 | 33.2167 | 0 | 13.4744 | 2.7628 | 0.43974 | 2.4736 | 0.90762 | 0.40967 | 7.6313 | 0 | 26.4707 | 106.4277 | 1.76%
CZ 3A | 0.13435 | 0.0095141 | 0.04169 | 0.024373 | 0 | 0.2694 | 0 | 0.11914 | 0.028493 | 0.0047493 | 0.025233 | 0.0092157 | 0.0041597 | 0.07431 | 0 | 0.26878 | 1.0134 | 19.81% | CZ 3A | 4.3124 | 0.30538 | 2.7416 | 2.4871 | 0 | 8.6472 | 0 | 3.8241 | 0.91457 | 0.15244 | 0.80991 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 37.3136 | 19.81% | CZ 3A | 1.2639 | 0.089502 | 0.20343 | 0 | 0 | 2.5344 | 0 | 1.1208 | 0.26804 | 0.044679 | 0.23737 | 0.086696 | 0.039132 | 0.47347 | 0 | 2.5285 | 8.8898 | 19.81% | CZ 3A | 0 | 0 | 0.020475 | 0.024871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.069816 | 19.81% | CZ 3A | 13.2316 | 0.937 | 4.3676 | 2.7184 | 0 | 26.5322 | 0 | 11.7333 | 2.8062 | 0.46774 | 2.485 | 0.90762 | 0.40967 | 7.6313 | 0 | 26.4707 | 100.6984 | 19.81%
CZ 3B | 0.13551 | 0.0095127 | 0.04103 | 0.015372 | 0 | 0.24973 | 0 | 0.1308 | 0 | 0.0037479 | 0.02509 | 0.0092157 | 0.0041597 | 0.07431 | 0 | 0.26878 | 0.96726 | 7.027% | CZ 3B | 4.3497 | 0.30534 | 2.6743 | 1.5686 | 0 | 8.0156 | 0 | 4.1985 | 0 | 0.1203 | 0.80533 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 35.1566 | 7.027% | CZ 3B | 1.2748 | 0.089489 | 0.20343 | 0 | 0 | 2.3493 | 0 | 1.2305 | 0 | 0.035258 | 0.23603 | 0.086696 | 0.039132 | 0.47347 | 0 | 2.5285 | 8.5466 | 7.027% | CZ 3B | 0 | 0 | 0.019802 | 0.015686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.059958 | 7.027% | CZ 3B | 13.3461 | 0.93686 | 4.294 | 1.7144 | 0 | 24.5943 | 0 | 12.8822 | 0 | 0.36912 | 2.471 | 0.90762 | 0.40967 | 7.6313 | 0 | 26.4707 | 96.0273 | 7.027%
CZ 3C | 0.13557 | 0.0095463 | 0.041525 | 0.0086289 | 0 | 0.18501 | 0 | 0.11025 | 0 | 0.0030602 | 0.025245 | 0.0092157 | 0.0041597 | 0.07431 | 0 | 0.26878 | 0.8753 | 1.237% | CZ 3C | 4.3515 | 0.30641 | 2.7247 | 0.8805 | 0 | 5.9385 | 0 | 3.5387 | 0 | 0.098227 | 0.81032 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 31.7679 | 1.237% | CZ 3C | 1.2754 | 0.089805 | 0.20343 | 0 | 0 | 1.7405 | 0 | 1.0371 | 0 | 0.028789 | 0.23749 | 0.086696 | 0.039132 | 0.47347 | 0 | 2.5285 | 7.7403 | 1.237% | CZ 3C | 0 | 0 | 0.020306 | 0.008805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.053582 | 1.237% | CZ 3C | 13.3517 | 0.94017 | 4.3492 | 0.96239 | 0 | 18.221 | 0 | 10.8577 | 0 | 0.30139 | 2.4863 | 0.90762 | 0.40967 | 7.6313 | 0 | 26.4707 | 86.8892 | 1.237%
CZ 4A | 0.1338 | 0.0095631 | 0.04364 | 0.027503 | 0 | 0.18963 | 0 | 0.12048 | 0.035185 | 0.0037997 | 0.025186 | 0.0092157 | 0.0041597 | 0.07431 | 0 | 0.26878 | 0.94526 | 18.1% | CZ 4A | 4.2948 | 0.30695 | 2.9405 | 2.8065 | 0 | 6.0868 | 0 | 3.8672 | 1.1294 | 0.12196 | 0.80843 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 35.4815 | 18.1% | CZ 4A | 1.2587 | 0.089963 | 0.20343 | 0 | 0 | 1.784 | 0 | 1.1334 | 0.331 | 0.035745 | 0.23694 | 0.086696 | 0.039132 | 0.47347 | 0 | 2.5285 | 8.2009 | 18.1% | CZ 4A | 0 | 0 | 0.022464 | 0.028065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.074999 | 18.1% | CZ 4A | 13.1775 | 0.94182 | 4.585 | 3.0675 | 0 | 18.6762 | 0 | 11.8658 | 3.4652 | 0.37422 | 2.4805 | 0.90762 | 0.40967 | 7.6313 | 0 | 26.4707 | 94.053 | 18.1%
CZ 4B | 0.13253 | 0.0095127 | 0.043059 | 0.031199 | 0 | 0.17888 | 0 | 0.13429 | 0 | 0.0030378 | 0.025045 | 0.0092157 | 0.0041583 | 0.07431 | 0 | 0.26878 | 0.91401 | 0.6509% | CZ 4B | 4.2538 | 0.30534 | 2.8813 | 3.1835 | 0 | 5.7418 | 0 | 4.3103 | 0 | 0.097508 | 0.80389 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 34.6965 | 0.6509% | CZ 4B | 1.2467 | 0.089489 | 0.20343 | 0 | 0 | 1.6828 | 0 | 1.2633 | 0 | 0.028578 | 0.23561 | 0.086696 | 0.039118 | 0.47347 | 0 | 2.5285 | 7.8777 | 0.6509% | CZ 4B | 0 | 0 | 0.021872 | 0.031835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.078178 | 0.6509% | CZ 4B | 13.0519 | 0.93686 | 4.5204 | 3.4796 | 0 | 17.6175 | 0 | 13.2253 | 0 | 0.29918 | 2.4666 | 0.90762 | 0.40953 | 7.6313 | 0 | 26.4707 | 91.0164 | 0.6509%
CZ 4C | 0.13652 | 0.0095701 | 0.043949 | 0.056675 | 0 | 0.084148 | 0 | 0.11014 | 0 | 0.0022787 | 0.025151 | 0.0092157 | 0.0041611 | 0.07431 | 0 | 0.26878 | 0.82489 | 2.48% | CZ 4C | 4.3819 | 0.30718 | 2.9721 | 5.7832 | 0 | 2.701 | 0 | 3.5353 | 0 | 0.073142 | 0.80731 | 0.29581 | 0.13356 | 4.0625 | 0 | 8.6272 | 33.6801 | 2.48% | CZ 4C | 1.2843 | 0.090029 | 0.20343 | 0 | 0 | 0.7916 | 0 | 1.0361 | 0 | 0.021437 | 0.23661 | 0.086696 | 0.039145 | 0.47347 | 0 | 2.5285 | 6.7913 | 2.48% | CZ 4C | 0 | 0 | 0.02278 | 0.057832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10508 | 2.48% | CZ 4C | 13.445 | 0.94251 | 4.6195 | 6.321 | 0 | 8.2873 | 0 | 10.8473 | 0 | 0.22442 | 2.477 | 0.90762 | 0.40981 | 7.6313 | 0 | 26.4707 | 82.5835 | 2.48%
CZ 5A | 0.13275 | 0.0095295 | 0.045249 | 0.054868 | 0 | 0.12727 | 0 | 0.12431 | 0.033087 | 0.0020868 | 0.025174 | 0.0092157 | 0.0041583 | 0.07431 | 0 | 0.26878 | 0.91079 | 19.94% | CZ 5A | 4.2609 | 0.30588 | 3.1047 | 5.5988 | 0 | 4.0852 | 0 | 3.9901 | 1.062 | 0.066983 | 0.80802 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 36.4016 | 19.94% | CZ 5A | 1.2488 | 0.089647 | 0.20343 | 0 | 0 | 1.1973 | 0 | 1.1694 | 0.31126 | 0.019632 | 0.23682 | 0.086696 | 0.039118 | 0.47347 | 0 | 2.5285 | 7.6041 | 19.94% | CZ 5A | 0 | 0 | 0.024106 | 0.055988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10456 | 19.94% | CZ 5A | 13.0735 | 0.93851 | 4.7645 | 6.1195 | 0 | 12.5345 | 0 | 12.2429 | 3.2586 | 0.20552 | 2.4793 | 0.90762 | 0.40953 | 7.6313 | 0 | 26.4707 | 91.0359 | 19.94%
CZ 5B | 0.13309 | 0.0095505 | 0.044744 | 0.071612 | 0 | 0.13485 | 0 | 0.13703 | 0 | 0.002916 | 0.025058 | 0.0092157 | 0.0041583 | 0.07431 | 0 | 0.26878 | 0.91531 | 4.639% | CZ 5B | 4.2718 | 0.30655 | 3.0532 | 7.3074 | 0 | 4.3284 | 0 | 4.3985 | 0 | 0.093597 | 0.80429 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 37.6827 | 4.639% | CZ 5B | 1.252 | 0.089845 | 0.20343 | 0 | 0 | 1.2686 | 0 | 1.2891 | 0 | 0.027432 | 0.23572 | 0.086696 | 0.039118 | 0.47347 | 0 | 2.5285 | 7.4939 | 4.639% | CZ 5B | 0 | 0 | 0.023591 | 0.073074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.12114 | 4.639% | CZ 5B | 13.1072 | 0.94058 | 4.7083 | 7.9869 | 0 | 13.2808 | 0 | 13.4958 | 0 | 0.28718 | 2.4678 | 0.90762 | 0.40953 | 7.6313 | 0 | 26.4707 | 91.6937 | 4.639%
CZ 5C | 0.13492 | 0.0095631 | 0.044809 | 0.028756 | 0 | 0.056458 | 0 | 0.10735 | 0.030248 | 0.0023586 | 0.025151 | 0.0092157 | 0.0041597 | 0.07431 | 0 | 0.26878 | 0.79608 | 0.08039% | CZ 5C | 4.3308 | 0.30695 | 3.0598 | 2.9343 | 0 | 1.8122 | 0 | 3.4456 | 0.9709 | 0.075705 | 0.80731 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 30.8625 | 0.08039% | CZ 5C | 1.2693 | 0.089963 | 0.20343 | 0 | 0 | 0.53112 | 0 | 1.0098 | 0.28455 | 0.022188 | 0.23661 | 0.086696 | 0.039132 | 0.47347 | 0 | 2.5285 | 6.7748 | 0.08039% | CZ 5C | 0 | 0 | 0.023657 | 0.029343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.077471 | 0.08039% | CZ 5C | 13.288 | 0.94182 | 4.7154 | 3.2072 | 0 | 5.5603 | 0 | 10.5721 | 2.979 | 0.23228 | 2.477 | 0.90762 | 0.40967 | 7.6313 | 0 | 26.4707 | 79.3925 | 0.08039%
CZ 6A | 0.13297 | 0.0095449 | 0.046554 | 0.10444 | 0 | 0.13628 | 0 | 0.13587 | 0.033126 | 0.0024188 | 0.025199 | 0.0092157 | 0.0041597 | 0.07431 | 0 | 0.26878 | 0.98287 | 3.358% | CZ 6A | 4.2682 | 0.30637 | 3.2379 | 10.6572 | 0 | 4.3741 | 0 | 4.3611 | 1.0633 | 0.077638 | 0.80883 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 42.2736 | 3.358% | CZ 6A | 1.2509 | 0.089792 | 0.20343 | 0 | 0 | 1.282 | 0 | 1.2782 | 0.31163 | 0.022754 | 0.23706 | 0.086696 | 0.039132 | 0.47347 | 0 | 2.5285 | 7.8035 | 3.358% | CZ 6A | 0 | 0 | 0.025438 | 0.10657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.15648 | 3.358% | CZ 6A | 13.096 | 0.94003 | 4.9101 | 11.6483 | 0 | 13.4211 | 0 | 13.3813 | 3.2625 | 0.23821 | 2.4817 | 0.90762 | 0.40967 | 7.6313 | 0 | 26.4707 | 98.7984 | 3.358%
CZ 6B | 0.13251 | 0.0095351 | 0.046178 | 0.062649 | 0 | 0.09397 | 0 | 0.13431 | 0.035671 | 0.001521 | 0.025052 | 0.0092157 | 0.0041597 | 0.07431 | 0 | 0.26878 | 0.89786 | 0.8663% | CZ 6B | 4.2533 | 0.30606 | 3.1995 | 6.3927 | 0 | 3.0162 | 0 | 4.3112 | 1.145 | 0.048821 | 0.80411 | 0.29581 | 0.13352 | 4.0625 | 0 | 8.6272 | 36.596 | 0.8663% | CZ 6B | 1.2466 | 0.0897 | 0.20343 | 0 | 0 | 0.884 | 0 | 1.2635 | 0.33557 | 0.014309 | 0.23567 | 0.086696 | 0.039132 | 0.47347 | 0 | 2.5285 | 7.4006 | 0.8663% | CZ 6B | 0 | 0 | 0.025054 | 0.063927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11345 | 0.8663% | CZ 6B | 13.0505 | 0.93907 | 4.8681 | 6.9873 | 0 | 9.2546 | 0 | 13.2279 | 3.5131 | 0.1498 | 2.4673 | 0.90762 | 0.40967 | 7.6313 | 0 | 26.4707 | 89.8769 | 0.8663%
CZ 7 | 0.13059 | 0.0095673 | 0.047965 | 0.12949 | 0 | 0.11249 | 0 | 0.14012 | 0.033366 | 0.0036121 | 0.025182 | 0.0092157 | 0.0041583 | 0.07431 | 0 | 0.26878 | 0.98885 | 0.5534% | CZ 7 | 4.1916 | 0.30709 | 3.3819 | 13.2137 | 0 | 3.6106 | 0 | 4.4975 | 1.071 | 0.11594 | 0.80829 | 0.29581 | 0.13347 | 4.0625 | 0 | 8.6272 | 44.3166 | 0.5534% | CZ 7 | 1.2285 | 0.090003 | 0.20343 | 0 | 0 | 1.0582 | 0 | 1.3182 | 0.31388 | 0.03398 | 0.2369 | 0.086696 | 0.039118 | 0.47347 | 0 | 2.5285 | 7.6108 | 0.5534% | CZ 7 | 0 | 0 | 0.026878 | 0.13214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.18349 | 0.5534% | CZ 7 | 12.8611 | 0.94224 | 5.0675 | 14.4425 | 0 | 11.0784 | 0 | 13.7998 | 3.286 | 0.35574 | 2.4801 | 0.90762 | 0.40953 | 7.6313 | 0 | 26.4707 | 99.7326 | 0.5534%
CZ 8 | 0.14025 | 0.0099328 | 0.049693 | 0.22747 | 0 | 0.053796 | 0 | 0.14651 | 0.036151 | 0.002388 | 0.025143 | 0.0092157 | 0.0041625 | 0.07431 | 0 | 0.26878 | 1.0478 | 0.05968% | CZ 8 | 4.5016 | 0.31882 | 3.5581 | 23.2117 | 0 | 1.7267 | 0 | 4.7028 | 1.1604 | 0.076649 | 0.80704 | 0.29581 | 0.13361 | 4.0625 | 0 | 8.6272 | 53.1829 | 0.05968% | CZ 8 | 1.3194 | 0.093441 | 0.20344 | 0 | 0 | 0.50608 | 0 | 1.3783 | 0.34009 | 0.022464 | 0.23653 | 0.086696 | 0.039158 | 0.47347 | 0 | 2.5285 | 7.2275 | 0.05968% | CZ 8 | 0 | 0 | 0.028639 | 0.23212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.28523 | 0.05968% | CZ 8 | 13.8123 | 0.97824 | 5.2602 | 25.3704 | 0 | 5.2981 | 0 | 14.4294 | 3.5604 | 0.23518 | 2.4762 | 0.90762 | 0.40994 | 7.6313 | 0 | 26.4707 | 106.8399 | 0.05968%
US Weighted | 0.1336 | 0.0095301 | 0.042548 | 0.032553 | 0 | 0.2415 | 0 | 0.12447 | 0.027737 | 0.0040832 | 0.025229 | 0.0092157 | 0.0041591 | 0.07431 | 0 | 0.26878 | 0.99771 | 100% | US Weighted | 4.2881 | 0.3059 | 2.8291 | 3.3218 | 0 | 7.7516 | 0 | 3.9952 | 0.8903 | 0.13106 | 0.8098 | 0.29581 | 0.1335 | 4.0625 | 0 | 8.6272 | 37.4418 | 100% | US Weighted | 1.2568 | 0.089653 | 0.20343 | 0 | 0 | 2.2719 | 0 | 1.1709 | 0.26093 | 0.038412 | 0.23734 | 0.086696 | 0.039126 | 0.47347 | 0 | 2.5285 | 8.6571 | 100% | US Weighted | 0 | 0 | 0.02135 | 0.033218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.079038 | 100% | US Weighted | 13.1573 | 0.93858 | 4.4633 | 3.6307 | 0 | 23.7841 | 0 | 12.2584 | 2.7317 | 0.40214 | 2.4847 | 0.90762 | 0.40961 | 7.6313 | 0 | 26.4707 | 99.27 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.24192 | 0.01651 | 0.035928 | 0.0074877 | 0 | 0.92195 | 0 | 0.20015 | 0.057975 | 0.0163 | 0.025682 | 0.0092157 | 0.0057185 | 0.07431 | 0 | 0.26878 | 1.8819 | 0% | CZ 0A | 7.7651 | 0.52993 | 2.1537 | 0.76405 | 0 | 29.5926 | 0 | 6.4243 | 1.8609 | 0.52319 | 0.82434 | 0.29581 | 0.18355 | 4.0625 | 0 | 8.6272 | 63.6072 | 0% | CZ 0A | 2.2758 | 0.15531 | 0.20342 | 0 | 0 | 8.6731 | 0 | 1.8829 | 0.54539 | 0.15334 | 0.2416 | 0.086696 | 0.053796 | 0.47347 | 0 | 2.5285 | 17.2733 | 0% | CZ 0A | 0 | 0 | 0.014597 | 0.0076405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.046707 | 0% | CZ 0A | 23.8256 | 1.626 | 3.725 | 0.83511 | 0 | 90.7986 | 0 | 19.7117 | 5.7097 | 1.6053 | 2.5293 | 0.90762 | 0.56319 | 7.6313 | 0 | 26.4707 | 185.939 | 0%
CZ 0B | 0.24529 | 0.016506 | 0.036318 | 0.00055982 | 0 | 0.7521 | 0 | 0.16807 | 0.042996 | 0.014143 | 0.025559 | 0.0092157 | 0.0057213 | 0.07431 | 0 | 0.26878 | 1.6596 | 0% | CZ 0B | 7.8734 | 0.5298 | 2.1935 | 0.057124 | 0 | 24.1409 | 0 | 5.3948 | 1.3801 | 0.45396 | 0.82039 | 0.29581 | 0.18364 | 4.0625 | 0 | 8.6272 | 56.013 | 0% | CZ 0B | 2.3076 | 0.15527 | 0.20342 | 0 | 0 | 7.0753 | 0 | 1.5811 | 0.40448 | 0.13305 | 0.24044 | 0.086696 | 0.053822 | 0.47347 | 0 | 2.5285 | 15.2431 | 0% | CZ 0B | 0 | 0 | 0.014994 | 0.00057124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.040036 | 0% | CZ 0B | 24.1579 | 1.6256 | 3.7685 | 0.062437 | 0 | 74.0713 | 0 | 16.5527 | 4.2345 | 1.3929 | 2.5172 | 0.90762 | 0.56347 | 7.6313 | 0 | 26.4707 | 163.9559 | 0%
CZ 1A | 0.24997 | 0.016508 | 0.037244 | 0.00015372 | 0 | 0.55566 | 0 | 0.14458 | 0.045552 | 0.0094874 | 0.025502 | 0.0092157 | 0.0057227 | 0.07431 | 0 | 0.26878 | 1.4427 | 2.407% | CZ 1A | 8.0233 | 0.52989 | 2.288 | 0.015686 | 0 | 17.8356 | 0 | 4.6409 | 1.4621 | 0.30453 | 0.81854 | 0.29581 | 0.18369 | 4.0625 | 0 | 8.6272 | 49.0877 | 2.407% | CZ 1A | 2.3515 | 0.1553 | 0.20342 | 0 | 0 | 5.2273 | 0 | 1.3602 | 0.42852 | 0.089252 | 0.2399 | 0.086696 | 0.053836 | 0.47347 | 0 | 2.5285 | 13.1978 | 2.407% | CZ 1A | 0 | 0 | 0.015939 | 0.00015686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.040566 | 2.407% | CZ 1A | 24.6179 | 1.6258 | 3.8717 | 0.017144 | 0 | 54.7247 | 0 | 14.2395 | 4.4862 | 0.93438 | 2.5115 | 0.90762 | 0.5636 | 7.6313 | 0 | 26.4707 | 142.6021 | 2.407%
CZ 1B | 0.24958 | 0.016483 | 0.037822 | 0.0032981 | 0 | 0.64292 | 0 | 0.17529 | 0.038422 | 0.012036 | 0.025418 | 0.0092157 | 0.0057227 | 0.07431 | 0 | 0.26878 | 1.5593 | 0% | CZ 1B | 8.0111 | 0.52908 | 2.347 | 0.33654 | 0 | 20.6364 | 0 | 5.6265 | 1.2333 | 0.38635 | 0.81585 | 0.29581 | 0.18369 | 4.0625 | 0 | 8.6272 | 53.0912 | 0% | CZ 1B | 2.3479 | 0.15506 | 0.20342 | 0 | 0 | 6.0482 | 0 | 1.649 | 0.36145 | 0.11323 | 0.23911 | 0.086696 | 0.053836 | 0.47347 | 0 | 2.5285 | 14.2599 | 0% | CZ 1B | 0 | 0 | 0.01653 | 0.0033654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.044365 | 0% | CZ 1B | 24.5803 | 1.6234 | 3.9363 | 0.36784 | 0 | 63.3183 | 0 | 17.2636 | 3.784 | 1.1854 | 2.5033 | 0.90762 | 0.5636 | 7.6313 | 0 | 26.4707 | 154.1355 | 0%
CZ 2A | 0.25144 | 0.016476 | 0.039009 | 0.0022032 | 0 | 0.46924 | 0 | 0.13485 | 0.0357 | 0.0090463 | 0.025448 | 0.0092157 | 0.0057241 | 0.07431 | 0 | 0.26878 | 1.3414 | 17.03% | CZ 2A | 8.0708 | 0.52885 | 2.468 | 0.22481 | 0 | 15.0616 | 0 | 4.3285 | 1.1459 | 0.29037 | 0.81684 | 0.29581 | 0.18373 | 4.0625 | 0 | 8.6272 | 46.1049 | 17.03% | CZ 2A | 2.3654 | 0.155 | 0.20343 | 0 | 0 | 4.4143 | 0 | 1.2686 | 0.33585 | 0.085101 | 0.2394 | 0.086696 | 0.053849 | 0.47347 | 0 | 2.5285 | 12.2096 | 17.03% | CZ 2A | 0 | 0 | 0.017739 | 0.0022481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.044458 | 17.03% | CZ 2A | 24.7636 | 1.6227 | 4.0686 | 0.24572 | 0 | 46.2134 | 0 | 13.281 | 3.516 | 0.89093 | 2.5063 | 0.90762 | 0.56374 | 7.6313 | 0 | 26.4707 | 132.6815 | 17.03%
CZ 2B | 0.25489 | 0.01649 | 0.039264 | 0.0013077 | 0 | 0.36057 | 0 | 0.14399 | 0.029544 | 0.0057227 | 0.025122 | 0.0092157 | 0.0057255 | 0.07431 | 0 | 0.26878 | 1.2349 | 1.76% | CZ 2B | 8.1814 | 0.5293 | 2.494 | 0.13344 | 0 | 11.5736 | 0 | 4.6219 | 0.94829 | 0.18369 | 0.80636 | 0.29581 | 0.18378 | 4.0625 | 0 | 8.6272 | 42.6412 | 1.76% | CZ 2B | 2.3978 | 0.15513 | 0.20343 | 0 | 0 | 3.392 | 0 | 1.3546 | 0.27793 | 0.053836 | 0.23633 | 0.086696 | 0.053862 | 0.47347 | 0 | 2.5285 | 11.2136 | 1.76% | CZ 2B | 0 | 0 | 0.017999 | 0.0013344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.043804 | 1.76% | CZ 2B | 25.1029 | 1.6241 | 4.097 | 0.14585 | 0 | 35.5112 | 0 | 14.1813 | 2.9096 | 0.5636 | 2.4741 | 0.90762 | 0.56388 | 7.6313 | 0 | 26.4707 | 122.1832 | 1.76%
CZ 3A | 0.25505 | 0.016487 | 0.04169 | 0.01715 | 0 | 0.28679 | 0 | 0.12517 | 0.030423 | 0.0058824 | 0.025228 | 0.0092157 | 0.0057269 | 0.07431 | 0 | 0.26878 | 1.1619 | 19.81% | CZ 3A | 8.1866 | 0.52921 | 2.7415 | 1.75 | 0 | 9.2053 | 0 | 4.0178 | 0.97652 | 0.18881 | 0.80978 | 0.29581 | 0.18382 | 4.0625 | 0 | 8.6272 | 41.575 | 19.81% | CZ 3A | 2.3993 | 0.1551 | 0.20343 | 0 | 0 | 2.6979 | 0 | 1.1776 | 0.2862 | 0.055338 | 0.23733 | 0.086696 | 0.053875 | 0.47347 | 0 | 2.5285 | 10.3548 | 19.81% | CZ 3A | 0 | 0 | 0.020474 | 0.0175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.062445 | 19.81% | CZ 3A | 25.1188 | 1.6238 | 4.3676 | 1.9128 | 0 | 28.2446 | 0 | 12.3279 | 2.9962 | 0.57933 | 2.4846 | 0.90762 | 0.56402 | 7.6313 | 0 | 26.4707 | 115.2292 | 19.81%
CZ 3B | 0.25376 | 0.016486 | 0.04103 | 0.0131 | 0 | 0.26582 | 0 | 0.13707 | 0 | 0.0045771 | 0.025098 | 0.0092157 | 0.0057255 | 0.07431 | 0 | 0.26878 | 1.115 | 7.027% | CZ 3B | 8.1451 | 0.52917 | 2.6743 | 1.3368 | 0 | 8.5324 | 0 | 4.3996 | 0 | 0.14691 | 0.8056 | 0.29581 | 0.18378 | 4.0625 | 0 | 8.6272 | 39.7391 | 7.027% | CZ 3B | 2.3872 | 0.15509 | 0.20343 | 0 | 0 | 2.5007 | 0 | 1.2894 | 0 | 0.043058 | 0.23611 | 0.086696 | 0.053862 | 0.47347 | 0 | 2.5285 | 9.9575 | 7.027% | CZ 3B | 0 | 0 | 0.019802 | 0.013368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.05764 | 7.027% | CZ 3B | 24.9916 | 1.6236 | 4.294 | 1.4611 | 0 | 26.1798 | 0 | 13.4992 | 0 | 0.45077 | 2.4718 | 0.90762 | 0.56388 | 7.6313 | 0 | 26.4707 | 110.5454 | 7.027%
CZ 3C | 0.25338 | 0.016514 | 0.041525 | 0.005437 | 0 | 0.19666 | 0 | 0.11698 | 0 | 0.0037213 | 0.025249 | 0.0092157 | 0.0057255 | 0.07431 | 0 | 0.26878 | 1.0175 | 1.237% | CZ 3C | 8.1328 | 0.53007 | 2.7248 | 0.55479 | 0 | 6.3125 | 0 | 3.7548 | 0 | 0.11945 | 0.81045 | 0.29581 | 0.18378 | 4.0625 | 0 | 8.6272 | 36.109 | 1.237% | CZ 3C | 2.3836 | 0.15535 | 0.20343 | 0 | 0 | 1.8501 | 0 | 1.1005 | 0 | 0.035008 | 0.23753 | 0.086696 | 0.053862 | 0.47347 | 0 | 2.5285 | 9.108 | 1.237% | CZ 3C | 0 | 0 | 0.020307 | 0.0055479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.050325 | 1.237% | CZ 3C | 24.9539 | 1.6264 | 4.3493 | 0.60639 | 0 | 19.3686 | 0 | 11.5209 | 0 | 0.36649 | 2.4867 | 0.90762 | 0.56388 | 7.6313 | 0 | 26.4707 | 100.8522 | 1.237%
CZ 4A | 0.2492 | 0.01652 | 0.043639 | 0.020274 | 0 | 0.20476 | 0 | 0.1248 | 0.033818 | 0.0042661 | 0.025182 | 0.0092157 | 0.0057241 | 0.07431 | 0 | 0.26878 | 1.0805 | 18.1% | CZ 4A | 7.9988 | 0.53025 | 2.9404 | 2.0688 | 0 | 6.5725 | 0 | 4.0058 | 1.0855 | 0.13693 | 0.80829 | 0.29581 | 0.18373 | 4.0625 | 0 | 8.6272 | 39.3164 | 18.1% | CZ 4A | 2.3443 | 0.15541 | 0.20343 | 0 | 0 | 1.9263 | 0 | 1.174 | 0.31814 | 0.040133 | 0.2369 | 0.086696 | 0.053849 | 0.47347 | 0 | 2.5285 | 9.5411 | 18.1% | CZ 4A | 0 | 0 | 0.022463 | 0.020688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.067621 | 18.1% | CZ 4A | 24.5426 | 1.6269 | 4.5849 | 2.2612 | 0 | 20.1662 | 0 | 12.2909 | 3.3306 | 0.42015 | 2.4801 | 0.90762 | 0.56374 | 7.6313 | 0 | 26.4707 | 107.2769 | 18.1%
CZ 4B | 0.24699 | 0.01648 | 0.043058 | 0.027854 | 0 | 0.19452 | 0 | 0.14403 | 0 | 0.0036793 | 0.025053 | 0.0092157 | 0.0057227 | 0.07431 | 0 | 0.26878 | 1.0597 | 0.6509% | CZ 4B | 7.9279 | 0.52899 | 2.8812 | 2.8422 | 0 | 6.2437 | 0 | 4.623 | 0 | 0.1181 | 0.80416 | 0.29581 | 0.18369 | 4.0625 | 0 | 8.6272 | 39.1385 | 0.6509% | CZ 4B | 2.3235 | 0.15504 | 0.20343 | 0 | 0 | 1.8299 | 0 | 1.3549 | 0 | 0.034612 | 0.23569 | 0.086696 | 0.053836 | 0.47347 | 0 | 2.5285 | 9.2796 | 0.6509% | CZ 4B | 0 | 0 | 0.021871 | 0.028422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.074764 | 0.6509% | CZ 4B | 24.3252 | 1.6231 | 4.5202 | 3.1066 | 0 | 19.1575 | 0 | 14.1847 | 0 | 0.36236 | 2.4674 | 0.90762 | 0.5636 | 7.6313 | 0 | 26.4707 | 105.3202 | 0.6509%
CZ 4C | 0.25499 | 0.016517 | 0.043947 | 0.047163 | 0 | 0.091881 | 0 | 0.1165 | 0 | 0.0025378 | 0.025146 | 0.0092157 | 0.0057269 | 0.07431 | 0 | 0.26878 | 0.95672 | 2.48% | CZ 4C | 8.1847 | 0.53016 | 2.9719 | 4.8125 | 0 | 2.9492 | 0 | 3.7394 | 0 | 0.081459 | 0.80713 | 0.29581 | 0.18382 | 4.0625 | 0 | 8.6272 | 37.2458 | 2.48% | CZ 4C | 2.3988 | 0.15538 | 0.20343 | 0 | 0 | 0.86436 | 0 | 1.096 | 0 | 0.023874 | 0.23656 | 0.086696 | 0.053875 | 0.47347 | 0 | 2.5285 | 8.1209 | 2.48% | CZ 4C | 0 | 0 | 0.022778 | 0.048125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.095373 | 2.48% | CZ 4C | 25.1131 | 1.6267 | 4.6193 | 5.2601 | 0 | 9.049 | 0 | 11.4736 | 0 | 0.24994 | 2.4765 | 0.90762 | 0.56402 | 7.6313 | 0 | 26.4707 | 95.4418 | 2.48%
CZ 5A | 0.25002 | 0.016492 | 0.045247 | 0.043712 | 0 | 0.13618 | 0 | 0.12608 | 0.033719 | 0.0035084 | 0.025157 | 0.0092157 | 0.0057241 | 0.07431 | 0 | 0.26878 | 1.0381 | 19.94% | CZ 5A | 8.025 | 0.52935 | 3.1045 | 4.4604 | 0 | 4.3712 | 0 | 4.047 | 1.0823 | 0.11261 | 0.80749 | 0.29581 | 0.18373 | 4.0625 | 0 | 8.6272 | 39.709 | 19.94% | CZ 5A | 2.352 | 0.15514 | 0.20343 | 0 | 0 | 1.2811 | 0 | 1.1861 | 0.3172 | 0.033005 | 0.23666 | 0.086696 | 0.053849 | 0.47347 | 0 | 2.5285 | 8.9072 | 19.94% | CZ 5A | 0 | 0 | 0.024104 | 0.044604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.093178 | 19.94% | CZ 5A | 24.623 | 1.6242 | 4.7643 | 4.8752 | 0 | 13.412 | 0 | 12.4174 | 3.3208 | 0.34553 | 2.4776 | 0.90762 | 0.56374 | 7.6313 | 0 | 26.4707 | 103.4334 | 19.94%
CZ 5B | 0.24869 | 0.01651 | 0.044739 | 0.063142 | 0 | 0.14507 | 0 | 0.14226 | 0 | 0.0033193 | 0.025053 | 0.0092157 | 0.0057241 | 0.07431 | 0 | 0.26878 | 1.0468 | 4.639% | CZ 5B | 7.9825 | 0.52993 | 3.0527 | 6.443 | 0 | 4.6564 | 0 | 4.5662 | 0 | 0.10654 | 0.80416 | 0.29581 | 0.18373 | 4.0625 | 0 | 8.6272 | 41.3107 | 4.639% | CZ 5B | 2.3395 | 0.15531 | 0.20343 | 0 | 0 | 1.3647 | 0 | 1.3383 | 0 | 0.031226 | 0.23569 | 0.086696 | 0.053849 | 0.47347 | 0 | 2.5285 | 8.8107 | 4.639% | CZ 5B | 0 | 0 | 0.023586 | 0.06443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11249 | 4.639% | CZ 5B | 24.4927 | 1.626 | 4.7077 | 7.0422 | 0 | 14.2872 | 0 | 14.0104 | 0 | 0.32691 | 2.4674 | 0.90762 | 0.56374 | 7.6313 | 0 | 26.4707 | 104.5338 | 4.639%
CZ 5C | 0.25332 | 0.016508 | 0.044802 | 0.018143 | 0 | 0.061334 | 0 | 0.11294 | 0.024391 | 0.0019664 | 0.025146 | 0.0092157 | 0.0057269 | 0.07431 | 0 | 0.26878 | 0.91658 | 0.08039% | CZ 5C | 8.1311 | 0.52989 | 3.0591 | 1.8513 | 0 | 1.9687 | 0 | 3.6252 | 0.78289 | 0.063117 | 0.80713 | 0.29581 | 0.18382 | 4.0625 | 0 | 8.6272 | 33.9878 | 0.08039% | CZ 5C | 2.3831 | 0.1553 | 0.20343 | 0 | 0 | 0.57699 | 0 | 1.0625 | 0.22945 | 0.018499 | 0.23656 | 0.086696 | 0.053875 | 0.47347 | 0 | 2.5285 | 8.0083 | 0.08039% | CZ 5C | 0 | 0 | 0.02365 | 0.018513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.066634 | 0.08039% | CZ 5C | 24.9485 | 1.6258 | 4.7147 | 2.0235 | 0 | 6.0405 | 0 | 11.1231 | 2.4021 | 0.19366 | 2.4765 | 0.90762 | 0.56402 | 7.6313 | 0 | 26.4707 | 91.1221 | 0.08039%
CZ 6A | 0.25069 | 0.016501 | 0.046553 | 0.09437 | 0 | 0.14381 | 0 | 0.13811 | 0.033733 | 0.0040869 | 0.025189 | 0.0092157 | 0.0057241 | 0.07431 | 0 | 0.26878 | 1.1111 | 3.358% | CZ 6A | 8.0467 | 0.52966 | 3.2378 | 9.6296 | 0 | 4.616 | 0 | 4.433 | 1.0827 | 0.13118 | 0.80852 | 0.29581 | 0.18373 | 4.0625 | 0 | 8.6272 | 45.6844 | 3.358% | CZ 6A | 2.3583 | 0.15524 | 0.20343 | 0 | 0 | 1.3529 | 0 | 1.2992 | 0.31733 | 0.038446 | 0.23696 | 0.086696 | 0.053849 | 0.47347 | 0 | 2.5285 | 9.1044 | 3.358% | CZ 6A | 0 | 0 | 0.025437 | 0.096296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.1462 | 3.358% | CZ 6A | 24.6895 | 1.6252 | 4.91 | 10.5251 | 0 | 14.1634 | 0 | 13.6017 | 3.3222 | 0.4025 | 2.4808 | 0.90762 | 0.56374 | 7.6313 | 0 | 26.4707 | 111.2936 | 3.358%
CZ 6B | 0.25121 | 0.016482 | 0.046176 | 0.054667 | 0 | 0.099447 | 0 | 0.13729 | 0.033604 | 0.0026821 | 0.025046 | 0.0092157 | 0.0057255 | 0.07431 | 0 | 0.26878 | 1.0246 | 0.8663% | CZ 6B | 8.0632 | 0.52903 | 3.1993 | 5.5783 | 0 | 3.192 | 0 | 4.4068 | 1.0786 | 0.086089 | 0.80393 | 0.29581 | 0.18378 | 4.0625 | 0 | 8.6272 | 40.1065 | 0.8663% | CZ 6B | 2.3632 | 0.15505 | 0.20343 | 0 | 0 | 0.93553 | 0 | 1.2916 | 0.31612 | 0.025231 | 0.23562 | 0.086696 | 0.053862 | 0.47347 | 0 | 2.5285 | 8.6682 | 0.8663% | CZ 6B | 0 | 0 | 0.025052 | 0.055783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10531 | 0.8663% | CZ 6B | 24.7401 | 1.6232 | 4.8679 | 6.0971 | 0 | 9.7941 | 0 | 13.5213 | 3.3095 | 0.26415 | 2.4667 | 0.90762 | 0.56388 | 7.6313 | 0 | 26.4707 | 102.2575 | 0.8663%
CZ 7 | 0.24702 | 0.016508 | 0.047965 | 0.11707 | 0 | 0.11804 | 0 | 0.14245 | 0.032841 | 0.0037549 | 0.025168 | 0.0092157 | 0.0057227 | 0.07431 | 0 | 0.26878 | 1.1089 | 0.5534% | CZ 7 | 7.9289 | 0.52989 | 3.3819 | 11.9461 | 0 | 3.7889 | 0 | 4.5724 | 1.0541 | 0.12052 | 0.80785 | 0.29581 | 0.18369 | 4.0625 | 0 | 8.6272 | 47.2997 | 0.5534% | CZ 7 | 2.3238 | 0.1553 | 0.20343 | 0 | 0 | 1.1105 | 0 | 1.3401 | 0.30894 | 0.035324 | 0.23677 | 0.086696 | 0.053836 | 0.47347 | 0 | 2.5285 | 8.8566 | 0.5534% | CZ 7 | 0 | 0 | 0.026878 | 0.11946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.17081 | 0.5534% | CZ 7 | 24.3282 | 1.6258 | 5.0674 | 13.0571 | 0 | 11.6253 | 0 | 14.0294 | 3.2343 | 0.36981 | 2.4787 | 0.90762 | 0.5636 | 7.6313 | 0 | 26.4707 | 111.3894 | 0.5534%
CZ 8 | 0.26127 | 0.016618 | 0.049693 | 0.22546 | 0 | 0.05647 | 0 | 0.15432 | 0.034542 | 0.0037395 | 0.025137 | 0.0092157 | 0.0057325 | 0.07431 | 0 | 0.26878 | 1.1853 | 0.05968% | CZ 8 | 8.3863 | 0.53339 | 3.5582 | 23.0064 | 0 | 1.8125 | 0 | 4.9534 | 1.1087 | 0.12003 | 0.80686 | 0.29581 | 0.184 | 4.0625 | 0 | 8.6272 | 57.4553 | 0.05968% | CZ 8 | 2.4579 | 0.15633 | 0.20343 | 0 | 0 | 0.53123 | 0 | 1.4518 | 0.32495 | 0.035179 | 0.23648 | 0.086696 | 0.053928 | 0.47347 | 0 | 2.5285 | 8.5398 | 0.05968% | CZ 8 | 0 | 0 | 0.028641 | 0.23006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.28318 | 0.05968% | CZ 8 | 25.7315 | 1.6366 | 5.2602 | 25.146 | 0 | 5.5614 | 0 | 15.1984 | 3.4019 | 0.36829 | 2.4757 | 0.90762 | 0.56457 | 7.6313 | 0 | 26.4707 | 120.3541 | 0.05968%
US Weighted | 0.25157 | 0.016495 | 0.042548 | 0.025893 | 0 | 0.25848 | 0 | 0.12981 | 0.028214 | 0.0053003 | 0.025224 | 0.0092157 | 0.0057249 | 0.07431 | 0 | 0.26878 | 1.1416 | 100% | US Weighted | 8.0747 | 0.52947 | 2.8291 | 2.6421 | 0 | 8.2965 | 0 | 4.1667 | 0.9056 | 0.17013 | 0.80965 | 0.29581 | 0.18376 | 4.0625 | 0 | 8.6272 | 41.5932 | 100% | US Weighted | 2.3666 | 0.15518 | 0.20343 | 0 | 0 | 2.4316 | 0 | 1.2212 | 0.26542 | 0.049862 | 0.23729 | 0.086696 | 0.053856 | 0.47347 | 0 | 2.5285 | 10.073 | 100% | US Weighted | 0 | 0 | 0.02135 | 0.026421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.072242 | 100% | US Weighted | 24.7756 | 1.6246 | 4.4633 | 2.8878 | 0 | 25.456 | 0 | 12.7845 | 2.7786 | 0.522 | 2.4842 | 0.90762 | 0.56381 | 7.6313 | 0 | 26.4707 | 113.3502 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.28385 | 0.01651 | 0.035998 | 0.011485 | 0 | 1.3336 | 0 | 0.23441 | 0.076498 | 0.023978 | 0.030311 | 0.0092395 | 0.0062059 | 0.07431 | 0 | 0.29592 | 2.4323 | 0% | CZ 0A | 9.1109 | 0.52993 | 2.1598 | 1.1719 | 0 | 42.8044 | 0 | 7.5239 | 2.4554 | 0.76963 | 0.97292 | 0.29657 | 0.1992 | 4.0625 | 0 | 9.4984 | 81.5556 | 0% | CZ 0A | 2.6703 | 0.15531 | 0.20356 | 0 | 0 | 12.5453 | 0 | 2.2051 | 0.71964 | 0.22557 | 0.28515 | 0.08692 | 0.058381 | 0.47347 | 0 | 2.7838 | 22.4125 | 0% | CZ 0A | 0 | 0 | 0.014652 | 0.011719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.050842 | 0% | CZ 0A | 27.955 | 1.626 | 3.7326 | 1.2809 | 0 | 131.3363 | 0 | 23.0856 | 7.5339 | 2.3615 | 2.9852 | 0.90996 | 0.61119 | 7.6313 | 0 | 29.1439 | 240.1933 | 0%
CZ 0B | 0.28572 | 0.016506 | 0.03632 | 0.0030841 | 0 | 0.89115 | 0 | 0.19922 | 0.050271 | 0.016284 | 0.031093 | 0.0092395 | 0.0062073 | 0.07431 | 0 | 0.29592 | 1.9153 | 0% | CZ 0B | 9.1709 | 0.5298 | 2.1938 | 0.3147 | 0 | 28.6041 | 0 | 6.3945 | 1.6136 | 0.52269 | 0.99801 | 0.29657 | 0.19924 | 4.0625 | 0 | 9.4984 | 64.3988 | 0% | CZ 0B | 2.6878 | 0.15527 | 0.20342 | 0 | 0 | 8.3834 | 0 | 1.8741 | 0.47291 | 0.15319 | 0.2925 | 0.08692 | 0.058394 | 0.47347 | 0 | 2.7838 | 17.6252 | 0% | CZ 0B | 0 | 0 | 0.014997 | 0.003147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.042614 | 0% | CZ 0B | 28.139 | 1.6256 | 3.7688 | 0.34397 | 0 | 87.7658 | 0 | 19.6201 | 4.9509 | 1.6038 | 3.0622 | 0.90996 | 0.61133 | 7.6313 | 0 | 29.1439 | 189.1765 | 0%
CZ 1A | 0.28853 | 0.016508 | 0.037319 | 0.0021045 | 0 | 0.8067 | 0 | 0.21018 | 0.073177 | 0.015017 | 0.029878 | 0.0092395 | 0.0062087 | 0.07431 | 0 | 0.29592 | 1.8651 | 2.407% | CZ 1A | 9.2613 | 0.52989 | 2.2943 | 0.21474 | 0 | 25.8932 | 0 | 6.7464 | 2.3488 | 0.48201 | 0.95903 | 0.29657 | 0.19929 | 4.0625 | 0 | 9.4984 | 62.7864 | 2.407% | CZ 1A | 2.7143 | 0.1553 | 0.2036 | 0 | 0 | 7.5889 | 0 | 1.9773 | 0.6884 | 0.14127 | 0.28108 | 0.08692 | 0.058408 | 0.47347 | 0 | 2.7838 | 17.1527 | 2.407% | CZ 1A | 0 | 0 | 0.015996 | 0.0021474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.042614 | 2.407% | CZ 1A | 28.4162 | 1.6258 | 3.8798 | 0.23472 | 0 | 79.4478 | 0 | 20.7 | 7.2069 | 1.4789 | 2.9426 | 0.90996 | 0.61147 | 7.6313 | 0 | 29.1439 | 184.2295 | 2.407%
CZ 1B | 0.28835 | 0.016483 | 0.037829 | 0.0080467 | 0 | 0.74504 | 0 | 0.19421 | 0.039044 | 0.013395 | 0.030957 | 0.0092395 | 0.0062087 | 0.07431 | 0 | 0.29592 | 1.759 | 0% | CZ 1B | 9.2553 | 0.52908 | 2.3476 | 0.82109 | 0 | 23.9142 | 0 | 6.2337 | 1.2532 | 0.42995 | 0.99365 | 0.29657 | 0.19929 | 4.0625 | 0 | 9.4984 | 59.8346 | 0% | CZ 1B | 2.7126 | 0.15506 | 0.20343 | 0 | 0 | 7.0088 | 0 | 1.827 | 0.3673 | 0.12601 | 0.29122 | 0.08692 | 0.058408 | 0.47347 | 0 | 2.7838 | 16.0941 | 0% | CZ 1B | 0 | 0 | 0.016535 | 0.0082109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.049216 | 0% | CZ 1B | 28.398 | 1.6234 | 3.937 | 0.89745 | 0 | 73.3756 | 0 | 19.1267 | 3.8452 | 1.3192 | 3.0488 | 0.90996 | 0.61147 | 7.6313 | 0 | 29.1439 | 173.868 | 0%
CZ 2A | 0.28958 | 0.016476 | 0.039075 | 0.0069526 | 0 | 0.63549 | 0 | 0.18461 | 0.034908 | 0.013754 | 0.02987 | 0.0092395 | 0.0062101 | 0.07431 | 0 | 0.29592 | 1.6364 | 17.03% | CZ 2A | 9.2949 | 0.52885 | 2.4735 | 0.70945 | 0 | 20.3979 | 0 | 5.9255 | 1.1205 | 0.44146 | 0.95876 | 0.29657 | 0.19933 | 4.0625 | 0 | 9.4984 | 55.9075 | 17.03% | CZ 2A | 2.7242 | 0.155 | 0.2036 | 0 | 0 | 5.9783 | 0 | 1.7367 | 0.32839 | 0.12938 | 0.281 | 0.08692 | 0.058421 | 0.47347 | 0 | 2.7838 | 14.9391 | 17.03% | CZ 2A | 0 | 0 | 0.017788 | 0.0070945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.049352 | 17.03% | CZ 2A | 28.5194 | 1.6227 | 4.0757 | 0.77542 | 0 | 62.5866 | 0 | 18.1811 | 3.4379 | 1.3545 | 2.9418 | 0.90996 | 0.61161 | 7.6313 | 0 | 29.1439 | 161.7919 | 17.03%
CZ 2B | 0.29195 | 0.01649 | 0.039269 | 0.0038051 | 0 | 0.41176 | 0 | 0.16676 | 0.02701 | 0.0064902 | 0.030658 | 0.0092395 | 0.0062115 | 0.07431 | 0 | 0.29592 | 1.3799 | 1.76% | CZ 2B | 9.3709 | 0.5293 | 2.4945 | 0.38827 | 0 | 13.2165 | 0 | 5.3527 | 0.86696 | 0.20832 | 0.98407 | 0.29657 | 0.19938 | 4.0625 | 0 | 9.4984 | 47.4684 | 1.76% | CZ 2B | 2.7465 | 0.15513 | 0.20343 | 0 | 0 | 3.8735 | 0 | 1.5688 | 0.25409 | 0.061056 | 0.28841 | 0.08692 | 0.058434 | 0.47347 | 0 | 2.7838 | 12.5535 | 1.76% | CZ 2B | 0 | 0 | 0.018004 | 0.0038827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.046357 | 1.76% | CZ 2B | 28.7527 | 1.6241 | 4.0976 | 0.42438 | 0 | 40.5519 | 0 | 16.4237 | 2.6601 | 0.63919 | 3.0194 | 0.90996 | 0.61174 | 7.6313 | 0 | 29.1439 | 136.4899 | 1.76%
CZ 3A | 0.2921 | 0.016487 | 0.041748 | 0.026077 | 0 | 0.37128 | 0 | 0.15654 | 0.033967 | 0.0088012 | 0.029611 | 0.0092395 | 0.0062115 | 0.07431 | 0 | 0.29592 | 1.3623 | 19.81% | CZ 3A | 9.3758 | 0.52921 | 2.7461 | 2.6609 | 0 | 11.9172 | 0 | 5.0245 | 1.0903 | 0.2825 | 0.95044 | 0.29657 | 0.19938 | 4.0625 | 0 | 9.4984 | 48.6336 | 19.81% | CZ 3A | 2.7479 | 0.1551 | 0.20362 | 0 | 0 | 3.4927 | 0 | 1.4726 | 0.31954 | 0.082796 | 0.27856 | 0.08692 | 0.058434 | 0.47347 | 0 | 2.7838 | 12.1554 | 19.81% | CZ 3A | 0 | 0 | 0.020513 | 0.026609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.071593 | 19.81% | CZ 3A | 28.7676 | 1.6238 | 4.3738 | 2.9083 | 0 | 36.5653 | 0 | 15.4165 | 3.3452 | 0.86679 | 2.9162 | 0.90996 | 0.61174 | 7.6313 | 0 | 29.1439 | 135.0804 | 19.81%
CZ 3B | 0.29131 | 0.016486 | 0.041035 | 0.0058417 | 0 | 0.2915 | 0 | 0.1542 | 0.030072 | 0.00493 | 0.030635 | 0.0092395 | 0.0062101 | 0.07431 | 0 | 0.29592 | 1.2517 | 7.027% | CZ 3B | 9.3505 | 0.52917 | 2.6748 | 0.5961 | 0 | 9.3564 | 0 | 4.9494 | 0.96523 | 0.15824 | 0.98331 | 0.29657 | 0.19933 | 4.0625 | 0 | 9.4984 | 43.6199 | 7.027% | CZ 3B | 2.7405 | 0.15509 | 0.20343 | 0 | 0 | 2.7422 | 0 | 1.4506 | 0.28289 | 0.046378 | 0.28819 | 0.08692 | 0.058421 | 0.47347 | 0 | 2.7838 | 11.3119 | 7.027% | CZ 3B | 0 | 0 | 0.019807 | 0.005961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.050238 | 7.027% | CZ 3B | 28.6899 | 1.6236 | 4.2946 | 0.65153 | 0 | 28.7081 | 0 | 15.1862 | 2.9616 | 0.48553 | 3.0171 | 0.90996 | 0.61161 | 7.6313 | 0 | 29.1439 | 123.9149 | 7.027%
CZ 3C | 0.29119 | 0.016514 | 0.041579 | 0.0068649 | 0 | 0.23483 | 0 | 0.14322 | 0.029199 | 0.0052003 | 0.029611 | 0.0092395 | 0.0062101 | 0.07431 | 0 | 0.29592 | 1.1839 | 1.237% | CZ 3C | 9.3467 | 0.53007 | 2.7289 | 0.7005 | 0 | 7.5374 | 0 | 4.5972 | 0.93723 | 0.16692 | 0.95044 | 0.29657 | 0.19933 | 4.0625 | 0 | 9.4984 | 41.5522 | 1.237% | CZ 3C | 2.7394 | 0.15535 | 0.20362 | 0 | 0 | 2.2091 | 0 | 1.3474 | 0.27469 | 0.048921 | 0.27856 | 0.08692 | 0.058421 | 0.47347 | 0 | 2.7838 | 10.6596 | 1.237% | CZ 3C | 0 | 0 | 0.020342 | 0.007005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.051817 | 1.237% | CZ 3C | 28.6785 | 1.6264 | 4.355 | 0.76565 | 0 | 23.127 | 0 | 14.1054 | 2.8757 | 0.51215 | 2.9162 | 0.90996 | 0.61161 | 7.6313 | 0 | 29.1439 | 117.2587 | 1.237%
CZ 4A | 0.28772 | 0.01652 | 0.043697 | 0.034195 | 0 | 0.26015 | 0 | 0.15528 | 0.033853 | 0.0066387 | 0.02956 | 0.0092395 | 0.0062087 | 0.07431 | 0 | 0.29592 | 1.2533 | 18.1% | CZ 4A | 9.2353 | 0.53025 | 2.945 | 3.4893 | 0 | 8.3504 | 0 | 4.9841 | 1.0866 | 0.21309 | 0.94882 | 0.29657 | 0.19929 | 4.0625 | 0 | 9.4984 | 45.8396 | 18.1% | CZ 4A | 2.7067 | 0.15541 | 0.20362 | 0 | 0 | 2.4474 | 0 | 1.4608 | 0.31847 | 0.062452 | 0.27808 | 0.08692 | 0.058408 | 0.47347 | 0 | 2.7838 | 11.0355 | 18.1% | CZ 4A | 0 | 0 | 0.022502 | 0.034893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.081865 | 18.1% | CZ 4A | 28.3367 | 1.6269 | 4.5912 | 3.8138 | 0 | 25.6214 | 0 | 15.2928 | 3.334 | 0.65381 | 2.9113 | 0.90996 | 0.61147 | 7.6313 | 0 | 29.1439 | 124.4784 | 18.1%
CZ 4B | 0.28653 | 0.01648 | 0.043121 | 0.014985 | 0 | 0.24768 | 0 | 0.19213 | 0.030733 | 0.0054972 | 0.02942 | 0.0092395 | 0.0062087 | 0.07431 | 0 | 0.29592 | 1.2522 | 0.6509% | CZ 4B | 9.1968 | 0.52899 | 2.8862 | 1.5291 | 0 | 7.95 | 0 | 6.1669 | 0.98645 | 0.17645 | 0.94433 | 0.29657 | 0.19929 | 4.0625 | 0 | 9.4984 | 44.422 | 0.6509% | CZ 4B | 2.6954 | 0.15504 | 0.20362 | 0 | 0 | 2.33 | 0 | 1.8074 | 0.28911 | 0.051714 | 0.27677 | 0.08692 | 0.058408 | 0.47347 | 0 | 2.7838 | 11.2117 | 0.6509% | CZ 4B | 0 | 0 | 0.021915 | 0.015291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.061676 | 0.6509% | CZ 4B | 28.2186 | 1.6231 | 4.5269 | 1.6713 | 0 | 24.3928 | 0 | 18.9219 | 3.0267 | 0.5414 | 2.8975 | 0.90996 | 0.61147 | 7.6313 | 0 | 29.1439 | 124.1167 | 0.6509%
CZ 4C | 0.29142 | 0.016517 | 0.043999 | 0.029178 | 0 | 0.10775 | 0 | 0.13987 | 0.032941 | 0.0027731 | 0.029527 | 0.0092395 | 0.0062115 | 0.07431 | 0 | 0.29592 | 1.0797 | 2.48% | CZ 4C | 9.3539 | 0.53016 | 2.9757 | 2.9774 | 0 | 3.4584 | 0 | 4.4896 | 1.0573 | 0.089011 | 0.94775 | 0.29657 | 0.19938 | 4.0625 | 0 | 9.4984 | 39.9362 | 2.48% | CZ 4C | 2.7415 | 0.15538 | 0.20363 | 0 | 0 | 1.0136 | 0 | 1.3158 | 0.30989 | 0.026088 | 0.27777 | 0.08692 | 0.058434 | 0.47347 | 0 | 2.7838 | 9.4463 | 2.48% | CZ 4C | 0 | 0 | 0.022809 | 0.029774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.077053 | 2.48% | CZ 4C | 28.7005 | 1.6267 | 4.6248 | 3.2543 | 0 | 10.6115 | 0 | 13.7753 | 3.2442 | 0.27311 | 2.908 | 0.90996 | 0.61174 | 7.6313 | 0 | 29.1439 | 107.3154 | 2.48%
CZ 5A | 0.28801 | 0.016492 | 0.045301 | 0.063676 | 0 | 0.1714 | 0 | 0.15347 | 0.033972 | 0.0050897 | 0.029504 | 0.0092395 | 0.0062087 | 0.07431 | 0 | 0.29592 | 1.1926 | 19.94% | CZ 5A | 9.2444 | 0.52935 | 3.1086 | 6.4975 | 0 | 5.5015 | 0 | 4.9259 | 1.0904 | 0.16337 | 0.94703 | 0.29657 | 0.19929 | 4.0625 | 0 | 9.4984 | 46.0648 | 19.94% | CZ 5A | 2.7094 | 0.15514 | 0.20363 | 0 | 0 | 1.6124 | 0 | 1.4437 | 0.31959 | 0.04788 | 0.27756 | 0.08692 | 0.058408 | 0.47347 | 0 | 2.7838 | 10.1719 | 19.94% | CZ 5A | 0 | 0 | 0.024138 | 0.064975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11358 | 19.94% | CZ 5A | 28.3644 | 1.6242 | 4.7701 | 7.1018 | 0 | 16.8803 | 0 | 15.1142 | 3.3458 | 0.50126 | 2.9058 | 0.90996 | 0.61147 | 7.6313 | 0 | 29.1439 | 118.9042 | 19.94%
CZ 5B | 0.28785 | 0.01651 | 0.044799 | 0.04142 | 0 | 0.18082 | 0 | 0.18636 | 0.033558 | 0.0042927 | 0.029412 | 0.0092395 | 0.0062087 | 0.07431 | 0 | 0.29592 | 1.2107 | 4.639% | CZ 5B | 9.2392 | 0.52993 | 3.0574 | 4.2265 | 0 | 5.804 | 0 | 5.9816 | 1.0771 | 0.13779 | 0.94406 | 0.29657 | 0.19929 | 4.0625 | 0 | 9.4984 | 45.0545 | 4.639% | CZ 5B | 2.7079 | 0.15531 | 0.20362 | 0 | 0 | 1.7011 | 0 | 1.7531 | 0.31569 | 0.040383 | 0.27669 | 0.08692 | 0.058408 | 0.47347 | 0 | 2.7838 | 10.5563 | 4.639% | CZ 5B | 0 | 0 | 0.023627 | 0.042265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.090362 | 4.639% | CZ 5B | 28.3487 | 1.626 | 4.7141 | 4.6196 | 0 | 17.8084 | 0 | 18.3533 | 3.3049 | 0.42277 | 2.8966 | 0.90996 | 0.61147 | 7.6313 | 0 | 29.1439 | 120.391 | 4.639%
CZ 5C | 0.29048 | 0.016508 | 0.044851 | 0.031808 | 0 | 0.065872 | 0 | 0.13172 | 0.031857 | 0.0019608 | 0.029532 | 0.0092395 | 0.0062115 | 0.07431 | 0 | 0.29592 | 1.0303 | 0.08039% | CZ 5C | 9.3237 | 0.52989 | 3.0628 | 3.2457 | 0 | 2.1143 | 0 | 4.2279 | 1.0226 | 0.062937 | 0.94793 | 0.29657 | 0.19938 | 4.0625 | 0 | 9.4984 | 38.5946 | 0.08039% | CZ 5C | 2.7326 | 0.1553 | 0.20362 | 0 | 0 | 0.61968 | 0 | 1.2391 | 0.29969 | 0.018446 | 0.27782 | 0.08692 | 0.058434 | 0.47347 | 0 | 2.7838 | 8.9489 | 0.08039% | CZ 5C | 0 | 0 | 0.023681 | 0.032457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.080608 | 0.08039% | CZ 5C | 28.6077 | 1.6258 | 4.72 | 3.5475 | 0 | 6.4874 | 0 | 12.9724 | 3.1375 | 0.19311 | 2.9085 | 0.90996 | 0.61174 | 7.6313 | 0 | 29.1439 | 102.4968 | 0.08039%
CZ 6A | 0.28875 | 0.016501 | 0.046611 | 0.12459 | 0 | 0.18275 | 0 | 0.16815 | 0.035548 | 0.0059384 | 0.029507 | 0.0092395 | 0.0062101 | 0.07431 | 0 | 0.29592 | 1.284 | 3.358% | CZ 6A | 9.2683 | 0.52966 | 3.2422 | 12.7128 | 0 | 5.8659 | 0 | 5.3971 | 1.141 | 0.19061 | 0.94712 | 0.29657 | 0.19933 | 4.0625 | 0 | 9.4984 | 53.3515 | 3.358% | CZ 6A | 2.7164 | 0.15524 | 0.20363 | 0 | 0 | 1.7192 | 0 | 1.5818 | 0.33441 | 0.055865 | 0.27758 | 0.08692 | 0.058421 | 0.47347 | 0 | 2.7838 | 10.4467 | 3.358% | CZ 6A | 0 | 0 | 0.025474 | 0.12713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.17707 | 3.358% | CZ 6A | 28.4378 | 1.6252 | 4.9161 | 13.8951 | 0 | 17.9982 | 0 | 16.56 | 3.5009 | 0.58485 | 2.906 | 0.90996 | 0.61161 | 7.6313 | 0 | 29.1439 | 128.7209 | 3.358%
CZ 6B | 0.28941 | 0.016482 | 0.046233 | 0.083534 | 0 | 0.1244 | 0 | 0.17035 | 0.036341 | 0.0038053 | 0.029395 | 0.0092395 | 0.0062101 | 0.07431 | 0 | 0.29592 | 1.1856 | 0.8663% | CZ 6B | 9.2896 | 0.52903 | 3.2037 | 8.5239 | 0 | 3.9931 | 0 | 5.4679 | 1.1665 | 0.12214 | 0.94352 | 0.29657 | 0.19933 | 4.0625 | 0 | 9.4984 | 47.296 | 0.8663% | CZ 6B | 2.7226 | 0.15505 | 0.20363 | 0 | 0 | 1.1703 | 0 | 1.6025 | 0.34187 | 0.035798 | 0.27653 | 0.08692 | 0.058421 | 0.47347 | 0 | 2.7838 | 9.911 | 0.8663% | CZ 6B | 0 | 0 | 0.025089 | 0.085239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.1348 | 0.8663% | CZ 6B | 28.5031 | 1.6232 | 4.874 | 9.3166 | 0 | 12.2518 | 0 | 16.777 | 3.579 | 0.37477 | 2.895 | 0.90996 | 0.61161 | 7.6313 | 0 | 29.1439 | 118.4913 | 0.8663%
CZ 7 | 0.28573 | 0.016508 | 0.048022 | 0.15912 | 0 | 0.14402 | 0 | 0.17264 | 0.034719 | 0.0051975 | 0.029474 | 0.0092395 | 0.0062087 | 0.07431 | 0 | 0.29592 | 1.2811 | 0.5534% | CZ 7 | 9.1712 | 0.52989 | 3.3863 | 16.2363 | 0 | 4.6228 | 0 | 5.5414 | 1.1144 | 0.16683 | 0.94604 | 0.29657 | 0.19929 | 4.0625 | 0 | 9.4984 | 55.7718 | 0.5534% | CZ 7 | 2.6879 | 0.1553 | 0.20363 | 0 | 0 | 1.3549 | 0 | 1.6241 | 0.32661 | 0.048895 | 0.27727 | 0.08692 | 0.058408 | 0.47347 | 0 | 2.7838 | 10.0812 | 0.5534% | CZ 7 | 0 | 0 | 0.026915 | 0.16236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.21375 | 0.5534% | CZ 7 | 28.1398 | 1.6258 | 5.0736 | 17.7462 | 0 | 14.1841 | 0 | 17.0025 | 3.4193 | 0.51188 | 2.9027 | 0.90996 | 0.61147 | 7.6313 | 0 | 29.1439 | 128.9025 | 0.5534%
CZ 8 | 0.29845 | 0.016618 | 0.049752 | 0.30254 | 0 | 0.065985 | 0 | 0.18699 | 0.038706 | 0.0049216 | 0.029408 | 0.0092395 | 0.0062171 | 0.07431 | 0 | 0.29592 | 1.3791 | 0.05968% | CZ 8 | 9.5796 | 0.53339 | 3.5627 | 30.8709 | 0 | 2.118 | 0 | 6.0019 | 1.2424 | 0.15797 | 0.94392 | 0.29657 | 0.19956 | 4.0625 | 0 | 9.4984 | 69.0679 | 0.05968% | CZ 8 | 2.8076 | 0.15633 | 0.20363 | 0 | 0 | 0.62074 | 0 | 1.7591 | 0.36412 | 0.046299 | 0.27665 | 0.08692 | 0.058487 | 0.47347 | 0 | 2.7838 | 9.6371 | 0.05968% | CZ 8 | 0 | 0 | 0.028679 | 0.30871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.36186 | 0.05968% | CZ 8 | 29.3931 | 1.6366 | 5.2665 | 33.7419 | 0 | 6.4986 | 0 | 18.4155 | 3.812 | 0.48471 | 2.8962 | 0.90996 | 0.6123 | 7.6313 | 0 | 29.1439 | 140.4425 | 0.05968%
US Weighted | 0.28949 | 0.016495 | 0.042602 | 0.034586 | 0 | 0.33387 | 0 | 0.16342 | 0.03461 | 0.007758 | 0.029703 | 0.0092395 | 0.0062098 | 0.07431 | 0 | 0.29592 | 1.3382 | 100% | US Weighted | 9.2919 | 0.52947 | 2.8334 | 3.5292 | 0 | 10.7163 | 0 | 5.2453 | 1.1109 | 0.24901 | 0.95339 | 0.29657 | 0.19932 | 4.0625 | 0 | 9.4984 | 48.5158 | 100% | US Weighted | 2.7233 | 0.15518 | 0.2036 | 0 | 0 | 3.1408 | 0 | 1.5373 | 0.32558 | 0.072982 | 0.27942 | 0.08692 | 0.058418 | 0.47347 | 0 | 2.7838 | 11.8408 | 100% | US Weighted | 0 | 0 | 0.021387 | 0.035292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.081149 | 100% | US Weighted | 28.5104 | 1.6246 | 4.4691 | 3.8574 | 0 | 32.8809 | 0 | 16.0942 | 3.4085 | 0.76405 | 2.9253 | 0.90996 | 0.61158 | 7.6313 | 0 | 29.1439 | 132.8311 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.46148 | 0.030405 | 0.036039 | 0.0063188 | 0 | 1.5617 | 0 | 0.27141 | 0.057457 | 0.066674 | 0.030534 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.9153 | 0% | CZ 0A | 14.8126 | 0.97593 | 2.1637 | 0.64477 | 0 | 50.1269 | 0 | 8.7117 | 1.8442 | 2.1401 | 0.98007 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 96.7012 | 0% | CZ 0A | 4.3413 | 0.28603 | 0.20359 | 0 | 0 | 14.6914 | 0 | 2.5533 | 0.54052 | 0.62723 | 0.28724 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 27.0048 | 0% | CZ 0A | 0 | 0 | 0.014691 | 0.0064477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.045609 | 0% | CZ 0A | 45.4494 | 2.9944 | 3.7371 | 0.70473 | 0 | 153.8039 | 0 | 26.7301 | 5.6587 | 6.5664 | 3.0071 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 287.698 | 0%
CZ 0B | 0.46148 | 0.030411 | 0.036336 | 0.0026432 | 0 | 1.0612 | 0 | 0.22958 | 0.053187 | 0.039948 | 0.031196 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.3393 | 0% | CZ 0B | 14.8126 | 0.97611 | 2.1953 | 0.26971 | 0 | 34.063 | 0 | 7.3691 | 1.7072 | 1.2823 | 1.0013 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 77.9777 | 0% | CZ 0B | 4.3413 | 0.28608 | 0.20342 | 0 | 0 | 9.9833 | 0 | 2.1598 | 0.50034 | 0.37581 | 0.29347 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 21.6177 | 0% | CZ 0B | 0 | 0 | 0.015013 | 0.0026971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.04218 | 0% | CZ 0B | 45.4494 | 2.995 | 3.7705 | 0.29479 | 0 | 104.515 | 0 | 22.6107 | 5.2381 | 3.9343 | 3.0724 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 230.9263 | 0%
CZ 1A | 0.46148 | 0.030415 | 0.037357 | 0.0036716 | 0 | 1.0054 | 0 | 0.26954 | 0.067171 | 0.043911 | 0.029871 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.3421 | 2.407% | CZ 1A | 14.8126 | 0.97625 | 2.298 | 0.37466 | 0 | 32.2704 | 0 | 8.6515 | 2.1561 | 1.4094 | 0.9588 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 78.2088 | 2.407% | CZ 1A | 4.3413 | 0.28612 | 0.20362 | 0 | 0 | 9.4579 | 0 | 2.5356 | 0.6319 | 0.41308 | 0.28101 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 21.6248 | 2.407% | CZ 1A | 0 | 0 | 0.016033 | 0.0037466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.04425 | 2.407% | CZ 1A | 45.4494 | 2.9954 | 3.8841 | 0.4095 | 0 | 99.0148 | 0 | 26.5454 | 6.6154 | 4.3246 | 2.9419 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 231.2266 | 2.407%
CZ 1B | 0.46148 | 0.030377 | 0.037843 | 0.0078731 | 0 | 0.89537 | 0 | 0.23877 | 0.040453 | 0.032297 | 0.031074 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.1688 | 0% | CZ 1B | 14.8126 | 0.97503 | 2.349 | 0.80338 | 0 | 28.7396 | 0 | 7.6641 | 1.2984 | 1.0367 | 0.99742 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 72.9774 | 0% | CZ 1B | 4.3413 | 0.28577 | 0.20343 | 0 | 0 | 8.4231 | 0 | 2.2462 | 0.38055 | 0.30383 | 0.29233 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 19.9508 | 0% | CZ 1B | 0 | 0 | 0.016549 | 0.0080338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.049054 | 0% | CZ 1B | 45.4494 | 2.9917 | 3.9386 | 0.87809 | 0 | 88.1814 | 0 | 23.5158 | 3.984 | 3.1808 | 3.0604 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 214.2262 | 0%
CZ 2A | 0.46148 | 0.030366 | 0.039109 | 0.0087857 | 0 | 0.87047 | 0 | 0.24216 | 0.059897 | 0.041115 | 0.029863 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.1765 | 17.03% | CZ 2A | 14.8126 | 0.97467 | 2.4769 | 0.8965 | 0 | 27.9403 | 0 | 7.7728 | 1.9226 | 1.3197 | 0.95854 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 73.3757 | 17.03% | CZ 2A | 4.3413 | 0.28566 | 0.20362 | 0 | 0 | 8.1888 | 0 | 2.2781 | 0.56347 | 0.38678 | 0.28093 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 20.0029 | 17.03% | CZ 2A | 0 | 0 | 0.017821 | 0.008965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.051257 | 17.03% | CZ 2A | 45.4494 | 2.9906 | 4.0795 | 0.97988 | 0 | 85.729 | 0 | 23.8493 | 5.899 | 4.0492 | 2.9411 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 215.0131 | 17.03%
CZ 2B | 0.46148 | 0.030388 | 0.039283 | 0.0080687 | 0 | 0.52571 | 0 | 0.21813 | 0.040661 | 0.019804 | 0.030595 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.7674 | 1.76% | CZ 2B | 14.8126 | 0.97539 | 2.496 | 0.82333 | 0 | 16.874 | 0 | 7.0014 | 1.3051 | 0.63567 | 0.98205 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 60.2066 | 1.76% | CZ 2B | 4.3413 | 0.28587 | 0.20343 | 0 | 0 | 4.9455 | 0 | 2.052 | 0.38251 | 0.1863 | 0.28782 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 16.159 | 1.76% | CZ 2B | 0 | 0 | 0.018019 | 0.0082333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.050722 | 1.76% | CZ 2B | 45.4494 | 2.9928 | 4.0992 | 0.8999 | 0 | 51.7744 | 0 | 21.4822 | 4.0045 | 1.9504 | 3.0132 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 174.7121 | 1.76%
CZ 3A | 0.46148 | 0.030383 | 0.041774 | 0.034111 | 0 | 0.50129 | 0 | 0.21584 | 0.053252 | 0.025338 | 0.029496 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.7863 | 19.81% | CZ 3A | 14.8126 | 0.97521 | 2.7487 | 3.4808 | 0 | 16.0902 | 0 | 6.9281 | 1.7093 | 0.81328 | 0.94676 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 62.806 | 19.81% | CZ 3A | 4.3413 | 0.28582 | 0.20362 | 0 | 0 | 4.7158 | 0 | 2.0305 | 0.50096 | 0.23836 | 0.27748 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 16.0681 | 19.81% | CZ 3A | 0 | 0 | 0.02054 | 0.034808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.079818 | 19.81% | CZ 3A | 45.4494 | 2.9922 | 4.3767 | 3.8045 | 0 | 49.3695 | 0 | 21.2574 | 5.2446 | 2.4954 | 2.9049 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 176.9406 | 19.81%
CZ 3B | 0.46148 | 0.030381 | 0.041049 | 0.013067 | 0 | 0.36075 | 0 | 0.21003 | 0.024695 | 0.01441 | 0.03049 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.5797 | 7.027% | CZ 3B | 14.8126 | 0.97517 | 2.6761 | 1.3333 | 0 | 11.5794 | 0 | 6.7416 | 0.79265 | 0.46254 | 0.97867 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 54.6531 | 7.027% | CZ 3B | 4.3413 | 0.28581 | 0.20344 | 0 | 0 | 3.3937 | 0 | 1.9758 | 0.23231 | 0.13556 | 0.28683 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 14.3291 | 7.027% | CZ 3B | 0 | 0 | 0.019819 | 0.013333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.057623 | 7.027% | CZ 3B | 45.4494 | 2.9921 | 4.2961 | 1.4573 | 0 | 35.529 | 0 | 20.6851 | 2.4321 | 1.4192 | 3.0029 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 156.3093 | 7.027%
CZ 3C | 0.46148 | 0.030377 | 0.041609 | 0.01021 | 0 | 0.2989 | 0 | 0.20031 | 0 | 0.015506 | 0.029581 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.4813 | 1.237% | CZ 3C | 14.8126 | 0.97503 | 2.7318 | 1.0419 | 0 | 9.594 | 0 | 6.4295 | 0 | 0.4977 | 0.9495 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 51.3332 | 1.237% | CZ 3C | 4.3413 | 0.28577 | 0.20363 | 0 | 0 | 2.8118 | 0 | 1.8844 | 0 | 0.14587 | 0.27828 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 13.4253 | 1.237% | CZ 3C | 0 | 0 | 0.020371 | 0.010419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.055259 | 1.237% | CZ 3C | 45.4494 | 2.9917 | 4.3583 | 1.1387 | 0 | 29.4372 | 0 | 19.7277 | 0 | 1.5271 | 2.9133 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 146.5896 | 1.237%
CZ 4A | 0.46148 | 0.030336 | 0.043726 | 0.074649 | 0 | 0.34533 | 0 | 0.20705 | 0.050913 | 0.018455 | 0.02936 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.6546 | 18.1% | CZ 4A | 14.8126 | 0.97373 | 2.9479 | 7.6172 | 0 | 11.0843 | 0 | 6.6457 | 1.6342 | 0.59237 | 0.9424 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 61.5515 | 18.1% | CZ 4A | 4.3413 | 0.28538 | 0.20363 | 0 | 0 | 3.2486 | 0 | 1.9478 | 0.47896 | 0.17362 | 0.2762 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 14.4297 | 18.1% | CZ 4A | 0 | 0 | 0.022531 | 0.076172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.12317 | 18.1% | CZ 4A | 45.4494 | 2.9877 | 4.5944 | 8.3256 | 0 | 34.0099 | 0 | 20.391 | 5.0142 | 1.8176 | 2.8915 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 164.5275 | 18.1%
CZ 4B | 0.46148 | 0.030359 | 0.043152 | 0.038447 | 0 | 0.28882 | 0 | 0.24878 | 0.023766 | 0.014496 | 0.029206 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.5718 | 0.6509% | CZ 4B | 14.8126 | 0.97445 | 2.8892 | 3.9232 | 0 | 9.2705 | 0 | 7.9854 | 0.76284 | 0.46529 | 0.93745 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 56.322 | 0.6509% | CZ 4B | 4.3413 | 0.28559 | 0.20364 | 0 | 0 | 2.717 | 0 | 2.3404 | 0.22358 | 0.13637 | 0.27475 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 13.9969 | 0.6509% | CZ 4B | 0 | 0 | 0.021944 | 0.039232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.085646 | 0.6509% | CZ 4B | 45.4494 | 2.9899 | 4.5304 | 4.288 | 0 | 28.4447 | 0 | 24.5015 | 2.3406 | 1.4276 | 2.8764 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 155.8946 | 0.6509%
CZ 4C | 0.46148 | 0.030301 | 0.04402 | 0.047191 | 0 | 0.12497 | 0 | 0.1886 | 0.029838 | 0.008395 | 0.029304 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.3574 | 2.48% | CZ 4C | 14.8126 | 0.97261 | 2.9779 | 4.8154 | 0 | 4.0113 | 0 | 6.0535 | 0.95773 | 0.26946 | 0.9406 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 50.1121 | 2.48% | CZ 4C | 4.3413 | 0.28505 | 0.20363 | 0 | 0 | 1.1756 | 0 | 1.7742 | 0.28069 | 0.078975 | 0.27567 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 11.8894 | 2.48% | CZ 4C | 0 | 0 | 0.022831 | 0.048154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.095455 | 2.48% | CZ 4C | 45.4494 | 2.9842 | 4.6272 | 5.2632 | 0 | 12.3077 | 0 | 18.574 | 2.9386 | 0.82679 | 2.886 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 134.9032 | 2.48%
CZ 5A | 0.46148 | 0.030345 | 0.045331 | 0.11371 | 0 | 0.21691 | 0 | 0.20688 | 0.034604 | 0.012927 | 0.029249 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.5447 | 19.94% | CZ 5A | 14.8126 | 0.974 | 3.1117 | 11.6027 | 0 | 6.9623 | 0 | 6.6406 | 1.1107 | 0.41494 | 0.93884 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 60.8694 | 19.94% | CZ 5A | 4.3413 | 0.28546 | 0.20363 | 0 | 0 | 2.0405 | 0 | 1.9462 | 0.32553 | 0.12161 | 0.27516 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 13.0137 | 19.94% | CZ 5A | 0 | 0 | 0.024169 | 0.11603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.16467 | 19.94% | CZ 5A | 45.4494 | 2.9885 | 4.7734 | 12.6818 | 0 | 21.3622 | 0 | 20.3751 | 3.408 | 1.2731 | 2.8806 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 154.2384 | 19.94%
CZ 5B | 0.46148 | 0.030346 | 0.04483 | 0.063716 | 0 | 0.24182 | 0 | 0.24272 | 0.03922 | 0.011576 | 0.029199 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.5582 | 4.639% | CZ 5B | 14.8126 | 0.97404 | 3.0605 | 6.5016 | 0 | 7.7619 | 0 | 7.7906 | 1.2589 | 0.37155 | 0.93723 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 57.7701 | 4.639% | CZ 5B | 4.3413 | 0.28548 | 0.20363 | 0 | 0 | 2.2749 | 0 | 2.2833 | 0.36896 | 0.1089 | 0.27469 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 13.6154 | 4.639% | CZ 5B | 0 | 0 | 0.023657 | 0.065016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11314 | 4.639% | CZ 5B | 45.4494 | 2.9886 | 4.7175 | 7.1063 | 0 | 23.8158 | 0 | 23.904 | 3.8626 | 1.14 | 2.8757 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 154.906 | 4.639%
CZ 5C | 0.46148 | 0.030298 | 0.044877 | 0.048769 | 0 | 0.073912 | 0 | 0.17855 | 0.022577 | 0.005437 | 0.029272 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.2885 | 0.08039% | CZ 5C | 14.8126 | 0.97252 | 3.0653 | 4.9764 | 0 | 2.3724 | 0 | 5.7311 | 0.72468 | 0.17452 | 0.93956 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 48.0701 | 0.08039% | CZ 5C | 4.3413 | 0.28503 | 0.20363 | 0 | 0 | 0.69532 | 0 | 1.6797 | 0.21239 | 0.051148 | 0.27537 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 11.2181 | 0.08039% | CZ 5C | 0 | 0 | 0.023705 | 0.049764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.097939 | 0.08039% | CZ 5C | 45.4494 | 2.984 | 4.7227 | 5.4392 | 0 | 7.2793 | 0 | 17.5846 | 2.2235 | 0.53547 | 2.8829 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 128.1471 | 0.08039%
CZ 6A | 0.46148 | 0.030331 | 0.046639 | 0.19371 | 0 | 0.22837 | 0 | 0.22225 | 0.03543 | 0.014675 | 0.029241 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.6554 | 3.358% | CZ 6A | 14.8126 | 0.97355 | 3.2451 | 19.7665 | 0 | 7.3303 | 0 | 7.1338 | 1.1372 | 0.47104 | 0.93857 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 70.1097 | 3.358% | CZ 6A | 4.3413 | 0.28533 | 0.20363 | 0 | 0 | 2.1484 | 0 | 2.0908 | 0.3333 | 0.13805 | 0.27508 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 13.2901 | 3.358% | CZ 6A | 0 | 0 | 0.025504 | 0.19766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.24764 | 3.358% | CZ 6A | 45.4494 | 2.9871 | 4.9193 | 21.6047 | 0 | 22.4914 | 0 | 21.8884 | 3.4894 | 1.4453 | 2.8798 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 166.201 | 3.358%
CZ 6B | 0.46148 | 0.03031 | 0.046261 | 0.15932 | 0 | 0.16897 | 0 | 0.23009 | 0.033434 | 0.0098754 | 0.029132 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.5622 | 0.8663% | CZ 6B | 14.8126 | 0.97288 | 3.2065 | 16.2573 | 0 | 5.4237 | 0 | 7.3853 | 1.0732 | 0.31698 | 0.93507 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 64.6845 | 0.8663% | CZ 6B | 4.3413 | 0.28513 | 0.20363 | 0 | 0 | 1.5896 | 0 | 2.1645 | 0.31453 | 0.092901 | 0.27405 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 12.7399 | 0.8663% | CZ 6B | 0 | 0 | 0.025117 | 0.16257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.21216 | 0.8663% | CZ 6B | 45.4494 | 2.9851 | 4.8771 | 17.7692 | 0 | 16.6414 | 0 | 22.6603 | 3.2928 | 0.97258 | 2.8691 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 156.563 | 0.8663%
CZ 7 | 0.46148 | 0.03029 | 0.048052 | 0.27661 | 0 | 0.18636 | 0 | 0.22762 | 0.03093 | 0.012819 | 0.029184 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.6966 | 0.5534% | CZ 7 | 14.8126 | 0.97225 | 3.3893 | 28.2256 | 0 | 5.9817 | 0 | 7.306 | 0.99279 | 0.41148 | 0.93673 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 77.3294 | 0.5534% | CZ 7 | 4.3413 | 0.28495 | 0.20363 | 0 | 0 | 1.7531 | 0 | 2.1413 | 0.29097 | 0.1206 | 0.27454 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 12.8846 | 0.5534% | CZ 7 | 0 | 0 | 0.026945 | 0.28226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.33367 | 0.5534% | CZ 7 | 45.4494 | 2.9831 | 5.0769 | 30.8505 | 0 | 18.3534 | 0 | 22.4169 | 3.0462 | 1.2625 | 2.8742 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 171.3593 | 0.5534%
CZ 8 | 0.46148 | 0.030123 | 0.049784 | 0.46585 | 0 | 0.097917 | 0 | 0.23927 | 0.031954 | 0.010098 | 0.029086 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.8089 | 0.05968% | CZ 8 | 14.8126 | 0.9669 | 3.566 | 47.5352 | 0 | 3.1429 | 0 | 7.6801 | 1.0257 | 0.32413 | 0.93358 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 94.2882 | 0.05968% | CZ 8 | 4.3413 | 0.28338 | 0.20363 | 0 | 0 | 0.92113 | 0 | 2.2509 | 0.3006 | 0.094996 | 0.27362 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 12.1438 | 0.05968% | CZ 8 | 0 | 0 | 0.028712 | 0.47535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.52853 | 0.05968% | CZ 8 | 45.4494 | 2.9667 | 5.27 | 51.956 | 0 | 9.6434 | 0 | 23.5649 | 3.147 | 0.99452 | 2.8645 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 184.9025 | 0.05968%
US Weighted | 0.46148 | 0.030358 | 0.04263 | 0.059824 | 0 | 0.44228 | 0 | 0.21885 | 0.045335 | 0.022048 | 0.02955 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.7456 | 100% | US Weighted | 14.8126 | 0.97441 | 2.8362 | 6.1045 | 0 | 14.1961 | 0 | 7.0246 | 1.4551 | 0.7077 | 0.94848 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 63.3609 | 100% | US Weighted | 4.3413 | 0.28558 | 0.20361 | 0 | 0 | 4.1606 | 0 | 2.0588 | 0.42648 | 0.20742 | 0.27798 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 15.4361 | 100% | US Weighted | 0 | 0 | 0.021415 | 0.061045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10693 | 100% | US Weighted | 45.4494 | 2.9898 | 4.4722 | 6.6723 | 0 | 43.5578 | 0 | 21.5536 | 4.4648 | 2.1714 | 2.9102 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 173.2877 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 210887 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.46148 | 0.030405 | 0.036041 | 0.015169 | 0 | 1.7533 | 0 | 0.33801 | 0.12046 | 0.072472 | 0.030542 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 3.2512 | 0% | CZ 0A | 14.8126 | 0.97593 | 2.164 | 1.5478 | 0 | 56.2766 | 0 | 10.8495 | 3.8666 | 2.3262 | 0.98034 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 108.1006 | 0% | CZ 0A | 4.3413 | 0.28603 | 0.20359 | 0 | 0 | 16.4937 | 0 | 3.1798 | 1.1332 | 0.68177 | 0.28732 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 30.081 | 0% | CZ 0A | 0 | 0 | 0.014693 | 0.015478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.054642 | 0% | CZ 0A | 45.4494 | 2.9944 | 3.7373 | 1.6918 | 0 | 172.6727 | 0 | 33.2894 | 11.8638 | 7.1375 | 3.008 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 320.8904 | 0%
CZ 0B | 0.46148 | 0.030411 | 0.036337 | 0.0042966 | 0 | 1.1692 | 0 | 0.28706 | 0.080204 | 0.04217 | 0.031196 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.5356 | 0% | CZ 0B | 14.8126 | 0.97611 | 2.1954 | 0.43843 | 0 | 37.5275 | 0 | 9.2141 | 2.5744 | 1.3536 | 1.0013 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 84.3945 | 0% | CZ 0B | 4.3413 | 0.28608 | 0.20342 | 0 | 0 | 10.9987 | 0 | 2.7005 | 0.7545 | 0.3967 | 0.29347 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 23.4489 | 0% | CZ 0B | 0 | 0 | 0.015014 | 0.0043843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.043868 | 0% | CZ 0B | 45.4494 | 2.995 | 3.7706 | 0.47921 | 0 | 115.1453 | 0 | 28.2714 | 7.8989 | 4.1531 | 3.0724 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 250.2813 | 0%
CZ 1A | 0.46148 | 0.030415 | 0.03736 | 0.0036227 | 0 | 1.0848 | 0 | 0.33389 | 0.11306 | 0.045614 | 0.02987 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.5334 | 2.407% | CZ 1A | 14.8126 | 0.97625 | 2.2984 | 0.36967 | 0 | 34.819 | 0 | 10.7171 | 3.6288 | 1.4641 | 0.95876 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 84.3457 | 2.407% | CZ 1A | 4.3413 | 0.28612 | 0.20362 | 0 | 0 | 10.2049 | 0 | 3.141 | 1.0635 | 0.4291 | 0.281 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 23.4248 | 2.407% | CZ 1A | 0 | 0 | 0.016036 | 0.0036967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.044203 | 2.407% | CZ 1A | 45.4494 | 2.9954 | 3.8844 | 0.40405 | 0 | 106.8348 | 0 | 32.8831 | 11.1343 | 4.4923 | 2.9418 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 250.0656 | 2.407%
CZ 1B | 0.46148 | 0.030377 | 0.037845 | 0.013138 | 0 | 0.95433 | 0 | 0.27958 | 0.078789 | 0.03489 | 0.031076 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.3148 | 0% | CZ 1B | 14.8126 | 0.97503 | 2.3492 | 1.3406 | 0 | 30.6319 | 0 | 8.9738 | 2.529 | 1.1199 | 0.99747 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 78.0305 | 0% | CZ 1B | 4.3413 | 0.28577 | 0.20343 | 0 | 0 | 8.9777 | 0 | 2.6301 | 0.74119 | 0.32822 | 0.29234 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 21.2742 | 0% | CZ 1B | 0 | 0 | 0.016551 | 0.013406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.054428 | 0% | CZ 1B | 45.4494 | 2.9917 | 3.9388 | 1.4653 | 0 | 93.9874 | 0 | 27.5343 | 7.7596 | 3.4361 | 3.0605 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 228.6691 | 0%
CZ 2A | 0.46148 | 0.030366 | 0.039111 | 0.01717 | 0 | 0.98149 | 0 | 0.31292 | 0.097072 | 0.044918 | 0.029866 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 2.4077 | 17.03% | CZ 2A | 14.8126 | 0.97467 | 2.4771 | 1.752 | 0 | 31.5036 | 0 | 10.0442 | 3.1158 | 1.4418 | 0.95862 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 81.3815 | 17.03% | CZ 2A | 4.3413 | 0.28566 | 0.20362 | 0 | 0 | 9.2332 | 0 | 2.9438 | 0.91319 | 0.42256 | 0.28096 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 22.0985 | 17.03% | CZ 2A | 0 | 0 | 0.017824 | 0.01752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.059814 | 17.03% | CZ 2A | 45.4494 | 2.9906 | 4.0798 | 1.915 | 0 | 96.6622 | 0 | 30.8185 | 9.5602 | 4.4237 | 2.9413 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 237.8868 | 17.03%
CZ 2B | 0.46148 | 0.030388 | 0.039286 | 0.017641 | 0 | 0.57754 | 0 | 0.27604 | 0.063664 | 0.021955 | 0.030593 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.9119 | 1.76% | CZ 2B | 14.8126 | 0.97539 | 2.4963 | 1.8001 | 0 | 18.5378 | 0 | 8.8604 | 2.0435 | 0.70472 | 0.98196 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 65.5137 | 1.76% | CZ 2B | 4.3413 | 0.28587 | 0.20343 | 0 | 0 | 5.4331 | 0 | 2.5968 | 0.59891 | 0.20654 | 0.2878 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 17.428 | 1.76% | CZ 2B | 0 | 0 | 0.018022 | 0.018001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.060493 | 1.76% | CZ 2B | 45.4494 | 2.9928 | 4.0995 | 1.9675 | 0 | 56.8792 | 0 | 27.1861 | 6.27 | 2.1623 | 3.0129 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 189.0658 | 1.76%
CZ 3A | 0.46148 | 0.030383 | 0.041779 | 0.05494 | 0 | 0.54741 | 0 | 0.28915 | 0.086437 | 0.027439 | 0.029496 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.9618 | 19.81% | CZ 3A | 14.8126 | 0.97521 | 2.7493 | 5.6061 | 0 | 17.5707 | 0 | 9.2812 | 2.7745 | 0.88072 | 0.94676 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 69.8981 | 19.81% | CZ 3A | 4.3413 | 0.28582 | 0.20362 | 0 | 0 | 5.1497 | 0 | 2.7202 | 0.81315 | 0.25812 | 0.27748 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 17.5236 | 19.81% | CZ 3A | 0 | 0 | 0.020545 | 0.056061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.10108 | 19.81% | CZ 3A | 45.4494 | 2.9922 | 4.3773 | 6.1275 | 0 | 53.912 | 0 | 28.4775 | 8.5128 | 2.7023 | 2.9049 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 194.502 | 19.81%
CZ 3B | 0.46148 | 0.030381 | 0.041054 | 0.024326 | 0 | 0.39931 | 0 | 0.27258 | 0.047038 | 0.015637 | 0.030486 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.7156 | 7.027% | CZ 3B | 14.8126 | 0.97517 | 2.6766 | 2.4822 | 0 | 12.8171 | 0 | 8.7493 | 1.5098 | 0.50192 | 0.97854 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 59.8044 | 7.027% | CZ 3B | 4.3413 | 0.28581 | 0.20344 | 0 | 0 | 3.7565 | 0 | 2.5643 | 0.4425 | 0.14711 | 0.28679 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 15.5019 | 7.027% | CZ 3B | 0 | 0 | 0.019824 | 0.024822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.069117 | 7.027% | CZ 3B | 45.4494 | 2.9921 | 4.2967 | 2.7131 | 0 | 39.3267 | 0 | 26.8453 | 4.6326 | 1.5401 | 3.0024 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 169.8444 | 7.027%
CZ 3C | 0.46148 | 0.030377 | 0.04161 | 0.027857 | 0 | 0.33969 | 0 | 0.28155 | 0 | 0.018472 | 0.029581 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.6239 | 1.237% | CZ 3C | 14.8126 | 0.97503 | 2.7319 | 2.8425 | 0 | 10.9032 | 0 | 9.037 | 0 | 0.59291 | 0.9495 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 57.1458 | 1.237% | CZ 3C | 4.3413 | 0.28577 | 0.20363 | 0 | 0 | 3.1955 | 0 | 2.6486 | 0 | 0.17377 | 0.27828 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 14.6011 | 1.237% | CZ 3C | 0 | 0 | 0.020371 | 0.028425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.073267 | 1.237% | CZ 3C | 45.4494 | 2.9917 | 4.3584 | 3.1069 | 0 | 33.4542 | 0 | 27.7282 | 0 | 1.8192 | 2.9133 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 160.8674 | 1.237%
CZ 4A | 0.46148 | 0.030336 | 0.043738 | 0.13019 | 0 | 0.36863 | 0 | 0.28689 | 0.083643 | 0.02007 | 0.02936 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.8476 | 18.1% | CZ 4A | 14.8126 | 0.97373 | 2.9491 | 13.2845 | 0 | 11.8322 | 0 | 9.2087 | 2.6848 | 0.64421 | 0.9424 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 71.6332 | 18.1% | CZ 4A | 4.3413 | 0.28538 | 0.20363 | 0 | 0 | 3.4678 | 0 | 2.6989 | 0.78686 | 0.18881 | 0.2762 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 15.7232 | 18.1% | CZ 4A | 0 | 0 | 0.022543 | 0.13285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.17986 | 18.1% | CZ 4A | 45.4494 | 2.9877 | 4.5957 | 14.52 | 0 | 36.3046 | 0 | 28.2549 | 8.2376 | 1.9766 | 2.8915 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 184.2642 | 18.1%
CZ 4B | 0.46148 | 0.030359 | 0.043159 | 0.065027 | 0 | 0.31155 | 0 | 0.3103 | 0.050796 | 0.015706 | 0.029199 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.7109 | 0.6509% | CZ 4B | 14.8126 | 0.97445 | 2.89 | 6.6354 | 0 | 10 | 0 | 9.9599 | 1.6304 | 0.50413 | 0.93723 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 62.6453 | 0.6509% | CZ 4B | 4.3413 | 0.28559 | 0.20363 | 0 | 0 | 2.9308 | 0 | 2.9191 | 0.47785 | 0.14775 | 0.27469 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 15.055 | 0.6509% | CZ 4B | 0 | 0 | 0.021953 | 0.066354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.11278 | 0.6509% | CZ 4B | 45.4494 | 2.9899 | 4.5312 | 7.2525 | 0 | 30.6829 | 0 | 30.5598 | 5.0026 | 1.5468 | 2.8757 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 169.937 | 0.6509%
CZ 4C | 0.46148 | 0.030301 | 0.044028 | 0.083944 | 0 | 0.12662 | 0 | 0.25815 | 0.045503 | 0.0095071 | 0.029301 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.4821 | 2.48% | CZ 4C | 14.8126 | 0.97261 | 2.9787 | 8.5657 | 0 | 4.0642 | 0 | 8.2862 | 1.4605 | 0.30516 | 0.94051 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 56.6872 | 2.48% | CZ 4C | 4.3413 | 0.28505 | 0.20363 | 0 | 0 | 1.1911 | 0 | 2.4285 | 0.42806 | 0.089436 | 0.27565 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 12.7171 | 2.48% | CZ 4C | 0 | 0 | 0.022839 | 0.085657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.13297 | 2.48% | CZ 4C | 45.4494 | 2.9842 | 4.6281 | 9.3623 | 0 | 12.4701 | 0 | 25.4244 | 4.4814 | 0.93631 | 2.8857 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 147.6681 | 2.48%
CZ 5A | 0.46148 | 0.030345 | 0.045341 | 0.1536 | 0 | 0.21952 | 0 | 0.2817 | 0.060236 | 0.014153 | 0.029248 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.6889 | 19.94% | CZ 5A | 14.8126 | 0.974 | 3.1127 | 15.673 | 0 | 7.046 | 0 | 9.0421 | 1.9334 | 0.45427 | 0.9388 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 68.288 | 19.94% | CZ 5A | 4.3413 | 0.28546 | 0.20363 | 0 | 0 | 2.0651 | 0 | 2.6501 | 0.56666 | 0.13314 | 0.27515 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 13.9947 | 19.94% | CZ 5A | 0 | 0 | 0.024179 | 0.15673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.20538 | 19.94% | CZ 5A | 45.4494 | 2.9885 | 4.7745 | 17.1306 | 0 | 21.6192 | 0 | 27.7438 | 5.9323 | 1.3938 | 2.8805 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 168.9588 | 19.94%
CZ 5B | 0.46148 | 0.030346 | 0.044838 | 0.10656 | 0 | 0.24627 | 0 | 0.31399 | 0.060527 | 0.012366 | 0.029193 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.6989 | 4.639% | CZ 5B | 14.8126 | 0.97404 | 3.0613 | 10.8736 | 0 | 7.9046 | 0 | 10.0783 | 1.9428 | 0.39691 | 0.93705 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 65.2822 | 4.639% | CZ 5B | 4.3413 | 0.28548 | 0.20363 | 0 | 0 | 2.3167 | 0 | 2.9538 | 0.5694 | 0.11633 | 0.27463 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 14.5355 | 4.639% | CZ 5B | 0 | 0 | 0.023665 | 0.10874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.15687 | 4.639% | CZ 5B | 45.4494 | 2.9886 | 4.7184 | 11.8848 | 0 | 24.2536 | 0 | 30.9231 | 5.961 | 1.2178 | 2.8751 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 169.3181 | 4.639%
CZ 5C | 0.46148 | 0.030298 | 0.044884 | 0.092875 | 0 | 0.070848 | 0 | 0.24442 | 0.049624 | 0.006486 | 0.029269 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.4235 | 0.08039% | CZ 5C | 14.8126 | 0.97252 | 3.066 | 9.477 | 0 | 2.2741 | 0 | 7.8452 | 1.5928 | 0.20819 | 0.93947 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 55.489 | 0.08039% | CZ 5C | 4.3413 | 0.28503 | 0.20363 | 0 | 0 | 0.66649 | 0 | 2.2993 | 0.46683 | 0.061016 | 0.27534 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 12.0732 | 0.08039% | CZ 5C | 0 | 0 | 0.023713 | 0.09477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.14295 | 0.08039% | CZ 5C | 45.4494 | 2.984 | 4.7236 | 10.3584 | 0 | 6.9775 | 0 | 24.0714 | 4.8872 | 0.63878 | 2.8826 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 142.0189 | 0.08039%
CZ 6A | 0.46148 | 0.030331 | 0.046649 | 0.3197 | 0 | 0.2329 | 0 | 0.29852 | 0.052083 | 0.01671 | 0.029241 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.8809 | 3.358% | CZ 6A | 14.8126 | 0.97355 | 3.2462 | 32.6225 | 0 | 7.4755 | 0 | 9.5818 | 1.6717 | 0.53636 | 0.93857 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 86.1599 | 3.358% | CZ 6A | 4.3413 | 0.28533 | 0.20363 | 0 | 0 | 2.1909 | 0 | 2.8083 | 0.48996 | 0.1572 | 0.27508 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 14.2259 | 3.358% | CZ 6A | 0 | 0 | 0.025514 | 0.32623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.37621 | 3.358% | CZ 6A | 45.4494 | 2.9871 | 4.9205 | 35.6564 | 0 | 22.937 | 0 | 29.3996 | 5.1294 | 1.6457 | 2.8798 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 190.0511 | 3.358%
CZ 6B | 0.46148 | 0.03031 | 0.046272 | 0.1976 | 0 | 0.16463 | 0 | 0.29911 | 0.059743 | 0.010511 | 0.029129 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.6921 | 0.8663% | CZ 6B | 14.8126 | 0.97288 | 3.2077 | 20.1637 | 0 | 5.2841 | 0 | 9.6009 | 1.9176 | 0.33739 | 0.93498 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 71.5329 | 0.8663% | CZ 6B | 4.3413 | 0.28513 | 0.20363 | 0 | 0 | 1.5487 | 0 | 2.8139 | 0.56202 | 0.098883 | 0.27403 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 13.6018 | 0.8663% | CZ 6B | 0 | 0 | 0.025129 | 0.20164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.25124 | 0.8663% | CZ 6B | 45.4494 | 2.9851 | 4.8784 | 22.0389 | 0 | 16.2132 | 0 | 29.4583 | 5.8838 | 1.0352 | 2.8688 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 169.8572 | 0.8663%
CZ 7 | 0.46148 | 0.03029 | 0.048062 | 0.39846 | 0 | 0.19096 | 0 | 0.31103 | 0.051754 | 0.014639 | 0.029185 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.9292 | 0.5534% | CZ 7 | 14.8126 | 0.97225 | 3.3904 | 40.6593 | 0 | 6.1295 | 0 | 9.9835 | 1.6612 | 0.46987 | 0.93678 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 93.3163 | 0.5534% | CZ 7 | 4.3413 | 0.28495 | 0.20363 | 0 | 0 | 1.7964 | 0 | 2.926 | 0.48687 | 0.13771 | 0.27455 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 13.9257 | 0.5534% | CZ 7 | 0 | 0 | 0.026956 | 0.40659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.45802 | 0.5534% | CZ 7 | 45.4494 | 2.9831 | 5.0781 | 44.4406 | 0 | 18.807 | 0 | 30.6322 | 5.097 | 1.4417 | 2.8743 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 195.8494 | 0.5534%
CZ 8 | 0.46148 | 0.030123 | 0.049786 | 0.55519 | 0 | 0.09255 | 0 | 0.30791 | 0.055481 | 0.010859 | 0.029087 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.9858 | 0.05968% | CZ 8 | 14.8126 | 0.9669 | 3.5662 | 56.6525 | 0 | 2.9706 | 0 | 9.8834 | 1.7808 | 0.34854 | 0.93363 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 106.2163 | 0.05968% | CZ 8 | 4.3413 | 0.28338 | 0.20363 | 0 | 0 | 0.87064 | 0 | 2.8966 | 0.52193 | 0.10215 | 0.27363 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 12.9675 | 0.05968% | CZ 8 | 0 | 0 | 0.028714 | 0.56653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.61971 | 0.05968% | CZ 8 | 45.4494 | 2.9667 | 5.2703 | 61.9212 | 0 | 9.1148 | 0 | 30.325 | 5.464 | 1.0694 | 2.8646 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 203.4916 | 0.05968%
US Weighted | 0.46148 | 0.030358 | 0.042637 | 0.09296 | 0 | 0.48162 | 0 | 0.29191 | 0.074845 | 0.024008 | 0.029549 | 0.010609 | 0.011115 | 0.07431 | 0 | 0.29726 | 1.9227 | 100% | US Weighted | 14.8126 | 0.97441 | 2.837 | 9.4857 | 0 | 15.4591 | 0 | 9.3698 | 2.4024 | 0.7706 | 0.94846 | 0.34054 | 0.35676 | 4.0625 | 0 | 9.5412 | 71.361 | 100% | US Weighted | 4.3413 | 0.28558 | 0.20361 | 0 | 0 | 4.5308 | 0 | 2.7461 | 0.70409 | 0.22585 | 0.27798 | 0.099805 | 0.10456 | 0.47347 | 0 | 2.7964 | 16.7896 | 100% | US Weighted | 0 | 0 | 0.021422 | 0.094857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02447 | 0 | 0 | 0.14075 | 100% | US Weighted | 45.4494 | 2.9898 | 4.473 | 10.3679 | 0 | 47.4329 | 0 | 28.7491 | 7.3712 | 2.3644 | 2.9102 | 1.0449 | 1.0947 | 7.6313 | 0 | 29.2753 | 191.1539 | 100%
Building Type: | Secondary School |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Secondary School |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 210887 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 210887 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 210887 | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.35035 | 0.020873 | 0.00013177 | 0.010384 | 0 | 0.99039 | 0 | 0.16828 | 0.073572 | 0.06232 | 0.01328 | 0.0013936 | 0.0069944 | 0 | 0 | 0.028478 | 1.7264 | 0% | CZ 0A | 11.2455 | 0.66997 | 0.01227 | 1.0596 | 0 | 31.7892 | 0 | 5.4013 | 2.3615 | 2.0003 | 0.42627 | 0.04473 | 0.22451 | 0 | 0 | 0.91407 | 56.1493 | 0% | CZ 0A | 3.2959 | 0.19636 | 0.00015811 | 0 | 0 | 9.3169 | 0 | 1.583 | 0.69212 | 0.58626 | 0.12493 | 0.01311 | 0.065799 | 0 | 0 | 0.2679 | 16.1424 | 0% | CZ 0A | 0 | 0 | 0.0001173 | 0.010596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010713 | 0% | CZ 0A | 34.5044 | 2.0557 | 0.014477 | 1.1582 | 0 | 97.5385 | 0 | 16.5728 | 7.2458 | 6.1376 | 1.3079 | 0.13725 | 0.68885 | 0 | 0 | 2.8046 | 170.166 | 0%
CZ 0B | 0.35086 | 0.020884 | 3.3836e-05 | 0.0037941 | 0 | 0.51343 | 0 | 0.14127 | 0.037507 | 0.03282 | 0.013976 | 0.0013936 | 0.0069944 | 0 | 0 | 0.028478 | 1.1514 | 0% | CZ 0B | 11.2618 | 0.67033 | 0.0035506 | 0.38715 | 0 | 16.4799 | 0 | 4.5343 | 1.2039 | 1.0534 | 0.44861 | 0.04473 | 0.22451 | 0 | 0 | 0.91407 | 37.2262 | 0% | CZ 0B | 3.3006 | 0.19646 | -1.3176e-05 | 0 | 0 | 4.83 | 0 | 1.3289 | 0.35284 | 0.30874 | 0.13148 | 0.01311 | 0.065799 | 0 | 0 | 0.2679 | 10.7959 | 0% | CZ 0B | 0 | 0 | 3.5955e-05 | 0.0038715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039075 | 0% | CZ 0B | 34.5544 | 2.0568 | 0.003792 | 0.42316 | 0 | 50.565 | 0 | 13.9126 | 3.6939 | 3.2322 | 1.3765 | 0.13725 | 0.68885 | 0 | 0 | 2.8046 | 113.449 | 0%
CZ 1A | 0.34765 | 0.020887 | 0.00013148 | 0.0033298 | 0 | 0.59947 | 0 | 0.20633 | 0.067589 | 0.039042 | 0.012686 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 1.334 | 2.407% | CZ 1A | 11.1587 | 0.67042 | 0.012045 | 0.33978 | 0 | 19.2417 | 0 | 6.6228 | 2.1694 | 1.2532 | 0.4072 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 43.0586 | 2.407% | CZ 1A | 3.2704 | 0.19649 | 0.00018446 | 0 | 0 | 5.6394 | 0 | 1.941 | 0.63583 | 0.36728 | 0.11934 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 12.5168 | 2.407% | CZ 1A | 0 | 0 | 0.00011416 | 0.0033978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0035119 | 2.407% | CZ 1A | 34.2382 | 2.057 | 0.014409 | 0.37138 | 0 | 59.0392 | 0 | 20.3207 | 6.6565 | 3.8451 | 1.2494 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 131.4225 | 2.407%
CZ 1B | 0.34891 | 0.020866 | 3.92e-05 | 0.010383 | 0 | 0.40081 | 0 | 0.137 | 0.04322 | 0.027289 | 0.013941 | 0.0013936 | 0.0069944 | 0 | 0 | 0.028478 | 1.0393 | 0% | CZ 1B | 11.1994 | 0.66974 | 0.004 | 1.0595 | 0 | 12.8651 | 0 | 4.3975 | 1.3873 | 0.87591 | 0.44748 | 0.04473 | 0.22451 | 0 | 0 | 0.91407 | 34.0892 | 0% | CZ 1B | 3.2823 | 0.19629 | 0 | 0 | 0 | 3.7705 | 0 | 1.2888 | 0.40659 | 0.25671 | 0.13115 | 0.01311 | 0.065799 | 0 | 0 | 0.2679 | 9.6793 | 0% | CZ 1B | 0 | 0 | 4e-05 | 0.010595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010635 | 0% | CZ 1B | 34.3629 | 2.055 | 0.004372 | 1.158 | 0 | 39.4738 | 0 | 13.4929 | 4.2566 | 2.6875 | 1.373 | 0.13725 | 0.68885 | 0 | 0 | 2.8046 | 102.4948 | 0%
CZ 2A | 0.34869 | 0.02086 | 0.00011959 | 0.01409 | 0 | 0.55854 | 0 | 0.19868 | 0.05996 | 0.038144 | 0.012741 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 1.2887 | 17.03% | CZ 2A | 11.1922 | 0.66956 | 0.010832 | 1.4378 | 0 | 17.928 | 0 | 6.3772 | 1.9246 | 1.2244 | 0.40896 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 42.3567 | 17.03% | CZ 2A | 3.2802 | 0.19624 | 0.00018446 | 0 | 0 | 5.2544 | 0 | 1.869 | 0.56406 | 0.35884 | 0.11986 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 11.9897 | 17.03% | CZ 2A | 0 | 0 | 0.00010202 | 0.014378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01448 | 17.03% | CZ 2A | 34.3408 | 2.0544 | 0.013082 | 1.5715 | 0 | 55.0083 | 0 | 19.567 | 5.9052 | 3.7567 | 1.2548 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 127.1023 | 17.03%
CZ 2B | 0.34635 | 0.020873 | 4.0522e-05 | 0.01577 | 0 | 0.25799 | 0 | 0.15371 | 0.030123 | 0.017597 | 0.013649 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.89296 | 1.76% | CZ 2B | 11.117 | 0.66997 | 0.0041349 | 1.6092 | 0 | 8.2809 | 0 | 4.9337 | 0.9669 | 0.56482 | 0.43809 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 29.768 | 1.76% | CZ 2B | 3.2582 | 0.19636 | 0 | 0 | 0 | 2.427 | 0 | 1.446 | 0.28338 | 0.16554 | 0.1284 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 8.2517 | 1.76% | CZ 2B | 0 | 0 | 4.1349e-05 | 0.016092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016134 | 1.76% | CZ 2B | 34.1102 | 2.0557 | 0.0045194 | 1.7589 | 0 | 25.4081 | 0 | 15.138 | 2.9667 | 1.733 | 1.3442 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 88.15 | 1.76%
CZ 3A | 0.34685 | 0.020868 | 0.00010682 | 0.034765 | 0 | 0.29175 | 0 | 0.18271 | 0.051864 | 0.022969 | 0.012493 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 1.0012 | 19.81% | CZ 3A | 11.133 | 0.66983 | 0.0095283 | 3.5475 | 0 | 9.3647 | 0 | 5.8647 | 1.6647 | 0.73727 | 0.401 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 34.5754 | 19.81% | CZ 3A | 3.2629 | 0.19632 | 0.00018446 | 0 | 0 | 2.7446 | 0 | 1.7189 | 0.48791 | 0.21608 | 0.11753 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 9.0912 | 19.81% | CZ 3A | 0 | 0 | 8.899e-05 | 0.035475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035564 | 19.81% | CZ 3A | 34.1592 | 2.0552 | 0.011658 | 3.8774 | 0 | 28.7335 | 0 | 17.9947 | 5.1079 | 2.2621 | 1.2304 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 99.0626 | 19.81%
CZ 3B | 0.34559 | 0.020868 | 4.1041e-05 | 0.0099459 | 0 | 0.16067 | 0 | 0.15677 | 0.047038 | 0.012116 | 0.013562 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.80347 | 7.027% | CZ 3B | 11.0928 | 0.66983 | 0.0040899 | 1.0149 | 0 | 5.1571 | 0 | 5.0319 | 1.5098 | 0.38891 | 0.4353 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 26.4879 | 7.027% | CZ 3B | 3.2511 | 0.19632 | 1.3176e-05 | 0 | 0 | 1.5115 | 0 | 1.4748 | 0.4425 | 0.11398 | 0.12758 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 7.4645 | 7.027% | CZ 3B | 0 | 0 | 4.045e-05 | 0.010149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010189 | 7.027% | CZ 3B | 34.0359 | 2.0552 | 0.0045591 | 1.1093 | 0 | 15.8236 | 0 | 15.4394 | 4.6326 | 1.1933 | 1.3356 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 79.26 | 7.027%
CZ 3C | 0.34495 | 0.020831 | 9.985e-05 | 0.019873 | 0 | 0.16144 | 0 | 0.18239 | 0 | 0.015698 | 0.012594 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.79474 | 1.237% | CZ 3C | 11.0721 | 0.66862 | 0.0087194 | 2.0278 | 0 | 5.1819 | 0 | 5.8543 | 0 | 0.50386 | 0.40424 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 26.9049 | 1.237% | CZ 3C | 3.245 | 0.19596 | 0.00019763 | 0 | 0 | 1.5187 | 0 | 1.7158 | 0 | 0.14767 | 0.11848 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 7.2887 | 1.237% | CZ 3C | 0 | 0 | 8.045e-05 | 0.020278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020359 | 1.237% | CZ 3C | 33.9724 | 2.0515 | 0.010862 | 2.2164 | 0 | 15.8996 | 0 | 17.9628 | 0 | 1.546 | 1.2403 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 78.5305 | 1.237%
CZ 4A | 0.34556 | 0.020773 | 0.00011747 | 0.10632 | 0 | 0.1866 | 0 | 0.17937 | 0.045673 | 0.016436 | 0.012382 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.9501 | 18.1% | CZ 4A | 11.0918 | 0.66678 | 0.010517 | 10.8491 | 0 | 5.9894 | 0 | 5.7574 | 1.466 | 0.52755 | 0.39745 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 37.9392 | 18.1% | CZ 4A | 3.2508 | 0.19542 | 0.00019763 | 0 | 0 | 1.7554 | 0 | 1.6874 | 0.42966 | 0.15462 | 0.11649 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 7.9368 | 18.1% | CZ 4A | 0 | 0 | 9.8428e-05 | 0.10849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10859 | 18.1% | CZ 4A | 34.033 | 2.0459 | 0.012827 | 11.858 | 0 | 18.3772 | 0 | 17.6653 | 4.4981 | 1.6187 | 1.2195 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 94.959 | 18.1%
CZ 4B | 0.34733 | 0.020846 | 0.00011879 | 0.036344 | 0 | 0.14022 | 0 | 0.19386 | 0.050796 | 0.012898 | 0.012297 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.85157 | 0.6509% | CZ 4B | 11.1485 | 0.66911 | 0.010652 | 3.7086 | 0 | 4.5008 | 0 | 6.2224 | 1.6304 | 0.41399 | 0.39471 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 29.8825 | 0.6509% | CZ 4B | 3.2674 | 0.19611 | 0.00019763 | 0 | 0 | 1.3191 | 0 | 1.8237 | 0.47785 | 0.12133 | 0.11568 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 7.6682 | 0.6509% | CZ 4B | 0 | 0 | 9.9776e-05 | 0.037086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037186 | 0.6509% | CZ 4B | 34.2069 | 2.053 | 0.012975 | 4.0535 | 0 | 13.8098 | 0 | 19.0922 | 5.0026 | 1.2702 | 1.2111 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 84.343 | 0.6509%
CZ 4C | 0.34305 | 0.020731 | 9.7207e-05 | 0.030266 | 0 | 0.044032 | 0 | 0.15577 | 0.045503 | 0.0062353 | 0.012347 | 0.0013936 | 0.0069916 | 0 | 0 | 0.028478 | 0.69489 | 2.48% | CZ 4C | 11.011 | 0.66543 | 0.0084497 | 3.0884 | 0 | 1.4133 | 0 | 5 | 1.4605 | 0.20014 | 0.39633 | 0.04473 | 0.22442 | 0 | 0 | 0.91407 | 24.4268 | 2.48% | CZ 4C | 3.2271 | 0.19503 | 0.00019763 | 0 | 0 | 0.41423 | 0 | 1.4654 | 0.42806 | 0.058658 | 0.11616 | 0.01311 | 0.065773 | 0 | 0 | 0.2679 | 6.2517 | 2.48% | CZ 4C | 0 | 0 | 7.7754e-05 | 0.030884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030962 | 2.48% | CZ 4C | 33.785 | 2.0417 | 0.010568 | 3.3756 | 0 | 4.3366 | 0 | 15.3413 | 4.4814 | 0.61409 | 1.216 | 0.13725 | 0.68857 | 0 | 0 | 2.8046 | 68.8327 | 2.48%
CZ 5A | 0.34676 | 0.020815 | 0.00011387 | 0.10289 | 0 | 0.096989 | 0 | 0.17253 | 0.024933 | 0.012128 | 0.012283 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.82631 | 19.94% | CZ 5A | 11.1304 | 0.66812 | 0.010247 | 10.4994 | 0 | 3.1131 | 0 | 5.5378 | 0.80029 | 0.38927 | 0.39426 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 33.7262 | 19.94% | CZ 5A | 3.2621 | 0.19582 | 0.00018446 | 0 | 0 | 0.91241 | 0 | 1.623 | 0.23455 | 0.11409 | 0.11555 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 6.8045 | 19.94% | CZ 5A | 0 | 0 | 9.6181e-05 | 0.10499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10509 | 19.94% | CZ 5A | 34.1512 | 2.05 | 0.012444 | 11.4759 | 0 | 9.552 | 0 | 16.9915 | 2.4555 | 1.1944 | 1.2097 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 82.7232 | 19.94%
CZ 5B | 0.34608 | 0.020796 | 0.00011791 | 0.039597 | 0 | 0.11728 | 0 | 0.19878 | 0.060527 | 0.0096345 | 0.012279 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.84195 | 4.639% | CZ 5B | 11.1086 | 0.66749 | 0.010562 | 4.0405 | 0 | 3.7644 | 0 | 6.3803 | 1.9428 | 0.30925 | 0.39412 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 29.8012 | 4.639% | CZ 5B | 3.2557 | 0.19563 | 0.00019763 | 0 | 0 | 1.1033 | 0 | 1.8699 | 0.5694 | 0.090635 | 0.11551 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 7.5471 | 4.639% | CZ 5B | 0 | 0 | 9.8877e-05 | 0.040405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040504 | 4.639% | CZ 5B | 34.0843 | 2.0481 | 0.012876 | 4.4163 | 0 | 11.5502 | 0 | 19.5765 | 5.961 | 0.94886 | 1.2093 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 83.438 | 4.639%
CZ 5C | 0.34432 | 0.020735 | 9.8088e-05 | 0.066122 | 0 | 0.015849 | 0 | 0.14657 | 0.014714 | 0.0041331 | 0.012318 | 0.0013936 | 0.0069916 | 0 | 0 | 0.028478 | 0.66171 | 0.08039% | CZ 5C | 11.0518 | 0.66556 | 0.0085396 | 6.7471 | 0 | 0.50871 | 0 | 4.7045 | 0.4723 | 0.13266 | 0.39538 | 0.04473 | 0.22442 | 0 | 0 | 0.91407 | 25.8698 | 0.08039% | CZ 5C | 3.2391 | 0.19507 | 0.00019763 | 0 | 0 | 0.1491 | 0 | 1.3788 | 0.13842 | 0.038881 | 0.11588 | 0.01311 | 0.065773 | 0 | 0 | 0.2679 | 5.6022 | 0.08039% | CZ 5C | 0 | 0 | 7.8653e-05 | 0.067471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06755 | 0.08039% | CZ 5C | 33.9101 | 2.0421 | 0.010666 | 7.3746 | 0 | 1.5609 | 0 | 14.4347 | 1.4492 | 0.40705 | 1.2131 | 0.13725 | 0.68857 | 0 | 0 | 2.8046 | 66.0329 | 0.08039%
CZ 6A | 0.34577 | 0.020786 | 0.00011827 | 0.2219 | 0 | 0.10308 | 0 | 0.18112 | 0.015367 | 0.014345 | 0.012287 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.95164 | 3.358% | CZ 6A | 11.0985 | 0.66718 | 0.010697 | 22.6428 | 0 | 3.3086 | 0 | 5.8136 | 0.49325 | 0.46043 | 0.39439 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 46.0727 | 3.358% | CZ 6A | 3.2528 | 0.19554 | 0.00018446 | 0 | 0 | 0.9697 | 0 | 1.7039 | 0.14456 | 0.13494 | 0.11559 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 6.864 | 3.358% | CZ 6A | 0 | 0 | 0.00010068 | 0.22643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22653 | 3.358% | CZ 6A | 34.0535 | 2.0471 | 0.012935 | 24.7486 | 0 | 10.1518 | 0 | 17.8377 | 1.5134 | 1.4127 | 1.2101 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 96.6185 | 3.358%
CZ 6B | 0.34621 | 0.020775 | 0.00011607 | 0.13513 | 0 | 0.075526 | 0 | 0.18404 | 0.0232 | 0.0090771 | 0.012224 | 0.0013936 | 0.0069916 | 0 | 0 | 0.028478 | 0.84315 | 0.8663% | CZ 6B | 11.1126 | 0.66682 | 0.010472 | 13.7886 | 0 | 2.4242 | 0 | 5.9072 | 0.74468 | 0.29135 | 0.39237 | 0.04473 | 0.22442 | 0 | 0 | 0.91407 | 36.5214 | 0.8663% | CZ 6B | 3.2569 | 0.19543 | 0.00018446 | 0 | 0 | 0.7105 | 0 | 1.7313 | 0.21825 | 0.085391 | 0.115 | 0.01311 | 0.065773 | 0 | 0 | 0.2679 | 6.6597 | 0.8663% | CZ 6B | 0 | 0 | 9.8428e-05 | 0.13789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13798 | 0.8663% | CZ 6B | 34.0966 | 2.046 | 0.012689 | 15.0709 | 0 | 7.4382 | 0 | 18.1249 | 2.2849 | 0.89396 | 1.2039 | 0.13725 | 0.68857 | 0 | 0 | 2.8046 | 84.8024 | 0.8663%
CZ 7 | 0.34838 | 0.020723 | 0.00012223 | 0.27928 | 0 | 0.085573 | 0 | 0.19073 | 0.014667 | 0.011245 | 0.012242 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.99984 | 0.5534% | CZ 7 | 11.1823 | 0.66516 | 0.011101 | 28.4982 | 0 | 2.7467 | 0 | 6.1222 | 0.47077 | 0.36095 | 0.39295 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 51.6336 | 0.5534% | CZ 7 | 3.2774 | 0.19495 | 0.00018446 | 0 | 0 | 0.80502 | 0 | 1.7943 | 0.13798 | 0.10579 | 0.11517 | 0.01311 | 0.065786 | 0 | 0 | 0.2679 | 6.7775 | 0.5534% | CZ 7 | 0 | 0 | 0.00010472 | 0.28498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28509 | 0.5534% | CZ 7 | 34.3106 | 2.0409 | 0.013377 | 31.1485 | 0 | 8.4277 | 0 | 18.7846 | 1.4445 | 1.1075 | 1.2057 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 102.114 | 0.5534%
CZ 8 | 0.33755 | 0.020191 | 0.00011555 | 0.34555 | 0 | 0.042105 | 0 | 0.1831 | 0.019675 | 0.0086219 | 0.012177 | 0.0013936 | 0.0069874 | 0 | 0 | 0.028478 | 1.006 | 0.05968% | CZ 8 | 10.8347 | 0.64807 | 0.010517 | 35.2606 | 0 | 1.3515 | 0 | 5.8772 | 0.63153 | 0.27674 | 0.39084 | 0.04473 | 0.22428 | 0 | 0 | 0.91407 | 56.4648 | 0.05968% | CZ 8 | 3.1755 | 0.18994 | 0.00017128 | 0 | 0 | 0.3961 | 0 | 1.7225 | 0.18509 | 0.081109 | 0.11455 | 0.01311 | 0.065733 | 0 | 0 | 0.2679 | 6.2117 | 0.05968% | CZ 8 | 0 | 0 | 9.9327e-05 | 0.35261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35271 | 0.05968% | CZ 8 | 33.244 | 1.9885 | 0.01265 | 38.5398 | 0 | 4.1468 | 0 | 18.033 | 1.9377 | 0.84913 | 1.1992 | 0.13725 | 0.68816 | 0 | 0 | 2.8046 | 103.5808 | 0.05968%
US Weighted | 0.34664 | 0.020827 | 0.00010795 | 0.063604 | 0 | 0.25036 | 0 | 0.18115 | 0.044275 | 0.020051 | 0.012549 | 0.0013936 | 0.006993 | 0 | 0 | 0.028478 | 0.97643 | 100% | US Weighted | 11.1265 | 0.66851 | 0.0097306 | 6.4902 | 0 | 8.0359 | 0 | 5.8145 | 1.4211 | 0.64359 | 0.40279 | 0.04473 | 0.22446 | 0 | 0 | 0.91407 | 35.7961 | 100% | US Weighted | 3.261 | 0.19593 | 0.00017275 | 0 | 0 | 2.3552 | 0 | 1.7041 | 0.41651 | 0.18862 | 0.11805 | 0.01311 | 0.065785 | 0 | 0 | 0.2679 | 8.5864 | 100% | US Weighted | 0 | 0 | 9.1411e-05 | 0.064902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064993 | 100% | US Weighted | 34.1393 | 2.0512 | 0.0118 | 7.0938 | 0 | 24.6564 | 0 | 17.8406 | 4.3604 | 1.9747 | 1.2359 | 0.13725 | 0.68871 | 0 | 0 | 2.8046 | 96.9946 | 100%
Building Type: | Secondary School |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Secondary School |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Secondary School |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Secondary School |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 210887 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 210887 | [17 empty] | Prototype Floor Area: | 210887 | Building Type: | Secondary School | [15 empty] | Prototype Floor Area: | 210887 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 75.92% | 68.65% | 0.3656% | 68.46% |  | 56.49% |  | 49.78% | 61.07% | 85.99% | 43.48% | 13.14% | 62.93% | 0% |  | 9.58% | 53.1% | 0% | CZ 0A | 75.92% | 68.65% | 0.567% | 68.46% |  | 56.49% |  | 49.78% | 61.07% | 85.99% | 43.48% | 13.14% | 62.93% | 0% |  | 9.58% | 51.94% | 0% | CZ 0A | 75.92% | 68.65% | 0.07766% |  |  | 56.49% |  | 49.78% | 61.07% | 85.99% | 43.48% | 13.14% | 62.93% | 0% |  | 9.58% | 53.66% | 0% | CZ 0A |  |  | 0.7984% | 68.46% | [9 empty] | 0% |  |  | 19.61% | 0% | CZ 0A | 75.92% | 68.65% | 0.3874% | 68.46% |  | 56.49% |  | 49.78% | 61.07% | 85.99% | 43.48% | 13.14% | 62.93% | 0% |  | 9.58% | 53.03% | 0%
CZ 0B | 76.03% | 68.67% | 0.09312% | 88.3% |  | 43.91% |  | 49.21% | 46.77% | 77.83% | 44.8% | 13.14% | 62.93% | 0% |  | 9.58% | 45.41% | 0% | CZ 0B | 76.03% | 68.67% | 0.1617% | 88.3% |  | 43.91% |  | 49.21% | 46.77% | 77.83% | 44.8% | 13.14% | 62.93% | 0% |  | 9.58% | 44.11% | 0% | CZ 0B | 76.03% | 68.67% | -0.006477% |  |  | 43.91% |  | 49.21% | 46.77% | 77.83% | 44.8% | 13.14% | 62.93% | 0% |  | 9.58% | 46.04% | 0% | CZ 0B |  |  | 0.2395% | 88.3% | [9 empty] | 0% |  |  | 8.907% | 0% | CZ 0B | 76.03% | 68.67% | 0.1006% | 88.3% |  | 43.91% |  | 49.21% | 46.77% | 77.83% | 44.8% | 13.14% | 62.93% | 0% |  | 9.58% | 45.33% | 0%
CZ 1A | 75.33% | 68.67% | 0.3519% | 91.91% |  | 55.26% |  | 61.8% | 59.78% | 85.59% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 52.66% | 2.407% | CZ 1A | 75.33% | 68.67% | 0.5241% | 91.91% |  | 55.26% |  | 61.8% | 59.78% | 85.59% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 51.05% | 2.407% | CZ 1A | 75.33% | 68.67% | 0.09059% |  |  | 55.26% |  | 61.8% | 59.78% | 85.59% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 53.43% | 2.407% | CZ 1A |  |  | 0.7119% | 91.91% | [9 empty] | 0% |  |  | 7.945% | 2.407% | CZ 1A | 75.33% | 68.67% | 0.3709% | 91.91% |  | 55.26% |  | 61.8% | 59.78% | 85.59% | 42.47% | 13.14% | 62.92% | 0% |  | 9.58% | 52.56% | 2.407%
CZ 1B | 75.61% | 68.69% | 0.1036% | 79.03% |  | 42% |  | 49% | 54.86% | 78.21% | 44.86% | 13.14% | 62.93% | 0% |  | 9.58% | 44.9% | 0% | CZ 1B | 75.61% | 68.69% | 0.1703% | 79.03% |  | 42% |  | 49% | 54.86% | 78.21% | 44.86% | 13.14% | 62.93% | 0% |  | 9.58% | 43.69% | 0% | CZ 1B | 75.61% | 68.69% | 0% |  |  | 42% |  | 49% | 54.86% | 78.21% | 44.86% | 13.14% | 62.93% | 0% |  | 9.58% | 45.5% | 0% | CZ 1B |  |  | 0.2417% | 79.03% | [9 empty] | 0% |  |  | 19.54% | 0% | CZ 1B | 75.61% | 68.69% | 0.111% | 79.03% |  | 42% |  | 49% | 54.86% | 78.21% | 44.86% | 13.14% | 62.93% | 0% |  | 9.58% | 44.82% | 0%
CZ 2A | 75.56% | 68.7% | 0.3058% | 82.06% |  | 56.91% |  | 63.49% | 61.77% | 84.92% | 42.66% | 13.14% | 62.92% | 0% |  | 9.58% | 53.52% | 17.03% | CZ 2A | 75.56% | 68.7% | 0.4373% | 82.06% |  | 56.91% |  | 63.49% | 61.77% | 84.92% | 42.66% | 13.14% | 62.92% | 0% |  | 9.58% | 52.05% | 17.03% | CZ 2A | 75.56% | 68.7% | 0.09059% |  |  | 56.91% |  | 63.49% | 61.77% | 84.92% | 42.66% | 13.14% | 62.92% | 0% |  | 9.58% | 54.26% | 17.03% | CZ 2A |  |  | 0.5724% | 82.06% | [9 empty] | 0% |  |  | 24.21% | 17.03% | CZ 2A | 75.56% | 68.7% | 0.3207% | 82.06% |  | 56.91% |  | 63.49% | 61.77% | 84.92% | 42.66% | 13.14% | 62.92% | 0% |  | 9.58% | 53.43% | 17.03%
CZ 2B | 75.05% | 68.69% | 0.1031% | 89.4% |  | 44.67% |  | 55.68% | 47.32% | 80.15% | 44.61% | 13.14% | 62.92% | 0% |  | 9.58% | 46.71% | 1.76% | CZ 2B | 75.05% | 68.69% | 0.1656% | 89.4% |  | 44.67% |  | 55.68% | 47.32% | 80.15% | 44.61% | 13.14% | 62.92% | 0% |  | 9.58% | 45.44% | 1.76% | CZ 2B | 75.05% | 68.69% | 0% |  |  | 44.67% |  | 55.68% | 47.32% | 80.15% | 44.61% | 13.14% | 62.92% | 0% |  | 9.58% | 47.35% | 1.76% | CZ 2B |  |  | 0.2294% | 89.4% | [9 empty] | 0% |  |  | 26.67% | 1.76% | CZ 2B | 75.05% | 68.69% | 0.1102% | 89.4% |  | 44.67% |  | 55.68% | 47.32% | 80.15% | 44.61% | 13.14% | 62.92% | 0% |  | 9.58% | 46.62% | 1.76%
CZ 3A | 75.16% | 68.69% | 0.2557% | 63.28% |  | 53.3% |  | 63.19% | 60% | 83.71% | 42.36% | 13.14% | 62.92% | 0% |  | 9.58% | 51.04% | 19.81% | CZ 3A | 75.16% | 68.69% | 0.3466% | 63.28% |  | 53.3% |  | 63.19% | 60% | 83.71% | 42.36% | 13.14% | 62.92% | 0% |  | 9.58% | 49.47% | 19.81% | CZ 3A | 75.16% | 68.69% | 0.09059% |  |  | 53.3% |  | 63.19% | 60% | 83.71% | 42.36% | 13.14% | 62.92% | 0% |  | 9.58% | 51.88% | 19.81% | CZ 3A |  |  | 0.4331% | 63.28% | [9 empty] | 0% |  |  | 35.18% | 19.81% | CZ 3A | 75.16% | 68.69% | 0.2663% | 63.28% |  | 53.3% |  | 63.19% | 60% | 83.71% | 42.36% | 13.14% | 62.92% | 0% |  | 9.58% | 50.93% | 19.81%
CZ 3B | 74.89% | 68.69% | 0.09997% | 40.89% |  | 40.24% |  | 57.51% | 100% | 77.48% | 44.48% | 13.14% | 62.92% | 0% |  | 9.58% | 46.83% | 7.027% | CZ 3B | 74.89% | 68.69% | 0.1528% | 40.89% |  | 40.24% |  | 57.51% | 100% | 77.48% | 44.48% | 13.14% | 62.92% | 0% |  | 9.58% | 44.29% | 7.027% | CZ 3B | 74.89% | 68.69% | 0.006476% |  |  | 40.24% |  | 57.51% | 100% | 77.48% | 44.48% | 13.14% | 62.92% | 0% |  | 9.58% | 48.15% | 7.027% | CZ 3B |  |  | 0.204% | 40.89% | [9 empty] | 0% |  |  | 14.74% | 7.027% | CZ 3B | 74.89% | 68.69% | 0.1061% | 40.89% |  | 40.24% |  | 57.51% | 100% | 77.48% | 44.48% | 13.14% | 62.92% | 0% |  | 9.58% | 46.67% | 7.027%
CZ 3C | 74.75% | 68.57% | 0.24% | 71.34% |  | 47.53% |  | 64.78% |  | 84.98% | 42.57% | 13.14% | 62.92% | 0% |  | 9.58% | 48.94% | 1.237% | CZ 3C | 74.75% | 68.57% | 0.3192% | 71.34% |  | 47.53% |  | 64.78% |  | 84.98% | 42.57% | 13.14% | 62.92% | 0% |  | 9.58% | 47.08% | 1.237% | CZ 3C | 74.75% | 68.57% | 0.09706% |  |  | 47.53% |  | 64.78% |  | 84.98% | 42.57% | 13.14% | 62.92% | 0% |  | 9.58% | 49.92% | 1.237% | CZ 3C |  |  | 0.3949% | 71.34% | [9 empty] | 0% |  |  | 27.79% | 1.237% | CZ 3C | 74.75% | 68.57% | 0.2492% | 71.34% |  | 47.53% |  | 64.78% |  | 84.98% | 42.57% | 13.14% | 62.92% | 0% |  | 9.58% | 48.82% | 1.237%
CZ 4A | 74.88% | 68.48% | 0.2686% | 81.67% |  | 50.62% |  | 62.52% | 54.6% | 81.89% | 42.17% | 13.14% | 62.92% | 0% |  | 9.58% | 51.42% | 18.1% | CZ 4A | 74.88% | 68.48% | 0.3566% | 81.67% |  | 50.62% |  | 62.52% | 54.6% | 81.89% | 42.17% | 13.14% | 62.92% | 0% |  | 9.58% | 52.96% | 18.1% | CZ 4A | 74.88% | 68.48% | 0.09706% |  |  | 50.62% |  | 62.52% | 54.6% | 81.89% | 42.17% | 13.14% | 62.92% | 0% |  | 9.58% | 50.48% | 18.1% | CZ 4A |  |  | 0.4366% | 81.67% | [9 empty] | 0% |  |  | 60.37% | 18.1% | CZ 4A | 74.88% | 68.48% | 0.2791% | 81.67% |  | 50.62% |  | 62.52% | 54.6% | 81.89% | 42.17% | 13.14% | 62.92% | 0% |  | 9.58% | 51.53% | 18.1%
CZ 4B | 75.26% | 68.67% | 0.2752% | 55.89% |  | 45.01% |  | 62.48% | 100% | 82.12% | 42.11% | 13.14% | 62.92% | 0% |  | 9.58% | 49.77% | 0.6509% | CZ 4B | 75.26% | 68.67% | 0.3686% | 55.89% |  | 45.01% |  | 62.48% | 100% | 82.12% | 42.11% | 13.14% | 62.92% | 0% |  | 9.58% | 47.7% | 0.6509% | CZ 4B | 75.26% | 68.67% | 0.09706% |  |  | 45.01% |  | 62.48% | 100% | 82.12% | 42.11% | 13.14% | 62.92% | 0% |  | 9.58% | 50.93% | 0.6509% | CZ 4B |  |  | 0.4545% | 55.89% | [9 empty] | 0% |  |  | 32.97% | 0.6509% | CZ 4B | 75.26% | 68.67% | 0.2863% | 55.89% |  | 45.01% |  | 62.48% | 100% | 82.12% | 42.11% | 13.14% | 62.92% | 0% |  | 9.58% | 49.63% | 0.6509%
CZ 4C | 74.34% | 68.42% | 0.2208% | 36.06% |  | 34.78% |  | 60.34% | 100% | 65.59% | 42.14% | 13.14% | 62.9% | 0% |  | 9.58% | 46.88% | 2.48% | CZ 4C | 74.34% | 68.42% | 0.2837% | 36.06% |  | 34.78% |  | 60.34% | 100% | 65.59% | 42.14% | 13.14% | 62.9% | 0% |  | 9.58% | 43.09% | 2.48% | CZ 4C | 74.34% | 68.42% | 0.09706% |  |  | 34.78% |  | 60.34% | 100% | 65.59% | 42.14% | 13.14% | 62.9% | 0% |  | 9.58% | 49.16% | 2.48% | CZ 4C |  |  | 0.3404% | 36.06% | [9 empty] | 0% |  |  | 23.29% | 2.48% | CZ 4C | 74.34% | 68.42% | 0.2283% | 36.06% |  | 34.78% |  | 60.34% | 100% | 65.59% | 42.14% | 13.14% | 62.9% | 0% |  | 9.58% | 46.61% | 2.48%
CZ 5A | 75.14% | 68.6% | 0.2511% | 66.99% |  | 44.18% |  | 61.24% | 41.39% | 85.69% | 42% | 13.14% | 62.92% | 0% |  | 9.58% | 48.93% | 19.94% | CZ 5A | 75.14% | 68.6% | 0.3292% | 66.99% |  | 44.18% |  | 61.24% | 41.39% | 85.69% | 42% | 13.14% | 62.92% | 0% |  | 9.58% | 49.39% | 19.94% | CZ 5A | 75.14% | 68.6% | 0.09059% |  |  | 44.18% |  | 61.24% | 41.39% | 85.69% | 42% | 13.14% | 62.92% | 0% |  | 9.58% | 48.62% | 19.94% | CZ 5A |  |  | 0.3978% | 66.99% | [9 empty] | 0% |  |  | 51.17% | 19.94% | CZ 5A | 75.14% | 68.6% | 0.2606% | 66.99% |  | 44.18% |  | 61.24% | 41.39% | 85.69% | 42% | 13.14% | 62.92% | 0% |  | 9.58% | 48.96% | 19.94%
CZ 5B | 74.99% | 68.53% | 0.263% | 37.16% |  | 47.62% |  | 63.31% | 100% | 77.91% | 42.06% | 13.14% | 62.92% | 0% |  | 9.58% | 49.56% | 4.639% | CZ 5B | 74.99% | 68.53% | 0.345% | 37.16% |  | 47.62% |  | 63.31% | 100% | 77.91% | 42.06% | 13.14% | 62.92% | 0% |  | 9.58% | 45.65% | 4.639% | CZ 5B | 74.99% | 68.53% | 0.09706% |  |  | 47.62% |  | 63.31% | 100% | 77.91% | 42.06% | 13.14% | 62.92% | 0% |  | 9.58% | 51.92% | 4.639% | CZ 5B |  |  | 0.4178% | 37.16% | [9 empty] | 0% |  |  | 25.82% | 4.639% | CZ 5B | 74.99% | 68.53% | 0.2729% | 37.16% |  | 47.62% |  | 63.31% | 100% | 77.91% | 42.06% | 13.14% | 62.92% | 0% |  | 9.58% | 49.28% | 4.639%
CZ 5C | 74.61% | 68.44% | 0.2185% | 71.19% |  | 22.37% |  | 59.97% | 29.65% | 63.72% | 42.09% | 13.14% | 62.9% | 0% |  | 9.58% | 46.49% | 0.08039% | CZ 5C | 74.61% | 68.44% | 0.2785% | 71.19% |  | 22.37% |  | 59.97% | 29.65% | 63.72% | 42.09% | 13.14% | 62.9% | 0% |  | 9.58% | 46.62% | 0.08039% | CZ 5C | 74.61% | 68.44% | 0.09706% |  |  | 22.37% |  | 59.97% | 29.65% | 63.72% | 42.09% | 13.14% | 62.9% | 0% |  | 9.58% | 46.4% | 0.08039% | CZ 5C |  |  | 0.3317% | 71.19% | [9 empty] | 0% |  |  | 47.25% | 0.08039% | CZ 5C | 74.61% | 68.44% | 0.2258% | 71.19% |  | 22.37% |  | 59.97% | 29.65% | 63.72% | 42.09% | 13.14% | 62.9% | 0% |  | 9.58% | 46.5% | 0.08039%
CZ 6A | 74.93% | 68.53% | 0.2535% | 69.41% |  | 44.26% |  | 60.67% | 29.5% | 85.84% | 42.02% | 13.14% | 62.92% | 0% |  | 9.58% | 50.59% | 3.358% | CZ 6A | 74.93% | 68.53% | 0.3295% | 69.41% |  | 44.26% |  | 60.67% | 29.5% | 85.84% | 42.02% | 13.14% | 62.92% | 0% |  | 9.58% | 53.47% | 3.358% | CZ 6A | 74.93% | 68.53% | 0.09059% |  |  | 44.26% |  | 60.67% | 29.5% | 85.84% | 42.02% | 13.14% | 62.92% | 0% |  | 9.58% | 48.25% | 3.358% | CZ 6A |  |  | 0.3946% | 69.41% | [9 empty] | 0% |  |  | 60.21% | 3.358% | CZ 6A | 74.93% | 68.53% | 0.2629% | 69.41% |  | 44.26% |  | 60.67% | 29.5% | 85.84% | 42.02% | 13.14% | 62.92% | 0% |  | 9.58% | 50.84% | 3.358%
CZ 6B | 75.02% | 68.54% | 0.2508% | 68.38% |  | 45.88% |  | 61.53% | 38.83% | 86.36% | 41.97% | 13.14% | 62.9% | 0% |  | 9.58% | 49.83% | 0.8663% | CZ 6B | 75.02% | 68.54% | 0.3265% | 68.38% |  | 45.88% |  | 61.53% | 38.83% | 86.36% | 41.97% | 13.14% | 62.9% | 0% |  | 9.58% | 51.06% | 0.8663% | CZ 6B | 75.02% | 68.54% | 0.09059% |  |  | 45.88% |  | 61.53% | 38.83% | 86.36% | 41.97% | 13.14% | 62.9% | 0% |  | 9.58% | 48.96% | 0.8663% | CZ 6B |  |  | 0.3917% | 68.38% | [9 empty] | 0% |  |  | 54.92% | 0.8663% | CZ 6B | 75.02% | 68.54% | 0.2601% | 68.38% |  | 45.88% |  | 61.53% | 38.83% | 86.36% | 41.97% | 13.14% | 62.9% | 0% |  | 9.58% | 49.93% | 0.8663%
CZ 7 | 75.49% | 68.41% | 0.2543% | 70.09% |  | 44.81% |  | 61.32% | 28.34% | 76.82% | 41.95% | 13.14% | 62.92% | 0% |  | 9.58% | 51.83% | 0.5534% | CZ 7 | 75.49% | 68.41% | 0.3274% | 70.09% |  | 44.81% |  | 61.32% | 28.34% | 76.82% | 41.95% | 13.14% | 62.92% | 0% |  | 9.58% | 55.33% | 0.5534% | CZ 7 | 75.49% | 68.41% | 0.09059% |  |  | 44.81% |  | 61.32% | 28.34% | 76.82% | 41.95% | 13.14% | 62.92% | 0% |  | 9.58% | 48.67% | 0.5534% | CZ 7 |  |  | 0.3885% | 70.09% | [9 empty] | 0% |  |  | 62.24% | 0.5534% | CZ 7 | 75.49% | 68.41% | 0.2634% | 70.09% |  | 44.81% |  | 61.32% | 28.34% | 76.82% | 41.95% | 13.14% | 62.92% | 0% |  | 9.58% | 52.14% | 0.5534%
CZ 8 | 73.15% | 67.03% | 0.2321% | 62.24% |  | 45.49% |  | 59.47% | 35.46% | 79.4% | 41.86% | 13.14% | 62.87% | 0% |  | 9.58% | 50.66% | 0.05968% | CZ 8 | 73.15% | 67.03% | 0.2949% | 62.24% |  | 45.49% |  | 59.47% | 35.46% | 79.4% | 41.86% | 13.14% | 62.87% | 0% |  | 9.58% | 53.16% | 0.05968% | CZ 8 | 73.15% | 67.03% | 0.08412% |  |  | 45.49% |  | 59.47% | 35.46% | 79.4% | 41.86% | 13.14% | 62.87% | 0% |  | 9.58% | 47.9% | 0.05968% | CZ 8 |  |  | 0.3459% | 62.24% | [9 empty] | 0% |  |  | 56.91% | 0.05968% | CZ 8 | 73.15% | 67.03% | 0.24% | 62.24% |  | 45.49% |  | 59.47% | 35.46% | 79.4% | 41.86% | 13.14% | 62.87% | 0% |  | 9.58% | 50.9% | 0.05968%
US Weighted | 75.12% | 68.61% | 0.2536% | 68.58% | 0% | 49.3% | 0% | 62% | 59.14% | 82.85% | 42.46% | 13.14% | 62.92% | 0% | 0% | 9.58% | 50.55% | 100% | US Weighted | 75.12% | 68.61% | 0.3451% | 68.58% | 0% | 49.3% | 0% | 62% | 59.14% | 82.85% | 42.46% | 13.14% | 62.92% | 0% | 0% | 9.58% | 49.93% | 100% | US Weighted | 75.12% | 68.61% | 0.08484% | 0% | 0% | 49.3% | 0% | 62% | 59.14% | 82.85% | 42.46% | 13.14% | 62.92% | 0% | 0% | 9.58% | 50.81% | 100% | US Weighted | 0% | 0% | 0.4321% | 68.58% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.17% | 100% | US Weighted | 75.12% | 68.61% | 0.2643% | 68.58% | 0% | 49.3% | 0% | 62% | 59.14% | 82.85% | 42.46% | 13.14% | 62.92% | 0% | 0% | 9.58% | 50.51% | 100%

## MedOP
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 40946 |  | Building Type: | Outpatient Healthcare |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 |  | Building Type: | Outpatient Healthcare |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Outpatient Healthcare |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Outpatient Healthcare | [14 empty] | Prototype Floor Area: | 40946 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.27495 | 0.039444 | 0.049662 | 0.23478 | 0.094266 | 0.51799 | 0 | 0.24466 | 0 | 0.0024475 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8206 |  | STD2019 | 8.8254 | 1.2661 | 5.0676 | 15.0651 | 3.0257 | 16.6263 | 0 | 7.8529 | 0 | 0.07856 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 104.5255 |  | STD2019 | 2.5866 | 0.37106 | 0 | 1.196 | 0.88679 | 4.8729 | 0 | 2.3016 | 0 | 0.023025 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.6522 |  | STD2019 | 0 | 0 | 0.050676 | 0.10984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20412 |  | STD2019 | 27.0788 | 3.8846 | 5.5389 | 24.527 | 9.2838 | 51.0144 | 0 | 24.095 | 0 | 0.24105 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 280.3943
STD2016 | 0.33387 | 0.039444 | 0.049663 | 0.25333 | 0.094302 | 0.5277 | 0 | 0.25163 | 0 | 0.0025319 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9148 |  | STD2016 | 10.7164 | 1.2661 | 5.0676 | 15.931 | 3.0269 | 16.9379 | 0 | 8.0769 | 0 | 0.081267 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.8218 |  | STD2016 | 3.1408 | 0.37106 | 0 | 1.3342 | 0.88713 | 4.9642 | 0 | 2.3672 | 0 | 0.023818 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 25.5026 |  | STD2016 | 0 | 0 | 0.050676 | 0.11379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20807 |  | STD2016 | 32.8809 | 3.8846 | 5.5389 | 26.4044 | 9.2874 | 51.9704 | 0 | 24.7823 | 0 | 0.24935 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 289.7289
STD2013 | 0.3627 | 0.080985 | 0.055544 | 0.28838 | 0.093399 | 0.54363 | 0 | 0.27289 | 0.012435 | 0.0028758 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.0752 |  | STD2013 | 11.642 | 2.5994 | 5.6678 | 17.5885 | 2.9979 | 17.4494 | 0 | 8.7593 | 0.39914 | 0.092308 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 113.9136 |  | STD2013 | 3.4121 | 0.76185 | 0 | 1.5922 | 0.87864 | 5.1141 | 0 | 2.5672 | 0.11698 | 0.027054 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.8844 |  | STD2013 | 0 | 0 | 0.056678 | 0.12156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22184 |  | STD2013 | 35.721 | 7.9759 | 6.1949 | 29.9549 | 9.1985 | 53.5397 | 0 | 26.8761 | 1.2247 | 0.28323 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 305.6996
STD2010 | 0.39034 | 0.080985 | 0.055545 | 0.35466 | 0.12578 | 0.56159 | 0 | 0.29077 | 0.012491 | 0.0027878 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.2404 |  | STD2010 | 12.5289 | 2.5994 | 5.6678 | 19.6761 | 4.0373 | 18.0257 | 0 | 9.3332 | 0.40094 | 0.089482 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 119.1772 |  | STD2010 | 3.672 | 0.76185 | 0 | 2.2211 | 1.1833 | 5.283 | 0 | 2.7354 | 0.11751 | 0.026226 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 28.4441 |  | STD2010 | 0 | 0 | 0.056678 | 0.12098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22126 |  | STD2010 | 38.4423 | 7.9759 | 6.1949 | 36.4754 | 12.3875 | 55.3081 | 0 | 28.637 | 1.2302 | 0.27456 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 321.9648
STD2007 | 0.44094 | 0.16367 | 0.056291 | 0.6029 | 0.098189 | 0.754 | 0 | 0.37155 | 0 | 0.0030606 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.8704 |  | STD2007 | 14.1533 | 5.2533 | 5.7439 | 29.0975 | 3.1517 | 24.2017 | 0 | 11.926 | 0 | 0.098238 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 140.9041 |  | STD2007 | 4.1481 | 1.5397 | 0 | 4.3609 | 0.9237 | 7.0931 | 0 | 3.4953 | 0 | 0.028792 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.1681 |  | STD2007 | 0 | 0 | 0.057439 | 0.14218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24323 |  | STD2007 | 43.4265 | 16.1186 | 6.2781 | 61.1944 | 9.6702 | 74.2579 | 0 | 36.5925 | 0 | 0.30142 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 384.2903
STD2004 | 0.44094 | 0.16367 | 0.05629 | 0.73425 | 0.12064 | 0.79807 | 0 | 0.41124 | 0 | 0.0034673 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1084 |  | STD2004 | 14.1533 | 5.2533 | 5.7439 | 35.1462 | 3.8724 | 25.6162 | 0 | 13.1999 | 0 | 0.11129 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 150.3748 |  | STD2004 | 4.1481 | 1.5397 | 0 | 5.35 | 1.1349 | 7.5077 | 0 | 3.8687 | 0 | 0.032618 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.1602 |  | STD2004 | 0 | 0 | 0.057439 | 0.16892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26996 |  | STD2004 | 43.4265 | 16.1186 | 6.278 | 74.472 | 11.8816 | 78.5979 | 0 | 40.5011 | 0 | 0.34148 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 408.0678
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | -7.8271e-07 | 0.13135 | 0.022454 | 0.044067 | 0 | 0.039687 | 0 | 0.00040676 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23796 |  | 2004-2007 | 0 | 0 | -7.9868e-05 | 6.0487 | 0.72073 | 1.4145 | 0 | 1.2739 | 0 | 0.013056 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4708 |  | 2004-2007 | 0 | 0 | 0 | 0.98912 | 0.21123 | 0.41455 | 0 | 0.37335 | 0 | 0.0038265 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9921 |  | 2004-2007 | 0 | 0 | -7.9868e-07 | 0.026738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026738 |  | 2004-2007 | 0 | 0 | -8.7296e-05 | 13.2776 | 2.2114 | 4.34 | 0 | 3.9086 | 0 | 0.040059 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7776
2007-2010 | 0.050608 | 0.08268 | 0.00074601 | 0.24824 | -0.027591 | 0.19241 | 0 | 0.080778 | -0.012491 | 0.00027279 | 0 | 0.0079204 | 0 | 0 | 0 | 0.0064128 | 0.62999 |  | 2007-2010 | 1.6244 | 2.6538 | 0.076123 | 9.4214 | -0.8856 | 6.176 | 0 | 2.5928 | -0.40094 | 0.0087559 | 0 | 0.25423 | 0 | 0 | 0 | 0.20584 | 21.7269 |  | 2007-2010 | 0.47609 | 0.7778 | 0 | 2.1398 | -0.25955 | 1.8101 | 0 | 0.75991 | -0.11751 | 0.0025662 | 0 | 0.07451 | 0 | 0 | 0 | 0.060327 | 5.724 |  | 2007-2010 | 0 | 0 | 0.00076123 | 0.021205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021966 |  | 2007-2010 | 4.9842 | 8.1428 | 0.083203 | 24.719 | -2.7173 | 18.9498 | 0 | 7.9555 | -1.2302 | 0.026866 | 0 | 0.78004 | 0 | 0 | 0 | 0.63156 | 62.3254
2010-2013 | 0.027632 | 0 | 2.1268e-07 | 0.066283 | 0.032381 | 0.017955 | 0 | 0.01788 | 5.5956e-05 | -8.804e-05 | 0 | 0.0012768 | 0 | 0 | 0 | 0.0018539 | 0.16523 |  | 2010-2013 | 0.88691 | 0 | 2.1702e-05 | 2.0876 | 1.0393 | 0.57633 | 0 | 0.57392 | 0.0017961 | -0.0028259 | 0 | 0.040982 | 0 | 0 | 0 | 0.059505 | 5.2636 |  | 2010-2013 | 0.25994 | 0 | 0 | 0.62892 | 0.30461 | 0.16891 | 0 | 0.16821 | 0.0005264 | -0.00082822 | 0 | 0.012011 | 0 | 0 | 0 | 0.01744 | 1.5597 |  | 2010-2013 | 0 | 0 | 2.1702e-07 | -0.00058215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00058193 |  | 2010-2013 | 2.7213 | 0 | 2.3721e-05 | 6.5205 | 3.189 | 1.7683 | 0 | 1.761 | 0.0055109 | -0.0086707 | 0 | 0.12574 | 0 | 0 | 0 | 0.18258 | 16.2653
2013-2016 | 0.028838 | 0.041542 | 0.0058815 | 0.035042 | -0.00090253 | 0.015935 | 0 | 0.02126 | 0.012435 | 0.00034399 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16037 |  | 2013-2016 | 0.92563 | 1.3334 | 0.60016 | 1.6575 | -0.028969 | 0.51148 | 0 | 0.68241 | 0.39914 | 0.011041 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0918 |  | 2013-2016 | 0.27129 | 0.3908 | 0 | 0.258 | -0.0084904 | 0.14991 | 0 | 0.2 | 0.11698 | 0.003236 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3817 |  | 2013-2016 | 0 | 0 | 0.0060016 | 0.007772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013774 |  | 2013-2016 | 2.8401 | 4.0912 | 0.65597 | 3.5505 | -0.088886 | 1.5694 | 0 | 2.0938 | 1.2247 | 0.033878 | 0 | 0 | 0 | 0 | 0 | 0 | 15.9707
2016-2019 | 0.058913 | 0 | 4.0796e-07 | 0.018551 | 3.5773e-05 | 0.0097065 | 0 | 0.0069782 | 0 | 8.4324e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094269 |  | 2016-2019 | 1.891 | 0 | 4.1629e-05 | 0.86586 | 0.0011482 | 0.31156 | 0 | 0.22398 | 0 | 0.0027066 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2963 |  | 2016-2019 | 0.55422 | 0 | 0 | 0.13814 | 0.00033652 | 0.091313 | 0 | 0.065646 | 0 | 0.00079326 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85045 |  | 2016-2019 | 0 | 0 | 4.1629e-07 | 0.0039452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039456 |  | 2016-2019 | 5.8021 | 0 | 4.55e-05 | 1.8774 | 0.0035231 | 0.95595 | 0 | 0.68725 | 0 | 0.0083047 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3346
2004-2019 | 0.16599 | 0.12422 | 0.0066274 | 0.49946 | 0.026377 | 0.28008 | 0 | 0.16658 | 0 | 0.0010198 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2878 |  | 2004-2019 | 5.3279 | 3.9872 | 0.67626 | 20.0811 | 0.84665 | 8.9899 | 0 | 5.347 | 0 | 0.032734 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 45.8493 |  | 2004-2019 | 1.5615 | 1.1686 | 0 | 4.154 | 0.24814 | 2.6348 | 0 | 1.5671 | 0 | 0.0095938 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.508 |  | 2004-2019 | 0 | 0 | 0.0067626 | 0.059078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065841 |  | 2004-2019 | 16.3477 | 12.234 | 0.73916 | 49.945 | 2.5978 | 27.5835 | 0 | 16.4061 | 0 | 0.10044 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 127.6735
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.001391% | 17.89% | 18.61% | 5.522% |  | 9.651% |  | 11.73% |  | 0% |  |  |  | 0% | 5.792% |  | 2004-2007 | 0% | 0% | -0.001391% | 17.21% | 18.61% | 5.522% |  | 9.651% |  | 11.73% |  | 0% |  |  |  | 0% | 6.298% |  | 2004-2007 | 0% | 0% |  | 18.49% | 18.61% | 5.522% |  | 9.651% |  | 11.73% |  | 0% |  |  |  | 0% | 5.509% |  | 2004-2007 |  |  | -0.001391% | 15.83% | [11 empty] | 0% | 9.904% |  | 2004-2007 | 0% | 0% | -0.001391% | 17.83% | 18.61% | 5.522% |  | 9.651% |  | 11.73% |  | 0% |  |  |  | 0% | 5.827%
2007-2010 | 11.48% | 50.52% | 1.325% | 41.17% | -28.1% | 25.52% |  | 21.74% |  | 8.913% |  | 1.684% |  |  |  | 0.7051% | 16.28% |  | 2007-2010 | 11.48% | 50.52% | 1.325% | 32.38% | -28.1% | 25.52% |  | 21.74% |  | 8.913% |  | 1.684% |  |  |  | 0.6396% | 15.42% |  | 2007-2010 | 11.48% | 50.52% |  | 49.07% | -28.1% | 25.52% |  | 21.74% |  | 8.913% |  | 1.684% |  |  |  | 0.7398% | 16.75% |  | 2007-2010 |  |  | 1.325% | 14.91% | [11 empty] | 0% | 9.031% |  | 2007-2010 | 11.48% | 50.52% | 1.325% | 40.39% | -28.1% | 25.52% |  | 21.74% |  | 8.913% |  | 1.684% |  |  |  | 0.7007% | 16.22%
2010-2013 | 7.079% | 0% | 0.0003829% | 18.69% | 25.74% | 3.197% |  | 6.149% | 0.448% | -3.158% |  | 0.2761% |  |  |  | 0.2053% | 5.099% |  | 2010-2013 | 7.079% | 0% | 0.0003829% | 10.61% | 25.74% | 3.197% |  | 6.149% | 0.448% | -3.158% |  | 0.2761% |  |  |  | 0.1861% | 4.417% |  | 2010-2013 | 7.079% | 0% |  | 28.32% | 25.74% | 3.197% |  | 6.149% | 0.448% | -3.158% |  | 0.2761% |  |  |  | 0.2155% | 5.484% |  | 2010-2013 |  |  | 0.0003829% | -0.4812% | [11 empty] | 0% | -0.263% |  | 2010-2013 | 7.079% | 0% | 0.0003829% | 17.88% | 25.74% | 3.197% |  | 6.149% | 0.448% | -3.158% |  | 0.2761% |  |  |  | 0.204% | 5.052%
2013-2016 | 7.951% | 51.3% | 10.59% | 12.15% | -0.9663% | 2.931% |  | 7.791% | 100% | 11.96% |  | 0% |  |  |  | 0% | 5.215% |  | 2013-2016 | 7.951% | 51.3% | 10.59% | 9.424% | -0.9663% | 2.931% |  | 7.791% | 100% | 11.96% |  | 0% |  |  |  | 0% | 5.348% |  | 2013-2016 | 7.951% | 51.3% |  | 16.2% | -0.9663% | 2.931% |  | 7.791% | 100% | 11.96% |  | 0% |  |  |  | 0% | 5.139% |  | 2013-2016 |  |  | 10.59% | 6.394% | [11 empty] | 0% | 6.209% |  | 2013-2016 | 7.951% | 51.3% | 10.59% | 11.85% | -0.9663% | 2.931% |  | 7.791% | 100% | 11.96% |  | 0% |  |  |  | 0% | 5.224%
2016-2019 | 17.65% | 0% | 0.0008215% | 7.323% | 0.03793% | 1.839% |  | 2.773% |  | 3.331% |  | 0% |  |  |  | 0% | 3.234% |  | 2016-2019 | 17.65% | 0% | 0.0008215% | 5.435% | 0.03793% | 1.839% |  | 2.773% |  | 3.331% |  | 0% |  |  |  | 0% | 3.057% |  | 2016-2019 | 17.65% | 0% |  | 10.35% | 0.03793% | 1.839% |  | 2.773% |  | 3.331% |  | 0% |  |  |  | 0% | 3.335% |  | 2016-2019 |  |  | 0.0008215% | 3.467% | [11 empty] | 0% | 1.896% |  | 2016-2019 | 17.65% | 0% | 0.0008215% | 7.11% | 0.03793% | 1.839% |  | 2.773% |  | 3.331% |  | 0% |  |  |  | 0% | 3.222%
2004-2019 | 37.64% | 75.9% | 11.77% | 68.02% | 21.86% | 35.09% |  | 40.51% |  | 29.41% |  | 1.955% |  |  |  | 0.9089% | 31.35% |  | 2004-2019 | 37.64% | 75.9% | 11.77% | 57.14% | 21.86% | 35.09% |  | 40.51% |  | 29.41% |  | 1.955% |  |  |  | 0.8245% | 30.49% |  | 2004-2019 | 37.64% | 75.9% |  | 77.64% | 21.86% | 35.09% |  | 40.51% |  | 29.41% |  | 1.955% |  |  |  | 0.9537% | 31.83% |  | 2004-2019 |  |  | 11.77% | 34.97% | [11 empty] | 0% | 24.39% |  | 2004-2019 | 37.64% | 75.9% | 11.77% | 67.07% | 21.86% | 35.09% |  | 40.51% |  | 29.41% |  | 1.955% |  |  |  | 0.9033% | 31.29%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.27415 | 0.038477 | 0.046475 | 0.14177 | 0 | 1.4706 | 0 | 0.27484 | 0 | 0.0016952 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.6103 | 0% | CZ 0A | 8.7998 | 1.235 | 4.7423 | 8.5446 | 0 | 47.2021 | 0 | 8.8217 | 0 | 0.054411 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 126.1177 | 0% | CZ 0A | 2.5791 | 0.36196 | 0 | 0.79653 | 0 | 13.8341 | 0 | 2.5855 | 0 | 0.015947 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 32.5874 | 0% | CZ 0A | 0 | 0 | 0.047423 | 0.058268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.1493 | 0% | CZ 0A | 27.0002 | 3.7894 | 5.1834 | 14.7076 | 0 | 144.8296 | 0 | 27.0677 | 0 | 0.16695 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 357.4754 | 0%
CZ 0B | 0.27466 | 0.03914 | 0.046475 | 0.16324 | 0.0003751 | 1.2831 | 0 | 0.25756 | 0 | 0.0018466 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.4288 | 0% | CZ 0B | 8.816 | 1.2563 | 4.7423 | 9.7269 | 0.01204 | 41.1851 | 0 | 8.2672 | 0 | 0.059273 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 120.7829 | 0% | CZ 0B | 2.5838 | 0.3682 | 0 | 0.93218 | 0.0035287 | 12.0707 | 0 | 2.423 | 0 | 0.017372 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 30.813 | 0% | CZ 0B | 0 | 0 | 0.047423 | 0.065462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15649 | 0% | CZ 0B | 27.0499 | 3.8547 | 5.1834 | 16.9141 | 0.036942 | 126.3679 | 0 | 25.3662 | 0 | 0.18187 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 339.6857 | 0%
CZ 1A | 0.27548 | 0.039313 | 0.046475 | 0.15967 | 0 | 1.0828 | 0 | 0.2529 | 0 | 0.0018827 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.2209 | 1.601% | CZ 1A | 8.8424 | 1.2619 | 4.7423 | 9.4014 | 0 | 34.7568 | 0 | 8.1176 | 0 | 0.060431 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 113.9006 | 1.601% | CZ 1A | 2.5915 | 0.36983 | 0 | 0.92696 | 0 | 10.1866 | 0 | 2.3791 | 0 | 0.017711 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 28.8861 | 1.601% | CZ 1A | 0 | 0 | 0.047423 | 0.062386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15341 | 1.601% | CZ 1A | 27.1309 | 3.8718 | 5.1834 | 16.5231 | 0 | 106.6438 | 0 | 24.9073 | 0 | 0.18542 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 319.1764 | 1.601%
CZ 1B | 0.27535 | 0.039183 | 0.046679 | 0.15306 | 0.00075741 | 1.0937 | 0 | 0.24927 | 0 | 0.0016158 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.222 | 0% | CZ 1B | 8.8382 | 1.2577 | 4.7632 | 9.1004 | 0.024311 | 35.1055 | 0 | 8.0012 | 0 | 0.051864 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 113.8601 | 0% | CZ 1B | 2.5903 | 0.36861 | 0 | 0.87661 | 0.0071252 | 10.2888 | 0 | 2.345 | 0 | 0.0152 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 28.906 | 0% | CZ 1B | 0 | 0 | 0.047632 | 0.061094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15233 | 0% | CZ 1B | 27.1181 | 3.859 | 5.2061 | 15.8548 | 0.074594 | 107.7137 | 0 | 24.5499 | 0 | 0.15913 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 319.2661 | 0%
CZ 2A | 0.27514 | 0.03932 | 0.046815 | 0.20493 | 0.014651 | 0.96223 | 0 | 0.23863 | 0 | 0.0018178 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.1459 | 15.85% | CZ 2A | 8.8315 | 1.2621 | 4.777 | 11.114 | 0.47025 | 30.8855 | 0 | 7.6594 | 0 | 0.058347 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 111.7759 | 15.85% | CZ 2A | 2.5884 | 0.3699 | 0 | 1.3178 | 0.13782 | 9.052 | 0 | 2.2449 | 0 | 0.017101 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 28.1421 | 15.85% | CZ 2A | 0 | 0 | 0.04777 | 0.066178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15755 | 15.85% | CZ 2A | 27.0975 | 3.8725 | 5.2213 | 21.0289 | 1.4429 | 94.7656 | 0 | 23.5014 | 0 | 0.17903 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 311.8397 | 15.85%
CZ 2B | 0.27568 | 0.039335 | 0.047056 | 0.14317 | 0.12062 | 0.6801 | 0 | 0.25059 | 0 | 0.0015725 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9205 | 2.601% | CZ 2B | 8.8486 | 1.2626 | 4.8016 | 8.3867 | 3.8715 | 21.8297 | 0 | 8.0433 | 0 | 0.050475 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 103.8123 | 2.601% | CZ 2B | 2.5934 | 0.37004 | 0 | 0.83691 | 1.1347 | 6.3979 | 0 | 2.3574 | 0 | 0.014793 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.1193 | 2.601% | CZ 2B | 0 | 0 | 0.048016 | 0.055312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.14693 | 2.601% | CZ 2B | 27.1501 | 3.8739 | 5.2481 | 14.8072 | 11.8789 | 66.9797 | 0 | 24.6792 | 0 | 0.15487 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 289.5027 | 2.601%
CZ 3A | 0.27563 | 0.039638 | 0.048349 | 0.17961 | 0.06865 | 0.60334 | 0 | 0.23949 | 0 | 0.0016014 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8187 | 15.52% | CZ 3A | 8.847 | 1.2723 | 4.9335 | 10.3747 | 2.2035 | 19.3659 | 0 | 7.687 | 0 | 0.051401 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 101.4531 | 15.52% | CZ 3A | 2.5929 | 0.37289 | 0 | 1.0697 | 0.64582 | 5.6758 | 0 | 2.2529 | 0 | 0.015065 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 25.0393 | 15.52% | CZ 3A | 0 | 0 | 0.049335 | 0.06725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16019 | 15.52% | CZ 3A | 27.1451 | 3.9038 | 5.3923 | 18.5487 | 6.7611 | 59.4202 | 0 | 23.5859 | 0 | 0.15771 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 279.6454 | 15.52%
CZ 3B | 0.27544 | 0.03901 | 0.047913 | 0.1405 | 0.10458 | 0.52426 | 0 | 0.24734 | 0 | 0.0016158 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.743 | 5.112% | CZ 3B | 8.841 | 1.2521 | 4.8891 | 8.5784 | 3.3568 | 16.8276 | 0 | 7.9391 | 0 | 0.051864 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 98.4537 | 5.112% | CZ 3B | 2.5911 | 0.36698 | 0 | 0.77448 | 0.98382 | 4.9319 | 0 | 2.3268 | 0 | 0.0152 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.4046 | 5.112% | CZ 3B | 0 | 0 | 0.048891 | 0.059358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15185 | 5.112% | CZ 3B | 27.1266 | 3.8419 | 5.3438 | 14.5959 | 10.2997 | 51.6318 | 0 | 24.3596 | 0 | 0.15913 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 272.0891 | 5.112%
CZ 3C | 0.27532 | 0.038895 | 0.048299 | 0.15672 | 0.026683 | 0.46724 | 0 | 0.23224 | 0 | 0.0018611 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.6096 | 1.289% | CZ 3C | 8.837 | 1.2484 | 4.9284 | 9.7527 | 0.85645 | 14.9973 | 0 | 7.4543 | 0 | 0.059736 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 94.8522 | 1.289% | CZ 3C | 2.59 | 0.3659 | 0 | 0.83915 | 0.25101 | 4.3955 | 0 | 2.1847 | 0 | 0.017508 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.058 | 1.289% | CZ 3C | 0 | 0 | 0.049284 | 0.068895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16178 | 1.289% | CZ 3C | 27.1146 | 3.8306 | 5.3868 | 16.3153 | 2.6278 | 46.016 | 0 | 22.8719 | 0 | 0.18329 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 259.0769 | 1.289%
CZ 4A | 0.27463 | 0.039313 | 0.049971 | 0.23958 | 0.11153 | 0.44399 | 0 | 0.24728 | 0 | 0.0025752 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.7712 | 18.12% | CZ 4A | 8.815 | 1.2619 | 5.099 | 15.5407 | 3.58 | 14.2513 | 0 | 7.9373 | 0 | 0.082658 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 103.2856 | 18.12% | CZ 4A | 2.5835 | 0.36983 | 0 | 1.1979 | 1.0492 | 4.1768 | 0 | 2.3263 | 0 | 0.024226 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.142 | 18.12% | CZ 4A | 0 | 0 | 0.05099 | 0.11454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20913 | 18.12% | CZ 4A | 27.0471 | 3.8718 | 5.5732 | 25.0591 | 10.9845 | 43.727 | 0 | 24.3539 | 0 | 0.25362 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 275.6009 | 18.12%
CZ 4B | 0.27442 | 0.03909 | 0.049428 | 0.15057 | 0.13574 | 0.39861 | 0 | 0.25841 | 0 | 0.0018611 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.6705 | 0.607% | CZ 4B | 8.8083 | 1.2547 | 5.0437 | 10.0413 | 4.3568 | 12.7947 | 0 | 8.2943 | 0 | 0.059736 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 97.3713 | 0.607% | CZ 4B | 2.5816 | 0.36773 | 0 | 0.71598 | 1.2769 | 3.7499 | 0 | 2.4309 | 0 | 0.017508 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.5548 | 0.607% | CZ 4B | 0 | 0 | 0.050437 | 0.075983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17002 | 0.607% | CZ 4B | 27.0265 | 3.8498 | 5.5128 | 15.8006 | 13.368 | 39.2578 | 0 | 25.4493 | 0 | 0.18329 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 265.1786 | 0.607%
CZ 4C | 0.27546 | 0.039825 | 0.050551 | 0.19308 | 0.034827 | 0.2648 | 0 | 0.24072 | 0 | 0.0024093 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.464 | 2.878% | CZ 4C | 8.8417 | 1.2783 | 5.1583 | 12.775 | 1.1179 | 8.4995 | 0 | 7.7266 | 0 | 0.077333 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 92.1923 | 2.878% | CZ 4C | 2.5913 | 0.37465 | 0 | 0.93164 | 0.32762 | 2.491 | 0 | 2.2645 | 0 | 0.022665 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 21.4178 | 2.878% | CZ 4C | 0 | 0 | 0.051583 | 0.095962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19115 | 2.878% | CZ 4C | 27.1288 | 3.9222 | 5.638 | 20.242 | 3.4299 | 26.0788 | 0 | 23.7074 | 0 | 0.23728 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 245.115 | 2.878%
CZ 5A | 0.27457 | 0.039573 | 0.051667 | 0.29816 | 0.13249 | 0.31562 | 0 | 0.24308 | 0 | 0.0031739 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.7207 | 23.41% | CZ 5A | 8.8132 | 1.2702 | 5.2722 | 20.3431 | 4.2526 | 10.1309 | 0 | 7.8023 | 0 | 0.10188 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 104.7041 | 23.41% | CZ 5A | 2.583 | 0.37228 | 0 | 1.3559 | 1.2464 | 2.9692 | 0 | 2.2867 | 0 | 0.029858 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.2576 | 23.41% | CZ 5A | 0 | 0 | 0.052722 | 0.15717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25349 | 23.41% | CZ 5A | 27.0414 | 3.8974 | 5.7625 | 31.3733 | 13.0483 | 31.0844 | 0 | 23.9397 | 0 | 0.31258 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 271.1902 | 23.41%
CZ 5B | 0.27436 | 0.039277 | 0.051166 | 0.1894 | 0.11826 | 0.31533 | 0 | 0.26655 | 0 | 0.0020342 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.6187 | 5.921% | CZ 5B | 8.8065 | 1.2607 | 5.221 | 12.6451 | 3.796 | 10.1214 | 0 | 8.5557 | 0 | 0.065293 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 97.1895 | 5.921% | CZ 5B | 2.581 | 0.36949 | 0 | 0.89859 | 1.1126 | 2.9664 | 0 | 2.5075 | 0 | 0.019136 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 22.869 | 5.921% | CZ 5B | 0 | 0 | 0.05221 | 0.095791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19161 | 5.921% | CZ 5B | 27.0208 | 3.8682 | 5.7066 | 19.8773 | 11.6473 | 31.0553 | 0 | 26.2514 | 0 | 0.20034 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 260.3579 | 5.921%
CZ 5C | 0.27505 | 0.039898 | 0.051479 | 0.18667 | 0.033088 | 0.20596 | 0 | 0.24936 | 0 | 0.0024526 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.4063 | 0.1093% | CZ 5C | 8.8285 | 1.2806 | 5.253 | 12.4884 | 1.0621 | 6.6108 | 0 | 8.004 | 0 | 0.078722 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 90.3238 | 0.1093% | CZ 5C | 2.5875 | 0.37533 | 0 | 0.88231 | 0.31127 | 1.9375 | 0 | 2.3458 | 0 | 0.023072 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 20.877 | 0.1093% | CZ 5C | 0 | 0 | 0.05253 | 0.094779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19091 | 0.1093% | CZ 5C | 27.0883 | 3.9293 | 5.7415 | 19.5963 | 3.2587 | 20.2839 | 0 | 24.5585 | 0 | 0.24154 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 239.4286 | 0.1093%
CZ 6A | 0.27462 | 0.039587 | 0.052929 | 0.39882 | 0.16848 | 0.31513 | 0 | 0.24466 | 0 | 0.0045228 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8611 | 5.29% | CZ 6A | 8.8146 | 1.2707 | 5.4009 | 28.1972 | 5.408 | 10.1151 | 0 | 7.853 | 0 | 0.14517 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 113.9224 | 5.29% | CZ 6A | 2.5834 | 0.37241 | 0 | 1.6811 | 1.585 | 2.9646 | 0 | 2.3016 | 0 | 0.042548 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.9448 | 5.29% | CZ 6A | 0 | 0 | 0.054009 | 0.22461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.32223 | 5.29% | CZ 6A | 27.0456 | 3.8988 | 5.9032 | 42.1495 | 16.5933 | 31.0361 | 0 | 24.0953 | 0 | 0.44543 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 285.8978 | 5.29%
CZ 6B | 0.27475 | 0.039919 | 0.052602 | 0.29514 | 0.16816 | 0.23582 | 0 | 0.25375 | 0 | 0.0039169 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.6864 | 0.7888% | CZ 6B | 8.8187 | 1.2813 | 5.3676 | 20.9779 | 5.3976 | 7.5694 | 0 | 8.1447 | 0 | 0.12572 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 104.4008 | 0.7888% | CZ 6B | 2.5846 | 0.37553 | 0 | 1.2291 | 1.5819 | 2.2185 | 0 | 2.3871 | 0 | 0.036848 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 22.8279 | 0.7888% | CZ 6B | 0 | 0 | 0.053676 | 0.16784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26512 | 0.7888% | CZ 6B | 27.0584 | 3.9315 | 5.8667 | 31.2129 | 16.5613 | 23.225 | 0 | 24.9904 | 0 | 0.38576 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 267.9626 | 0.7888%
CZ 7 | 0.2747 | 0.039919 | 0.054458 | 0.47794 | 0.22986 | 0.25036 | 0 | 0.24919 | 0 | 0.0053884 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9442 | 0.8424% | CZ 7 | 8.8174 | 1.2813 | 5.5569 | 36.0032 | 7.3781 | 8.0359 | 0 | 7.9984 | 0 | 0.17296 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 121.962 | 0.8424% | CZ 7 | 2.5842 | 0.37553 | 0 | 1.717 | 2.1624 | 2.3552 | 0 | 2.3442 | 0 | 0.050691 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.0035 | 0.8424% | CZ 7 | 0 | 0 | 0.055569 | 0.30145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.40062 | 0.8424% | CZ 7 | 27.0542 | 3.9315 | 6.0737 | 50.9239 | 22.6382 | 24.6565 | 0 | 24.5414 | 0 | 0.53068 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 295.0807 | 0.8424%
CZ 8 | 0.27691 | 0.042631 | 0.056506 | 0.63839 | 0.31859 | 0.14433 | 0 | 0.25312 | 0 | 0.0069538 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.0998 | 0.06096% | CZ 8 | 8.8882 | 1.3684 | 5.7659 | 49.9647 | 10.226 | 4.6326 | 0 | 8.1246 | 0 | 0.2232 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 135.9114 | 0.06096% | CZ 8 | 2.605 | 0.40105 | 0 | 2.0413 | 2.9971 | 1.3577 | 0 | 2.3812 | 0 | 0.065416 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.263 | 0.06096% | CZ 8 | 0 | 0 | 0.057659 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.53126 | 0.06096% | CZ 8 | 27.2716 | 4.1986 | 6.3022 | 68.3695 | 31.3764 | 14.2141 | 0 | 24.9286 | 0 | 0.68484 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 312.0763 | 0.06096%
US Weighted | 0.27495 | 0.039444 | 0.049662 | 0.23478 | 0.094266 | 0.51799 | 0 | 0.24466 | 0 | 0.0024475 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8206 | 100% | US Weighted | 8.8254 | 1.2661 | 5.0676 | 15.0651 | 3.0257 | 16.6263 | 0 | 7.8529 | 0 | 0.07856 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 104.5255 | 100% | US Weighted | 2.5866 | 0.37106 | 0 | 1.196 | 0.88679 | 4.8729 | 0 | 2.3016 | 0 | 0.023025 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.6522 | 100% | US Weighted | 0 | 0 | 0.050676 | 0.10984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20412 | 100% | US Weighted | 27.0788 | 3.8846 | 5.5389 | 24.527 | 9.2838 | 51.0144 | 0 | 24.095 | 0 | 0.24105 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 280.3943 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.33317 | 0.038477 | 0.046475 | 0.14138 | 0 | 1.5131 | 0 | 0.28253 | 0 | 0.0017312 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.7193 | 0% | CZ 0A | 10.6942 | 1.235 | 4.7423 | 8.6969 | 0 | 48.5684 | 0 | 9.0686 | 0 | 0.055569 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 129.7787 | 0% | CZ 0A | 3.1343 | 0.36196 | 0 | 0.77068 | 0 | 14.2346 | 0 | 2.6578 | 0 | 0.016286 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 33.5899 | 0% | CZ 0A | 0 | 0 | 0.047423 | 0.060673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.1517 | 0% | CZ 0A | 32.8128 | 3.7894 | 5.1834 | 14.6998 | 0 | 149.0217 | 0 | 27.825 | 0 | 0.1705 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 368.2333 | 0%
CZ 0B | 0.33382 | 0.03914 | 0.046475 | 0.16965 | 0.0003751 | 1.3195 | 0 | 0.26535 | 0 | 0.0018827 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.5385 | 0% | CZ 0B | 10.7148 | 1.2563 | 4.7423 | 10.0973 | 0.01204 | 42.3516 | 0 | 8.517 | 0 | 0.060431 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 124.4696 | 0% | CZ 0B | 3.1403 | 0.3682 | 0 | 0.97032 | 0.0035287 | 12.4126 | 0 | 2.4962 | 0 | 0.017711 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 31.8231 | 0% | CZ 0B | 0 | 0 | 0.047423 | 0.067865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15889 | 0% | CZ 0B | 32.8761 | 3.8547 | 5.1834 | 17.576 | 0.036942 | 129.947 | 0 | 26.1328 | 0 | 0.18542 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 350.5229 | 0%
CZ 1A | 0.33436 | 0.039313 | 0.046475 | 0.1611 | 0 | 1.1175 | 0 | 0.25735 | 0 | 0.0019116 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.3204 | 1.601% | CZ 1A | 10.7322 | 1.2619 | 4.7423 | 9.5993 | 0 | 35.8691 | 0 | 8.2603 | 0 | 0.061357 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 117.2442 | 1.601% | CZ 1A | 3.1454 | 0.36983 | 0 | 0.9199 | 0 | 10.5126 | 0 | 2.4209 | 0 | 0.017983 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 29.801 | 1.601% | CZ 1A | 0 | 0 | 0.047423 | 0.064606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15563 | 1.601% | CZ 1A | 32.9293 | 3.8718 | 5.1834 | 16.6919 | 0 | 110.0567 | 0 | 25.3449 | 0 | 0.18826 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 328.9969 | 1.601%
CZ 1B | 0.33409 | 0.039183 | 0.046679 | 0.16055 | 0.00076462 | 1.1351 | 0 | 0.25704 | 0 | 0.0016735 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.3374 | 0% | CZ 1B | 10.7236 | 1.2577 | 4.7632 | 9.5053 | 0.024543 | 36.4343 | 0 | 8.2503 | 0 | 0.053716 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 117.7304 | 0% | CZ 1B | 3.1429 | 0.36861 | 0 | 0.92499 | 0.0071931 | 10.6783 | 0 | 2.418 | 0 | 0.015743 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 29.97 | 0% | CZ 1B | 0 | 0 | 0.047632 | 0.063493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15473 | 0% | CZ 1B | 32.9031 | 3.859 | 5.2061 | 16.6235 | 0.075304 | 111.7908 | 0 | 25.3144 | 0 | 0.16482 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 330.6676 | 0%
CZ 2A | 0.3346 | 0.03932 | 0.046817 | 0.20955 | 0.014679 | 0.98803 | 0 | 0.24391 | 0 | 0.0018466 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.2411 | 15.85% | CZ 2A | 10.74 | 1.2621 | 4.7773 | 11.3334 | 0.47118 | 31.7137 | 0 | 7.8289 | 0 | 0.059273 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 114.9037 | 15.85% | CZ 2A | 3.1477 | 0.3699 | 0 | 1.3516 | 0.13809 | 9.2948 | 0 | 2.2945 | 0 | 0.017372 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 29.0282 | 15.85% | CZ 2A | 0 | 0 | 0.047773 | 0.067219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.1586 | 15.85% | CZ 2A | 32.9535 | 3.8725 | 5.2216 | 21.4965 | 1.4457 | 97.3068 | 0 | 24.0214 | 0 | 0.18187 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 321.2305 | 15.85%
CZ 2B | 0.33572 | 0.039335 | 0.047056 | 0.15254 | 0.12088 | 0.69871 | 0 | 0.25801 | 0 | 0.0016375 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.0163 | 2.601% | CZ 2B | 10.7759 | 1.2626 | 4.8016 | 8.9331 | 3.8801 | 22.427 | 0 | 8.2816 | 0 | 0.052559 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.1322 | 2.601% | CZ 2B | 3.1582 | 0.37004 | 0 | 0.89208 | 1.1372 | 6.573 | 0 | 2.4272 | 0 | 0.015404 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.9874 | 2.601% | CZ 2B | 0 | 0 | 0.048016 | 0.058893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15051 | 2.601% | CZ 2B | 33.0636 | 3.8739 | 5.2481 | 15.7762 | 11.9052 | 68.8126 | 0 | 25.4103 | 0 | 0.16127 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 298.9818 | 2.601%
CZ 3A | 0.33511 | 0.039638 | 0.048349 | 0.2681 | 0.068708 | 0.62405 | 0 | 0.24394 | 0 | 0.0016447 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9919 | 15.52% | CZ 3A | 10.7562 | 1.2723 | 4.9335 | 13.2019 | 2.2054 | 20.0306 | 0 | 7.8298 | 0 | 0.05279 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.0004 | 15.52% | CZ 3A | 3.1525 | 0.37289 | 0 | 1.9039 | 0.64636 | 5.8706 | 0 | 2.2948 | 0 | 0.015472 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.6708 | 15.52% | CZ 3A | 0 | 0 | 0.049335 | 0.067057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16 | 15.52% | CZ 3A | 33.0032 | 3.9038 | 5.3923 | 27.2616 | 6.7667 | 61.4598 | 0 | 24.0242 | 0 | 0.16198 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 296.7043 | 15.52%
CZ 3B | 0.33514 | 0.03901 | 0.047913 | 0.14694 | 0.10447 | 0.52722 | 0 | 0.25541 | 0 | 0.0016879 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8202 | 5.112% | CZ 3B | 10.7572 | 1.2521 | 4.8891 | 8.9536 | 3.3533 | 16.9227 | 0 | 8.1982 | 0 | 0.054179 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 101.0983 | 5.112% | CZ 3B | 3.1527 | 0.36698 | 0 | 0.81241 | 0.98281 | 4.9598 | 0 | 2.4028 | 0 | 0.015879 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 25.1076 | 5.112% | CZ 3B | 0 | 0 | 0.048891 | 0.061817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.15431 | 5.112% | CZ 3B | 33.0061 | 3.8419 | 5.3438 | 15.2617 | 10.289 | 51.9238 | 0 | 25.1545 | 0 | 0.16624 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 279.7177 | 5.112%
CZ 3C | 0.33493 | 0.038895 | 0.048299 | 0.16082 | 0.026733 | 0.47371 | 0 | 0.2383 | 0 | 0.0019909 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.686 | 1.289% | CZ 3C | 10.7507 | 1.2484 | 4.9284 | 10.0928 | 0.85807 | 15.2052 | 0 | 7.6488 | 0 | 0.063904 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 97.5141 | 1.289% | CZ 3C | 3.1508 | 0.3659 | 0 | 0.84967 | 0.25149 | 4.4564 | 0 | 2.2417 | 0 | 0.018729 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.749 | 1.289% | CZ 3C | 0 | 0 | 0.049284 | 0.071937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16483 | 1.289% | CZ 3C | 32.9862 | 3.8306 | 5.3868 | 16.7579 | 2.6328 | 46.6539 | 0 | 23.4687 | 0 | 0.19608 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 266.6436 | 1.289%
CZ 4A | 0.3331 | 0.039313 | 0.049973 | 0.24265 | 0.11156 | 0.4533 | 0 | 0.25406 | 0 | 0.002669 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.849 | 18.12% | CZ 4A | 10.6916 | 1.2619 | 5.0993 | 15.937 | 3.5809 | 14.5499 | 0 | 8.1547 | 0 | 0.085668 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 106.0788 | 18.12% | CZ 4A | 3.1335 | 0.36983 | 0 | 1.1868 | 1.0495 | 4.2643 | 0 | 2.39 | 0 | 0.025108 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.8334 | 18.12% | CZ 4A | 0 | 0 | 0.050993 | 0.11888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21347 | 18.12% | CZ 4A | 32.805 | 3.8718 | 5.5735 | 25.4177 | 10.9873 | 44.6434 | 0 | 25.021 | 0 | 0.26286 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 283.3133 | 18.12%
CZ 4B | 0.33322 | 0.03909 | 0.049428 | 0.15811 | 0.13568 | 0.39081 | 0 | 0.27477 | 0 | 0.001926 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.7454 | 0.607% | CZ 4B | 10.6956 | 1.2547 | 5.0437 | 10.458 | 4.355 | 12.5442 | 0 | 8.8194 | 0 | 0.06182 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 99.9501 | 0.607% | CZ 4B | 3.1347 | 0.36773 | 0 | 0.76342 | 1.2764 | 3.6765 | 0 | 2.5848 | 0 | 0.018118 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.2359 | 0.607% | CZ 4B | 0 | 0 | 0.050437 | 0.078532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17257 | 0.607% | CZ 4B | 32.8171 | 3.8498 | 5.5128 | 16.5757 | 13.3623 | 38.4891 | 0 | 27.0606 | 0 | 0.18968 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 272.5876 | 0.607%
CZ 4C | 0.33459 | 0.039825 | 0.050558 | 0.19726 | 0.034848 | 0.25942 | 0 | 0.24834 | 0 | 0.0024814 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.5297 | 2.878% | CZ 4C | 10.7396 | 1.2783 | 5.159 | 13.0817 | 1.1185 | 8.3267 | 0 | 7.9713 | 0 | 0.079648 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 94.4726 | 2.878% | CZ 4C | 3.1476 | 0.37465 | 0 | 0.94786 | 0.32783 | 2.4404 | 0 | 2.3363 | 0 | 0.023344 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 22.0122 | 2.878% | CZ 4C | 0 | 0 | 0.05159 | 0.098476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19367 | 2.878% | CZ 4C | 32.9521 | 3.9222 | 5.6388 | 20.6866 | 3.432 | 25.5488 | 0 | 24.4583 | 0 | 0.24438 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 251.6138 | 2.878%
CZ 5A | 0.33308 | 0.039573 | 0.051665 | 0.30457 | 0.13251 | 0.3159 | 0 | 0.25101 | 0 | 0.0032821 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.794 | 23.41% | CZ 5A | 10.6912 | 1.2702 | 5.272 | 20.9882 | 4.2533 | 10.1397 | 0 | 8.057 | 0 | 0.10535 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.4947 | 23.41% | CZ 5A | 3.1334 | 0.37228 | 0 | 1.3572 | 1.2466 | 2.9718 | 0 | 2.3614 | 0 | 0.030876 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.8877 | 23.41% | CZ 5A | 0 | 0 | 0.05272 | 0.16358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2599 | 23.41% | CZ 5A | 32.8036 | 3.8974 | 5.7622 | 32.0871 | 13.0504 | 31.1114 | 0 | 24.7212 | 0 | 0.32324 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 278.4872 | 23.41%
CZ 5B | 0.33289 | 0.039277 | 0.051166 | 0.19602 | 0.11825 | 0.3067 | 0 | 0.27661 | 0 | 0.0020991 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.6854 | 5.921% | CZ 5B | 10.6852 | 1.2607 | 5.221 | 13.0896 | 3.7956 | 9.8444 | 0 | 8.8785 | 0 | 0.067377 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 99.5601 | 5.921% | CZ 5B | 3.1316 | 0.36949 | 0 | 0.92974 | 1.1124 | 2.8852 | 0 | 2.6021 | 0 | 0.019747 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.4647 | 5.921% | CZ 5B | 0 | 0 | 0.05221 | 0.099173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19499 | 5.921% | CZ 5B | 32.7851 | 3.8682 | 5.7066 | 20.573 | 11.6459 | 30.2056 | 0 | 27.2417 | 0 | 0.20673 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 266.9636 | 5.921%
CZ 5C | 0.33369 | 0.039898 | 0.051477 | 0.18957 | 0.033189 | 0.19416 | 0 | 0.26349 | 0 | 0.0025031 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.4703 | 0.1093% | CZ 5C | 10.7106 | 1.2806 | 5.2527 | 12.7296 | 1.0653 | 6.2323 | 0 | 8.4573 | 0 | 0.080343 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 92.5266 | 0.1093% | CZ 5C | 3.1391 | 0.37533 | 0 | 0.88964 | 0.31222 | 1.8266 | 0 | 2.4787 | 0 | 0.023547 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 21.4593 | 0.1093% | CZ 5C | 0 | 0 | 0.052527 | 0.096941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19307 | 0.1093% | CZ 5C | 32.8633 | 3.9293 | 5.7412 | 19.9093 | 3.2686 | 19.1223 | 0 | 25.9495 | 0 | 0.24652 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 245.7608 | 0.1093%
CZ 6A | 0.33273 | 0.039587 | 0.052929 | 0.41183 | 0.16865 | 0.31735 | 0 | 0.25426 | 0 | 0.0047537 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9445 | 5.29% | CZ 6A | 10.6801 | 1.2707 | 5.4009 | 29.6725 | 5.4133 | 10.1862 | 0 | 8.1612 | 0 | 0.15258 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 117.6551 | 5.29% | CZ 6A | 3.1301 | 0.37241 | 0 | 1.6613 | 1.5866 | 2.9854 | 0 | 2.3919 | 0 | 0.044719 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.5866 | 5.29% | CZ 6A | 0 | 0 | 0.054009 | 0.24004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.33765 | 5.29% | CZ 6A | 32.7695 | 3.8988 | 5.9032 | 43.6284 | 16.6096 | 31.2542 | 0 | 25.0408 | 0 | 0.46817 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 294.3033 | 5.29%
CZ 6B | 0.33297 | 0.039919 | 0.0526 | 0.30217 | 0.16825 | 0.22863 | 0 | 0.26461 | 0 | 0.0041333 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.7556 | 0.7888% | CZ 6B | 10.6875 | 1.2813 | 5.3673 | 21.686 | 5.4006 | 7.3385 | 0 | 8.4934 | 0 | 0.13267 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.1052 | 0.7888% | CZ 6B | 3.1323 | 0.37553 | 0 | 1.2304 | 1.5828 | 2.1508 | 0 | 2.4893 | 0 | 0.038883 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.4142 | 0.7888% | CZ 6B | 0 | 0 | 0.053673 | 0.17488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.27216 | 0.7888% | CZ 6B | 32.7922 | 3.9315 | 5.8665 | 31.9951 | 16.5705 | 22.5167 | 0 | 26.0603 | 0 | 0.40707 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 274.8705 | 0.7888%
CZ 7 | 0.33226 | 0.039919 | 0.054458 | 0.48591 | 0.22995 | 0.25595 | 0 | 0.25885 | 0 | 0.005713 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.0254 | 0.8424% | CZ 7 | 10.6648 | 1.2813 | 5.5569 | 36.7738 | 7.3809 | 8.2156 | 0 | 8.3084 | 0 | 0.18338 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 125.0829 | 0.8424% | CZ 7 | 3.1257 | 0.37553 | 0 | 1.7227 | 2.1632 | 2.4079 | 0 | 2.4351 | 0 | 0.053745 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.6981 | 0.8424% | CZ 7 | 0 | 0 | 0.055569 | 0.30896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.40813 | 0.8424% | CZ 7 | 32.7226 | 3.9315 | 6.0737 | 51.8046 | 22.6467 | 25.2078 | 0 | 25.4927 | 0 | 0.56265 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 303.1728 | 0.8424%
CZ 8 | 0.33475 | 0.042631 | 0.056495 | 0.6488 | 0.31878 | 0.14051 | 0 | 0.26307 | 0 | 0.0072423 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.1746 | 0.06096% | CZ 8 | 10.7449 | 1.3684 | 5.7648 | 50.7831 | 10.232 | 4.5101 | 0 | 8.4439 | 0 | 0.23246 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 138.7974 | 0.06096% | CZ 8 | 3.1491 | 0.40105 | 0 | 2.0741 | 2.9988 | 1.3218 | 0 | 2.4748 | 0 | 0.068131 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.9021 | 0.06096% | CZ 8 | 0 | 0 | 0.057648 | 0.43706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.53831 | 0.06096% | CZ 8 | 32.9684 | 4.1986 | 6.3009 | 69.4848 | 31.3948 | 13.8383 | 0 | 25.9083 | 0 | 0.71326 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 319.5379 | 0.06096%
US Weighted | 0.33387 | 0.039444 | 0.049663 | 0.25333 | 0.094302 | 0.5277 | 0 | 0.25163 | 0 | 0.0025319 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9148 | 100% | US Weighted | 10.7164 | 1.2661 | 5.0676 | 15.931 | 3.0269 | 16.9379 | 0 | 8.0769 | 0 | 0.081267 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.8218 | 100% | US Weighted | 3.1408 | 0.37106 | 0 | 1.3342 | 0.88713 | 4.9642 | 0 | 2.3672 | 0 | 0.023818 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 25.5026 | 100% | US Weighted | 0 | 0 | 0.050676 | 0.11379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20807 | 100% | US Weighted | 32.8809 | 3.8846 | 5.5389 | 26.4044 | 9.2874 | 51.9704 | 0 | 24.7823 | 0 | 0.24935 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 289.7289 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.3609 | 0.08105 | 0.053759 | 0.16625 | 0 | 1.4967 | 0 | 0.29413 | 0.021792 | 0.0022722 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.8392 | 0% | CZ 0A | 11.5842 | 2.6015 | 5.4856 | 10.9631 | 0 | 48.0416 | 0 | 9.4409 | 0.69947 | 0.072934 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 135.6071 | 0% | CZ 0A | 3.3951 | 0.76247 | 0 | 0.80712 | 0 | 14.0802 | 0 | 2.767 | 0.205 | 0.021376 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 34.4525 | 0% | CZ 0A | 0 | 0 | 0.054856 | 0.082092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18055 | 0% | CZ 0A | 35.5437 | 7.9823 | 5.9958 | 17.4224 | 0 | 147.4055 | 0 | 28.9673 | 2.1462 | 0.22378 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 380.4176 | 0%
CZ 0B | 0.3619 | 0.081036 | 0.053759 | 0.19393 | 0.00036067 | 1.3741 | 0 | 0.28361 | 0 | 0.0023372 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.7134 | 0% | CZ 0B | 11.6162 | 2.6011 | 5.4856 | 12.1397 | 0.011577 | 44.1046 | 0 | 9.1033 | 0 | 0.075018 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 131.8548 | 0% | CZ 0B | 3.4045 | 0.76233 | 0 | 1.0288 | 0.003393 | 12.9263 | 0 | 2.668 | 0 | 0.021986 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 33.2296 | 0% | CZ 0B | 0 | 0 | 0.054856 | 0.086293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18475 | 0% | CZ 0B | 35.6417 | 7.9808 | 5.9958 | 20.2025 | 0.035521 | 135.3256 | 0 | 27.9315 | 0 | 0.23018 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 368.0743 | 0%
CZ 1A | 0.36362 | 0.08105 | 0.053759 | 0.1816 | 0 | 1.1222 | 0 | 0.27668 | 0.021792 | 0.0024526 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.4655 | 1.601% | CZ 1A | 11.6713 | 2.6015 | 5.4856 | 11.538 | 0 | 36.0205 | 0 | 8.8808 | 0.69947 | 0.078722 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 123.6937 | 1.601% | CZ 1A | 3.4207 | 0.76247 | 0 | 0.94053 | 0 | 10.557 | 0 | 2.6028 | 0.205 | 0.023072 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 30.9258 | 1.601% | CZ 1A | 0 | 0 | 0.054856 | 0.083289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18175 | 1.601% | CZ 1A | 35.8108 | 7.9823 | 5.9958 | 18.9499 | 0 | 110.5213 | 0 | 27.2488 | 2.1462 | 0.24154 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 343.6272 | 1.601%
CZ 1B | 0.36331 | 0.080928 | 0.053759 | 0.19263 | 0.00077184 | 1.178 | 0 | 0.27444 | 0 | 0.0020126 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.5082 | 0% | CZ 1B | 11.6615 | 2.5976 | 5.4856 | 11.6957 | 0.024774 | 37.8114 | 0 | 8.809 | 0 | 0.064599 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 124.8681 | 0% | CZ 1B | 3.4178 | 0.76131 | 0 | 1.0707 | 0.0072609 | 11.0819 | 0 | 2.5818 | 0 | 0.018933 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 31.3539 | 0% | CZ 1B | 0 | 0 | 0.054856 | 0.080425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17889 | 0% | CZ 1B | 35.781 | 7.9702 | 5.9958 | 19.9995 | 0.076015 | 116.0164 | 0 | 27.0286 | 0 | 0.19821 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 347.7963 | 0%
CZ 2A | 0.3639 | 0.080899 | 0.053759 | 0.25217 | 0.01455 | 0.99304 | 0 | 0.26354 | 0.017738 | 0.0022073 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.4042 | 15.85% | CZ 2A | 11.6805 | 2.5967 | 5.4856 | 13.9892 | 0.46701 | 31.8744 | 0 | 8.4592 | 0.56935 | 0.07085 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 121.9105 | 15.85% | CZ 2A | 3.4234 | 0.76104 | 0 | 1.5794 | 0.13687 | 9.3418 | 0 | 2.4792 | 0.16687 | 0.020765 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 30.3236 | 15.85% | CZ 2A | 0 | 0 | 0.054856 | 0.086004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18446 | 15.85% | CZ 2A | 35.8392 | 7.9673 | 5.9958 | 25.9345 | 1.4329 | 97.7998 | 0 | 25.9552 | 1.7469 | 0.21739 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 337.6197 | 15.85%
CZ 2B | 0.36522 | 0.080964 | 0.053791 | 0.18239 | 0.12018 | 0.73015 | 0 | 0.27622 | 0 | 0.0019476 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.1732 | 2.601% | CZ 2B | 11.7229 | 2.5988 | 5.4888 | 10.7987 | 3.8576 | 23.4363 | 0 | 8.8662 | 0 | 0.062515 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 113.5496 | 2.601% | CZ 2B | 3.4358 | 0.76165 | 0 | 1.0507 | 1.1306 | 6.8688 | 0 | 2.5985 | 0 | 0.018322 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 28.2787 | 2.601% | CZ 2B | 0 | 0 | 0.054888 | 0.072136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17063 | 2.601% | CZ 2B | 35.9692 | 7.9737 | 5.9993 | 18.8846 | 11.8363 | 71.9093 | 0 | 27.2041 | 0 | 0.19181 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 314.699 | 2.601%
CZ 3A | 0.36447 | 0.080949 | 0.054535 | 0.33186 | 0.067806 | 0.64547 | 0 | 0.26759 | 0.014189 | 0.0024381 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.1917 | 15.52% | CZ 3A | 11.6986 | 2.5983 | 5.5648 | 17.2295 | 2.1764 | 20.7181 | 0 | 8.5891 | 0.45543 | 0.078259 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 115.8262 | 15.52% | CZ 3A | 3.4287 | 0.76152 | 0 | 2.2372 | 0.63788 | 6.0721 | 0 | 2.5173 | 0.13348 | 0.022936 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 28.2253 | 15.52% | CZ 3A | 0 | 0 | 0.055648 | 0.095962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19521 | 15.52% | CZ 3A | 35.8946 | 7.9723 | 6.0823 | 33.9098 | 6.6779 | 63.569 | 0 | 26.3537 | 1.3974 | 0.24012 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 316.8278 | 15.52%
CZ 3B | 0.36457 | 0.080942 | 0.054253 | 0.18485 | 0.10319 | 0.55346 | 0 | 0.27379 | 0 | 0.002027 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9794 | 5.112% | CZ 3B | 11.7018 | 2.5981 | 5.5361 | 11.3255 | 3.3121 | 17.7648 | 0 | 8.7882 | 0 | 0.065062 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 107.8095 | 5.112% | CZ 3B | 3.4296 | 0.76145 | 0 | 1.0137 | 0.97073 | 5.2066 | 0 | 2.5757 | 0 | 0.019068 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.391 | 5.112% | CZ 3B | 0 | 0 | 0.055361 | 0.078668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17763 | 5.112% | CZ 3B | 35.9046 | 7.9716 | 6.0509 | 19.2107 | 10.1625 | 54.5076 | 0 | 26.9647 | 0 | 0.19963 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 295.7029 | 5.112%
CZ 3C | 0.36433 | 0.081072 | 0.054024 | 0.19998 | 0.026452 | 0.50269 | 0 | 0.25781 | 0 | 0.0023804 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8511 | 1.289% | CZ 3C | 11.6942 | 2.6022 | 5.5127 | 12.6897 | 0.84904 | 16.1353 | 0 | 8.2751 | 0 | 0.076407 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 104.5524 | 1.289% | CZ 3C | 3.4274 | 0.76267 | 0 | 1.0378 | 0.24884 | 4.729 | 0 | 2.4253 | 0 | 0.022394 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 25.0676 | 1.289% | CZ 3C | 0 | 0 | 0.055127 | 0.091485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19022 | 1.289% | CZ 3C | 35.8811 | 7.9844 | 6.0254 | 20.8645 | 2.6051 | 49.5077 | 0 | 25.3904 | 0 | 0.23444 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 283.2237 | 1.289%
CZ 4A | 0.36118 | 0.081086 | 0.055583 | 0.27165 | 0.11045 | 0.4697 | 0 | 0.27705 | 0.015192 | 0.0029647 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.0072 | 18.12% | CZ 4A | 11.5932 | 2.6027 | 5.6717 | 17.0971 | 3.5453 | 15.0765 | 0 | 8.8926 | 0.48761 | 0.095161 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 111.7797 | 18.12% | CZ 4A | 3.3978 | 0.76281 | 0 | 1.4286 | 1.0391 | 4.4187 | 0 | 2.6063 | 0.14291 | 0.02789 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.2383 | 18.12% | CZ 4A | 0 | 0 | 0.056717 | 0.12223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22255 | 18.12% | CZ 4A | 35.5714 | 7.9858 | 6.1992 | 28.3157 | 10.8779 | 46.2589 | 0 | 27.2851 | 1.4961 | 0.29198 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 299.0128 | 18.12%
CZ 4B | 0.36139 | 0.080913 | 0.055213 | 0.18354 | 0.13564 | 0.41291 | 0 | 0.29675 | 0 | 0.002164 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8909 | 0.607% | CZ 4B | 11.5997 | 2.5971 | 5.634 | 11.9349 | 4.3538 | 13.2536 | 0 | 9.5252 | 0 | 0.069461 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 105.6856 | 0.607% | CZ 4B | 3.3997 | 0.76118 | 0 | 0.91373 | 1.276 | 3.8844 | 0 | 2.7917 | 0 | 0.020358 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 25.4613 | 0.607% | CZ 4B | 0 | 0 | 0.05634 | 0.088173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18812 | 0.607% | CZ 4B | 35.5913 | 7.9688 | 6.1579 | 19.2031 | 13.3587 | 40.6658 | 0 | 29.2259 | 0 | 0.21313 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 287.1153 | 0.607%
CZ 4C | 0.36292 | 0.081065 | 0.055878 | 0.23532 | 0.034927 | 0.27953 | 0 | 0.27086 | 0 | 0.0027916 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.6857 | 2.878% | CZ 4C | 11.649 | 2.602 | 5.7018 | 15.3303 | 1.1211 | 8.9722 | 0 | 8.6942 | 0 | 0.089604 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 100.878 | 2.878% | CZ 4C | 3.4141 | 0.7626 | 0 | 1.1678 | 0.32857 | 2.6296 | 0 | 2.5481 | 0 | 0.026262 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 23.2913 | 2.878% | CZ 4C | 0 | 0 | 0.057018 | 0.11346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21408 | 2.878% | CZ 4C | 35.7426 | 7.9837 | 6.2321 | 24.6265 | 3.4398 | 27.5294 | 0 | 26.6762 | 0 | 0.27493 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 267.236 | 2.878%
CZ 5A | 0.36166 | 0.080964 | 0.056953 | 0.32562 | 0.13115 | 0.3318 | 0 | 0.27213 | 0.014434 | 0.0034625 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9405 | 23.41% | CZ 5A | 11.6085 | 2.5988 | 5.8115 | 21.0558 | 4.2098 | 10.65 | 0 | 8.7347 | 0.4633 | 0.11114 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 111.9613 | 23.41% | CZ 5A | 3.4023 | 0.76165 | 0 | 1.6369 | 1.2338 | 3.1213 | 0 | 2.56 | 0.13579 | 0.032572 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 25.2986 | 23.41% | CZ 5A | 0 | 0 | 0.058115 | 0.15471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25643 | 23.41% | CZ 5A | 35.6183 | 7.9737 | 6.352 | 34.0462 | 12.9168 | 32.6771 | 0 | 26.8006 | 1.4215 | 0.341 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 292.878 | 23.41%
CZ 5B | 0.36148 | 0.081043 | 0.056486 | 0.22511 | 0.11793 | 0.32237 | 0 | 0.2968 | 0 | 0.0023588 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.8259 | 5.921% | CZ 5B | 11.6027 | 2.6013 | 5.7638 | 14.689 | 3.7851 | 10.3473 | 0 | 9.5265 | 0 | 0.075712 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 105.1094 | 5.921% | CZ 5B | 3.4006 | 0.7624 | 0 | 1.1139 | 1.1094 | 3.0326 | 0 | 2.7921 | 0 | 0.02219 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.6474 | 5.921% | CZ 5B | 0 | 0 | 0.057638 | 0.10888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21013 | 5.921% | CZ 5B | 35.6005 | 7.9816 | 6.2999 | 23.5625 | 11.6139 | 31.7486 | 0 | 29.2302 | 0 | 0.23231 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 281.0001 | 5.921%
CZ 5C | 0.3623 | 0.081029 | 0.056844 | 0.22079 | 0.032756 | 0.20478 | 0 | 0.27531 | 0 | 0.0028421 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.599 | 0.1093% | CZ 5C | 11.6289 | 2.6008 | 5.8004 | 14.5424 | 1.0514 | 6.5728 | 0 | 8.8368 | 0 | 0.091225 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 97.8427 | 0.1093% | CZ 5C | 3.4082 | 0.76226 | 0 | 1.0743 | 0.30815 | 1.9264 | 0 | 2.5899 | 0 | 0.026737 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 22.5102 | 0.1093% | CZ 5C | 0 | 0 | 0.058004 | 0.10877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21038 | 0.1093% | CZ 5C | 35.6808 | 7.9801 | 6.3399 | 23.1352 | 3.226 | 20.1674 | 0 | 27.1138 | 0 | 0.27991 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 258.6538 | 0.1093%
CZ 6A | 0.36177 | 0.081007 | 0.058203 | 0.43388 | 0.16705 | 0.32969 | 0 | 0.27446 | 0.015177 | 0.0047969 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.0884 | 5.29% | CZ 6A | 11.612 | 2.6001 | 5.9391 | 29.2232 | 5.3619 | 10.5823 | 0 | 8.8095 | 0.48715 | 0.15397 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 121.4871 | 5.29% | CZ 6A | 3.4033 | 0.76206 | 0 | 2.0242 | 1.5715 | 3.1015 | 0 | 2.5819 | 0.14278 | 0.045126 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.0466 | 5.29% | CZ 6A | 0 | 0 | 0.059391 | 0.22317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.32616 | 5.29% | CZ 6A | 35.6289 | 7.978 | 6.4914 | 45.5837 | 16.4519 | 32.4697 | 0 | 27.03 | 1.4947 | 0.47243 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 308.3315 | 5.29%
CZ 6B | 0.36206 | 0.080906 | 0.057881 | 0.34458 | 0.16605 | 0.24213 | 0 | 0.28381 | 0 | 0.0043353 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 2.9041 | 0.7888% | CZ 6B | 11.6215 | 2.5969 | 5.9062 | 23.7921 | 5.33 | 7.772 | 0 | 9.1098 | 0 | 0.13915 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 112.9853 | 0.7888% | CZ 6B | 3.4061 | 0.76111 | 0 | 1.5292 | 1.5621 | 2.2778 | 0 | 2.6699 | 0 | 0.040783 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 24.6613 | 0.7888% | CZ 6B | 0 | 0 | 0.059062 | 0.18574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.28841 | 0.7888% | CZ 6B | 35.6581 | 7.9681 | 6.4555 | 36.3111 | 16.3538 | 23.8466 | 0 | 27.9514 | 0 | 0.42696 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 289.7022 | 0.7888%
CZ 7 | 0.36123 | 0.081029 | 0.0597 | 0.50285 | 0.22823 | 0.26765 | 0 | 0.27945 | 0.015329 | 0.0055832 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.1634 | 0.8424% | CZ 7 | 11.5949 | 2.6008 | 6.0919 | 35.4837 | 7.3256 | 8.5911 | 0 | 8.9697 | 0.49201 | 0.17921 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 128.0467 | 0.8424% | CZ 7 | 3.3983 | 0.76226 | 0 | 2.1287 | 2.147 | 2.5179 | 0 | 2.6289 | 0.1442 | 0.052523 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.194 | 0.8424% | CZ 7 | 0 | 0 | 0.060919 | 0.2822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.38673 | 0.8424% | CZ 7 | 35.5764 | 7.9801 | 6.6584 | 53.1307 | 22.4769 | 26.3601 | 0 | 27.5216 | 1.5096 | 0.54986 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 316.4945 | 0.8424%
CZ 8 | 0.36403 | 0.081497 | 0.061776 | 0.67627 | 0.31623 | 0.14963 | 0 | 0.28161 | 0.01491 | 0.0070764 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.3154 | 0.06096% | CZ 8 | 11.6845 | 2.6159 | 6.3037 | 49.0745 | 10.1503 | 4.8027 | 0 | 9.0392 | 0.47858 | 0.22714 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 141.0943 | 0.06096% | CZ 8 | 3.4245 | 0.76667 | 0 | 2.6809 | 2.9749 | 1.4076 | 0 | 2.6492 | 0.14027 | 0.06657 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.5249 | 0.06096% | CZ 8 | 0 | 0 | 0.063037 | 0.39927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.50591 | 0.06096% | CZ 8 | 35.8513 | 8.0263 | 6.8899 | 71.707 | 31.1441 | 14.7362 | 0 | 27.7348 | 1.4684 | 0.69692 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 332.9856 | 0.06096%
US Weighted | 0.3627 | 0.080985 | 0.055544 | 0.28838 | 0.093399 | 0.54363 | 0 | 0.27289 | 0.012435 | 0.0028758 | 0 | 0.46113 | 0 | 0 | 0 | 0.90123 | 3.0752 | 100% | US Weighted | 11.642 | 2.5994 | 5.6678 | 17.5885 | 2.9979 | 17.4494 | 0 | 8.7593 | 0.39914 | 0.092308 | 0 | 14.8014 | 0 | 0 | 0 | 31.9164 | 113.9136 | 100% | US Weighted | 3.4121 | 0.76185 | 0 | 1.5922 | 0.87864 | 5.1141 | 0 | 2.5672 | 0.11698 | 0.027054 | 0 | 4.338 | 0 | 0 | 0 | 8.0762 | 26.8844 | 100% | US Weighted | 0 | 0 | 0.056678 | 0.12156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22184 | 100% | US Weighted | 35.721 | 7.9759 | 6.1949 | 29.9549 | 9.1985 | 53.5397 | 0 | 26.8761 | 1.2247 | 0.28323 | 0 | 45.415 | 0 | 0 | 0 | 89.3157 | 305.6996 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.39025 | 0.08105 | 0.053759 | 0.16343 | 0 | 1.6263 | 0 | 0.3347 | 0 | 0.0023444 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 4.0174 | 0% | CZ 0A | 12.5261 | 2.6015 | 5.4856 | 11.248 | 0 | 52.2019 | 0 | 10.7433 | 0 | 0.075249 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 141.6999 | 0% | CZ 0A | 3.6712 | 0.76247 | 0 | 0.7301 | 0 | 15.2995 | 0 | 3.1487 | 0 | 0.022054 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 36.0777 | 0% | CZ 0A | 0 | 0 | 0.054856 | 0.087569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18603 | 0% | CZ 0A | 38.4337 | 7.9823 | 5.9958 | 17.2147 | 0 | 160.1703 | 0 | 32.9634 | 0 | 0.23089 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 398.03 | 0%
CZ 0B | 0.3903 | 0.081036 | 0.053759 | 0.20981 | 0.0006997 | 1.4302 | 0 | 0.31495 | 0 | 0.0021424 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.8484 | 0% | CZ 0B | 12.5279 | 2.6011 | 5.4856 | 12.5819 | 0.022459 | 45.9066 | 0 | 10.1093 | 0 | 0.068766 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 136.122 | 0% | CZ 0B | 3.6717 | 0.76233 | 0 | 1.1873 | 0.0065824 | 13.4545 | 0 | 2.9629 | 0 | 0.020154 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 34.5091 | 0% | CZ 0B | 0 | 0 | 0.054856 | 0.08531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18377 | 0% | CZ 0B | 38.4393 | 7.9808 | 5.9958 | 21.7538 | 0.068911 | 140.8548 | 0 | 31.0183 | 0 | 0.21099 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 381.3618 | 0%
CZ 1A | 0.39033 | 0.08105 | 0.053759 | 0.18758 | 0 | 1.1607 | 0 | 0.30964 | 0.021792 | 0.0025103 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.5728 | 1.601% | CZ 1A | 12.5286 | 2.6015 | 5.4856 | 12.0322 | 0 | 37.2548 | 0 | 9.9389 | 0.69947 | 0.080574 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 127.44 | 1.601% | CZ 1A | 3.6719 | 0.76247 | 0 | 0.95607 | 0 | 10.9188 | 0 | 2.9129 | 0.205 | 0.023615 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 31.8945 | 1.601% | CZ 1A | 0 | 0 | 0.054856 | 0.087701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18616 | 1.601% | CZ 1A | 38.4415 | 7.9823 | 5.9958 | 19.5948 | 0 | 114.3085 | 0 | 30.4954 | 2.1462 | 0.24723 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 354.2507 | 1.601%
CZ 1B | 0.39036 | 0.080928 | 0.053759 | 0.19643 | 0.0013273 | 1.2223 | 0 | 0.30543 | 0 | 0.0016952 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.6177 | 0% | CZ 1B | 12.5296 | 2.5976 | 5.4856 | 11.6434 | 0.042603 | 39.2324 | 0 | 9.8037 | 0 | 0.054411 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 128.2076 | 0% | CZ 1B | 3.6722 | 0.76131 | 0 | 1.1299 | 0.012486 | 11.4984 | 0 | 2.8733 | 0 | 0.015947 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 32.4072 | 0% | CZ 1B | 0 | 0 | 0.054856 | 0.077881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17634 | 0% | CZ 1B | 38.4443 | 7.9702 | 5.9958 | 20.3416 | 0.13072 | 120.3762 | 0 | 30.0806 | 0 | 0.16695 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 358.5453 | 0%
CZ 2A | 0.39035 | 0.080899 | 0.053759 | 0.26819 | 0.014225 | 1.0262 | 0 | 0.29222 | 0.017709 | 0.0019909 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.511 | 15.85% | CZ 2A | 12.5293 | 2.5967 | 5.4856 | 14.3277 | 0.45659 | 32.9385 | 0 | 9.3798 | 0.56842 | 0.063904 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 125.1648 | 15.85% | CZ 2A | 3.6721 | 0.76104 | 0 | 1.7538 | 0.13382 | 9.6537 | 0 | 2.749 | 0.16659 | 0.018729 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 31.3526 | 15.85% | CZ 2A | 0 | 0 | 0.054856 | 0.083439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.1819 | 15.85% | CZ 2A | 38.4436 | 7.9673 | 5.9958 | 27.48 | 1.4009 | 101.0649 | 0 | 28.7798 | 1.7441 | 0.19608 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 348.1115 | 15.85%
CZ 2B | 0.39041 | 0.080964 | 0.053791 | 0.2599 | 0.21119 | 0.7722 | 0 | 0.30944 | 0 | 0.001623 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.445 | 2.601% | CZ 2B | 12.5314 | 2.5988 | 5.4888 | 12.7517 | 6.7787 | 24.7859 | 0 | 9.9324 | 0 | 0.052096 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 121.7381 | 2.601% | CZ 2B | 3.6727 | 0.76165 | 0 | 1.8519 | 1.9867 | 7.2643 | 0 | 2.911 | 0 | 0.015268 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 30.9073 | 2.601% | CZ 2B | 0 | 0 | 0.054888 | 0.064331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16282 | 2.601% | CZ 2B | 38.45 | 7.9737 | 5.9993 | 26.4187 | 20.7989 | 76.0503 | 0 | 30.4756 | 0 | 0.15984 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 341.3654 | 2.601%
CZ 3A | 0.39042 | 0.080949 | 0.054535 | 0.39241 | 0.086395 | 0.6612 | 0 | 0.2783 | 0.014117 | 0.0024093 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.3262 | 15.52% | CZ 3A | 12.5316 | 2.5983 | 5.5648 | 19.2846 | 2.7731 | 21.223 | 0 | 8.9329 | 0.45312 | 0.077333 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 120.2571 | 15.52% | CZ 3A | 3.6728 | 0.76152 | 0 | 2.7918 | 0.81275 | 6.2201 | 0 | 2.6181 | 0.1328 | 0.022665 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 29.4762 | 15.52% | CZ 3A | 0 | 0 | 0.055648 | 0.09759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19684 | 15.52% | CZ 3A | 38.4507 | 7.9723 | 6.0823 | 39.8939 | 8.5087 | 65.1184 | 0 | 27.4087 | 1.3903 | 0.23728 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 330.1016 | 15.52%
CZ 3B | 0.39035 | 0.080942 | 0.054253 | 0.24745 | 0.19806 | 0.58208 | 0 | 0.30058 | 0 | 0.0017384 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.2209 | 5.112% | CZ 3B | 12.5293 | 2.5981 | 5.5361 | 12.6969 | 6.3573 | 18.6836 | 0 | 9.6479 | 0 | 0.0558 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 114.9232 | 5.112% | CZ 3B | 3.6721 | 0.76145 | 0 | 1.6883 | 1.8632 | 5.4758 | 0 | 2.8276 | 0 | 0.016354 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 28.7487 | 5.112% | CZ 3B | 0 | 0 | 0.055361 | 0.069363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.16833 | 5.112% | CZ 3B | 38.4436 | 7.9716 | 6.0509 | 25.2566 | 19.506 | 57.3265 | 0 | 29.6024 | 0 | 0.17121 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 319.3679 | 5.112%
CZ 3C | 0.39036 | 0.081072 | 0.054024 | 0.20266 | 0.03158 | 0.51316 | 0 | 0.291 | 0 | 0.002027 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 2.9314 | 1.289% | CZ 3C | 12.5298 | 2.6022 | 5.5127 | 11.7613 | 1.0137 | 16.4712 | 0 | 9.3406 | 0 | 0.065062 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 106.1149 | 1.289% | CZ 3C | 3.6723 | 0.76267 | 0 | 1.1995 | 0.29709 | 4.8274 | 0 | 2.7376 | 0 | 0.019068 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 25.9594 | 1.289% | CZ 3C | 0 | 0 | 0.055127 | 0.076685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17542 | 1.289% | CZ 3C | 38.445 | 7.9844 | 6.0254 | 20.9397 | 3.1102 | 50.5385 | 0 | 28.6597 | 0 | 0.19963 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 290.9415 | 1.289%
CZ 4A | 0.39029 | 0.081086 | 0.055583 | 0.34158 | 0.12137 | 0.48075 | 0 | 0.28655 | 0.015408 | 0.002871 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.141 | 18.12% | CZ 4A | 12.5275 | 2.6027 | 5.6717 | 19.2136 | 3.8956 | 15.4312 | 0 | 9.1975 | 0.49456 | 0.092151 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 115.9448 | 18.12% | CZ 4A | 3.6716 | 0.76281 | 0 | 2.1038 | 1.1417 | 4.5226 | 0 | 2.6956 | 0.14495 | 0.027008 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 27.5139 | 18.12% | CZ 4A | 0 | 0 | 0.056717 | 0.12035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22067 | 18.12% | CZ 4A | 38.4379 | 7.9858 | 6.1992 | 35.1797 | 11.9528 | 47.3473 | 0 | 28.2207 | 1.5175 | 0.28275 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 312.1626 | 18.12%
CZ 4B | 0.39025 | 0.080913 | 0.055213 | 0.26752 | 0.26567 | 0.43077 | 0 | 0.3226 | 0 | 0.0018394 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.1803 | 0.607% | CZ 4B | 12.5263 | 2.5971 | 5.634 | 13.8083 | 8.5275 | 13.8269 | 0 | 10.3547 | 0 | 0.059042 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 114.1522 | 0.607% | CZ 4B | 3.6713 | 0.76118 | 0 | 1.8143 | 2.4993 | 4.0524 | 0 | 3.0348 | 0 | 0.017304 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 28.2942 | 0.607% | CZ 4B | 0 | 0 | 0.05634 | 0.07618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.17612 | 0.607% | CZ 4B | 38.4344 | 7.9688 | 6.1579 | 27.3202 | 26.1647 | 42.4248 | 0 | 31.7714 | 0 | 0.18116 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 315.4623 | 0.607%
CZ 4C | 0.39038 | 0.081065 | 0.05588 | 0.26658 | 0.026899 | 0.2835 | 0 | 0.28899 | 0 | 0.0027339 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 2.7615 | 2.878% | CZ 4C | 12.5303 | 2.602 | 5.702 | 16.5342 | 0.8634 | 9.0996 | 0 | 9.276 | 0 | 0.087752 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 103.5135 | 2.878% | CZ 4C | 3.6724 | 0.7626 | 0 | 1.4348 | 0.25305 | 2.6669 | 0 | 2.7186 | 0 | 0.025719 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 23.9779 | 2.878% | CZ 4C | 0 | 0 | 0.05702 | 0.11639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21701 | 2.878% | CZ 4C | 38.4465 | 7.9837 | 6.2323 | 27.7421 | 2.6492 | 27.9202 | 0 | 28.4615 | 0 | 0.26925 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 274.7436 | 2.878%
CZ 5A | 0.39031 | 0.080964 | 0.056953 | 0.40139 | 0.14939 | 0.3381 | 0 | 0.28399 | 0.014578 | 0.0032965 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.0845 | 23.41% | CZ 5A | 12.5282 | 2.5988 | 5.8115 | 23.1923 | 4.7951 | 10.8523 | 0 | 9.1153 | 0.46793 | 0.10581 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 116.2856 | 23.41% | CZ 5A | 3.6718 | 0.76165 | 0 | 2.3895 | 1.4054 | 3.1806 | 0 | 2.6716 | 0.13714 | 0.031012 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 26.6924 | 23.41% | CZ 5A | 0 | 0 | 0.058115 | 0.15039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.25211 | 23.41% | CZ 5A | 38.4401 | 7.9737 | 6.352 | 41.4539 | 14.7128 | 33.298 | 0 | 27.9685 | 1.4358 | 0.32466 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 306.9984 | 23.41%
CZ 5B | 0.39027 | 0.081043 | 0.05649 | 0.34349 | 0.26362 | 0.34205 | 0 | 0.31756 | 0 | 0.0023732 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.1624 | 5.921% | CZ 5B | 12.5268 | 2.6013 | 5.7643 | 18.4723 | 8.4615 | 10.979 | 0 | 10.1929 | 0 | 0.076175 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 115.8925 | 5.921% | CZ 5B | 3.6714 | 0.7624 | 0 | 2.2297 | 2.4799 | 3.2178 | 0 | 2.9874 | 0 | 0.022326 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 27.8146 | 5.921% | CZ 5B | 0 | 0 | 0.057643 | 0.10865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20989 | 5.921% | CZ 5B | 38.4358 | 7.9816 | 6.3004 | 35.2178 | 25.9623 | 33.6866 | 0 | 31.2748 | 0 | 0.23373 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 314.132 | 5.921%
CZ 5C | 0.39039 | 0.081029 | 0.056844 | 0.26457 | 0.018163 | 0.20972 | 0 | 0.29357 | 0 | 0.0029575 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 2.6827 | 0.1093% | CZ 5C | 12.5307 | 2.6008 | 5.8004 | 16.9913 | 0.58301 | 6.7314 | 0 | 9.423 | 0 | 0.09493 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 101.574 | 0.1093% | CZ 5C | 3.6725 | 0.76226 | 0 | 1.3458 | 0.17087 | 1.9729 | 0 | 2.7617 | 0 | 0.027822 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 23.1576 | 0.1093% | CZ 5C | 0 | 0 | 0.058004 | 0.12399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2256 | 0.1093% | CZ 5C | 38.4479 | 7.9801 | 6.3399 | 27.6416 | 1.7888 | 20.654 | 0 | 28.9126 | 0 | 0.29127 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 267.0952 | 0.1093%
CZ 6A | 0.3903 | 0.081007 | 0.058201 | 0.57077 | 0.25435 | 0.35826 | 0 | 0.30276 | 0.0153 | 0.0053019 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.4018 | 5.29% | CZ 6A | 12.5279 | 2.6001 | 5.9388 | 35.2234 | 8.1642 | 11.4992 | 0 | 9.718 | 0.49109 | 0.17018 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 133.1513 | 5.29% | CZ 6A | 3.6717 | 0.76206 | 0 | 3.096 | 2.3928 | 3.3702 | 0 | 2.8482 | 0.14393 | 0.049877 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 28.7785 | 5.29% | CZ 6A | 0 | 0 | 0.059388 | 0.2466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.34959 | 5.29% | CZ 6A | 38.4393 | 7.978 | 6.4912 | 59.3653 | 25.0501 | 35.283 | 0 | 29.8177 | 1.5068 | 0.52216 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 339.4925 | 5.29%
CZ 6B | 0.39034 | 0.080906 | 0.057883 | 0.51921 | 0.33612 | 0.28068 | 0 | 0.32126 | 0 | 0.005035 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.3569 | 0.7888% | CZ 6B | 12.5291 | 2.5969 | 5.9064 | 31.6926 | 10.7889 | 9.0093 | 0 | 10.3117 | 0 | 0.16161 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 129.8148 | 0.7888% | CZ 6B | 3.6721 | 0.76111 | 0 | 2.8633 | 3.162 | 2.6405 | 0 | 3.0222 | 0 | 0.047366 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 28.6122 | 0.7888% | CZ 6B | 0 | 0 | 0.059064 | 0.21923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.3219 | 0.7888% | CZ 6B | 38.4429 | 7.9681 | 6.4557 | 53.9375 | 33.1034 | 27.6431 | 0 | 31.6392 | 0 | 0.49587 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 334.7248 | 0.7888%
CZ 7 | 0.3903 | 0.081029 | 0.059698 | 0.66267 | 0.327 | 0.2974 | 0 | 0.30886 | 0.015487 | 0.0059944 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.5139 | 0.8424% | CZ 7 | 12.5279 | 2.6008 | 6.0916 | 41.953 | 10.496 | 9.546 | 0 | 9.9137 | 0.49711 | 0.19241 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 140.6369 | 0.8424% | CZ 7 | 3.6717 | 0.76226 | 0 | 3.4521 | 3.0762 | 2.7978 | 0 | 2.9055 | 0.14569 | 0.056391 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 29.3113 | 0.8424% | CZ 7 | 0 | 0 | 0.060916 | 0.30175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.40627 | 0.8424% | CZ 7 | 38.4393 | 7.9801 | 6.6581 | 69.1205 | 32.2047 | 29.2899 | 0 | 30.418 | 1.5253 | 0.59036 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 351.2653 | 0.8424%
CZ 8 | 0.39063 | 0.081497 | 0.061776 | 0.9316 | 0.40982 | 0.17374 | 0 | 0.30988 | 0 | 0.0076535 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.7321 | 0.06096% | CZ 8 | 12.5384 | 2.6159 | 6.3037 | 61.5186 | 13.1542 | 5.5765 | 0 | 9.9466 | 0 | 0.24566 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 158.7178 | 0.06096% | CZ 8 | 3.6748 | 0.76667 | 0 | 4.5115 | 3.8553 | 1.6344 | 0 | 2.9152 | 0 | 0.071999 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 29.8735 | 0.06096% | CZ 8 | 0 | 0 | 0.063037 | 0.46125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.56789 | 0.06096% | CZ 8 | 38.4713 | 8.0263 | 6.8899 | 97.6458 | 40.361 | 17.1104 | 0 | 30.5189 | 0 | 0.75375 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 374.8164 | 0.06096%
US Weighted | 0.39034 | 0.080985 | 0.055545 | 0.35466 | 0.12578 | 0.56159 | 0 | 0.29077 | 0.012491 | 0.0027878 | 0 | 0.46241 | 0 | 0 | 0 | 0.90309 | 3.2404 | 100% | US Weighted | 12.5289 | 2.5994 | 5.6678 | 19.6761 | 4.0373 | 18.0257 | 0 | 9.3332 | 0.40094 | 0.089482 | 0 | 14.8424 | 0 | 0 | 0 | 31.9759 | 119.1772 | 100% | US Weighted | 3.672 | 0.76185 | 0 | 2.2211 | 1.1833 | 5.283 | 0 | 2.7354 | 0.11751 | 0.026226 | 0 | 4.3501 | 0 | 0 | 0 | 8.0936 | 28.4441 | 100% | US Weighted | 0 | 0 | 0.056678 | 0.12098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22126 | 100% | US Weighted | 38.4423 | 7.9759 | 6.1949 | 36.4754 | 12.3875 | 55.3081 | 0 | 28.637 | 1.2302 | 0.27456 | 0 | 45.5407 | 0 | 0 | 0 | 89.4983 | 321.9648 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.44094 | 0.16394 | 0.054653 | 0.27712 | 0 | 1.871 | 0 | 0.42139 | 0 | 0.0033326 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.6122 | 0% | CZ 0A | 14.1533 | 5.2621 | 5.5768 | 17.3441 | 0 | 60.0558 | 0 | 13.5259 | 0 | 0.10697 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 163.3034 | 0% | CZ 0A | 4.1481 | 1.5422 | 0 | 1.4706 | 0 | 17.6013 | 0 | 3.9642 | 0 | 0.031351 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 41.3364 | 0% | CZ 0A | 0 | 0 | 0.055768 | 0.12327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22264 | 0% | CZ 0A | 43.4265 | 16.1457 | 6.0955 | 28.8684 | 0 | 184.2685 | 0 | 41.5013 | 0 | 0.32821 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 457.0845 | 0%
CZ 0B | 0.44094 | 0.16397 | 0.054653 | 0.38486 | 0.00028132 | 1.6711 | 0 | 0.41098 | 0 | 0.0027555 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.5094 | 0% | CZ 0B | 14.1533 | 5.263 | 5.5768 | 20.2515 | 0.0090299 | 53.6383 | 0 | 13.1915 | 0 | 0.088447 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 159.4503 | 0% | CZ 0B | 4.1481 | 1.5425 | 0 | 2.5582 | 0.0026465 | 15.7205 | 0 | 3.8662 | 0 | 0.025922 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 40.4426 | 0% | CZ 0B | 0 | 0 | 0.055768 | 0.11523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2146 | 0% | CZ 0B | 43.4265 | 16.1485 | 6.0955 | 39.3761 | 0.027706 | 164.5778 | 0 | 40.4754 | 0 | 0.27138 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 446.8494 | 0%
CZ 1A | 0.44094 | 0.16399 | 0.054653 | 0.29373 | 0 | 1.3898 | 0 | 0.39773 | 0 | 0.0031306 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1238 | 1.601% | CZ 1A | 14.1533 | 5.2637 | 5.5768 | 16.9242 | 0 | 44.6096 | 0 | 12.7664 | 0 | 0.10049 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 146.6729 | 1.601% | CZ 1A | 4.1481 | 1.5427 | 0 | 1.755 | 0 | 13.0743 | 0 | 3.7416 | 0 | 0.029451 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.8697 | 1.601% | CZ 1A | 0 | 0 | 0.055768 | 0.10936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20873 | 1.601% | CZ 1A | 43.4265 | 16.1507 | 6.0955 | 30.3262 | 0 | 136.875 | 0 | 39.1711 | 0 | 0.30832 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 408.8038 | 1.601%
CZ 1B | 0.44094 | 0.16378 | 0.054653 | 0.38088 | 0.00020919 | 1.4369 | 0 | 0.39572 | 0 | 0.0018394 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.2548 | 0% | CZ 1B | 14.1533 | 5.257 | 5.5768 | 18.5246 | 0.0067145 | 46.122 | 0 | 12.7016 | 0 | 0.059042 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 149.6794 | 0% | CZ 1B | 4.1481 | 1.5407 | 0 | 2.7358 | 0.0019679 | 13.5176 | 0 | 3.7226 | 0 | 0.017304 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 38.2627 | 0% | CZ 1B | 0 | 0 | 0.055768 | 0.0919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19127 | 0% | CZ 1B | 43.4265 | 16.1301 | 6.0955 | 38.6859 | 0.020602 | 141.5155 | 0 | 38.9722 | 0 | 0.18116 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 421.4779 | 0%
CZ 2A | 0.44094 | 0.16373 | 0.054653 | 0.39381 | 0.0068744 | 1.2895 | 0 | 0.3825 | 0 | 0.0020919 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1139 | 15.85% | CZ 2A | 14.1533 | 5.2554 | 5.5768 | 19.8211 | 0.22065 | 41.3898 | 0 | 12.2774 | 0 | 0.067145 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 146.04 | 15.85% | CZ 2A | 4.1481 | 1.5403 | 0 | 2.7389 | 0.06467 | 12.1307 | 0 | 3.5983 | 0 | 0.019679 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.8192 | 15.85% | CZ 2A | 0 | 0 | 0.055768 | 0.10476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20413 | 15.85% | CZ 2A | 43.4265 | 16.1251 | 6.0955 | 40.124 | 0.67703 | 126.9959 | 0 | 37.6707 | 0 | 0.20602 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 407.7713 | 15.85%
CZ 2B | 0.44094 | 0.16385 | 0.054653 | 0.47659 | 0.12291 | 0.95971 | 0 | 0.40188 | 0 | 0.0017745 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.0021 | 2.601% | CZ 2B | 14.1533 | 5.2591 | 5.5768 | 21.5001 | 3.9451 | 30.8045 | 0 | 12.8996 | 0 | 0.056958 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 141.4738 | 2.601% | CZ 2B | 4.1481 | 1.5414 | 0 | 3.6492 | 1.1563 | 9.0283 | 0 | 3.7806 | 0 | 0.016693 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 35.8991 | 2.601% | CZ 2B | 0 | 0 | 0.055768 | 0.09049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18986 | 2.601% | CZ 2B | 43.4265 | 16.1365 | 6.0955 | 48.0941 | 12.1048 | 94.517 | 0 | 39.5796 | 0 | 0.17476 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 396.5792 | 2.601%
CZ 3A | 0.44094 | 0.16382 | 0.055326 | 0.52627 | 0.063933 | 0.90883 | 0 | 0.36564 | 0 | 0.0027627 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.9074 | 15.52% | CZ 3A | 14.1533 | 5.2582 | 5.6456 | 25.0491 | 2.0521 | 29.1714 | 0 | 11.7363 | 0 | 0.088678 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 140.433 | 15.52% | CZ 3A | 4.1481 | 1.5411 | 0 | 3.8537 | 0.60144 | 8.5497 | 0 | 3.4397 | 0 | 0.02599 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.7383 | 15.52% | CZ 3A | 0 | 0 | 0.056456 | 0.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21906 | 15.52% | CZ 3A | 43.4265 | 16.1336 | 6.1706 | 53.3516 | 6.2964 | 89.5064 | 0 | 36.0104 | 0 | 0.27209 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 387.6182 | 15.52%
CZ 3B | 0.44094 | 0.16381 | 0.055045 | 0.48894 | 0.14518 | 0.74524 | 0 | 0.38771 | 0 | 0.0023876 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.8091 | 5.112% | CZ 3B | 14.1533 | 5.2579 | 5.6169 | 22.6538 | 4.6601 | 23.9207 | 0 | 12.4446 | 0 | 0.076638 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 136.0623 | 5.112% | CZ 3B | 4.1481 | 1.541 | 0 | 3.6636 | 1.3658 | 7.0107 | 0 | 3.6473 | 0 | 0.022461 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 33.9776 | 5.112% | CZ 3B | 0 | 0 | 0.056169 | 0.10154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20131 | 5.112% | CZ 3B | 43.4265 | 16.1329 | 6.1392 | 49.452 | 14.2986 | 73.3955 | 0 | 38.1836 | 0 | 0.23515 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 377.7141 | 5.112%
CZ 3C | 0.44094 | 0.16378 | 0.054802 | 0.43127 | 0.019123 | 0.69811 | 0 | 0.36263 | 0 | 0.0024309 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.5529 | 1.289% | CZ 3C | 14.1533 | 5.257 | 5.5921 | 21.1478 | 0.6138 | 22.4078 | 0 | 11.6398 | 0 | 0.078028 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 128.168 | 1.289% | CZ 3C | 4.1481 | 1.5407 | 0 | 3.0746 | 0.17989 | 6.5674 | 0 | 3.4114 | 0 | 0.022869 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 31.5236 | 1.289% | CZ 3C | 0 | 0 | 0.055921 | 0.10657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.2061 | 1.289% | CZ 3C | 43.4265 | 16.1301 | 6.1122 | 43.8366 | 1.8833 | 68.7536 | 0 | 35.7142 | 0 | 0.23941 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 352.5464 | 1.289%
CZ 4A | 0.44094 | 0.16356 | 0.056345 | 0.63985 | 0.097252 | 0.74504 | 0 | 0.36077 | 0 | 0.0032244 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.8868 | 18.12% | CZ 4A | 14.1533 | 5.2501 | 5.7495 | 30.1095 | 3.1216 | 23.9142 | 0 | 11.58 | 0 | 0.1035 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 141.26 | 18.12% | CZ 4A | 4.1481 | 1.5387 | 0 | 4.7319 | 0.91488 | 7.0088 | 0 | 3.3939 | 0 | 0.030333 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.3452 | 18.12% | CZ 4A | 0 | 0 | 0.057495 | 0.13964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24074 | 18.12% | CZ 4A | 43.4265 | 16.1087 | 6.2842 | 64.8011 | 9.5779 | 73.3756 | 0 | 35.5309 | 0 | 0.31756 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 385.8731 | 18.12%
CZ 4B | 0.44094 | 0.16369 | 0.05598 | 0.51236 | 0.20892 | 0.55653 | 0 | 0.40448 | 0 | 0.0022001 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.7249 | 0.607% | CZ 4B | 14.1533 | 5.254 | 5.7122 | 22.3437 | 6.7057 | 17.8635 | 0 | 12.9829 | 0 | 0.070618 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 132.3643 | 0.607% | CZ 4B | 4.1481 | 1.5399 | 0 | 4.0267 | 1.9653 | 5.2355 | 0 | 3.8051 | 0 | 0.020697 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 33.3198 | 0.607% | CZ 4B | 0 | 0 | 0.057122 | 0.086046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18677 | 0.607% | CZ 4B | 43.4265 | 16.1208 | 6.2435 | 51.5603 | 20.5752 | 54.8102 | 0 | 39.8353 | 0 | 0.21668 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 369.2391 | 0.607%
CZ 4C | 0.44094 | 0.16338 | 0.056549 | 0.56626 | 0.014658 | 0.41239 | 0 | 0.36096 | 0 | 0.0023949 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.3974 | 2.878% | CZ 4C | 14.1533 | 5.2441 | 5.7703 | 25.1847 | 0.47048 | 13.2369 | 0 | 11.5861 | 0 | 0.07687 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 123.0011 | 2.878% | CZ 4C | 4.1481 | 1.5369 | 0 | 4.3843 | 0.13789 | 3.8795 | 0 | 3.3957 | 0 | 0.022529 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 30.0835 | 2.878% | CZ 4C | 0 | 0 | 0.057703 | 0.10225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20356 | 2.878% | CZ 4C | 43.4265 | 16.0903 | 6.307 | 57.0758 | 1.4436 | 40.6147 | 0 | 35.5494 | 0 | 0.23586 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 337.1936 | 2.878%
CZ 5A | 0.44094 | 0.16362 | 0.0576 | 0.73432 | 0.12503 | 0.45051 | 0 | 0.35829 | 0 | 0.0035923 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.7137 | 23.41% | CZ 5A | 14.1533 | 5.2517 | 5.8775 | 35.1565 | 4.0132 | 14.4603 | 0 | 11.5004 | 0 | 0.1153 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 137.8066 | 23.41% | CZ 5A | 4.1481 | 1.5392 | 0 | 5.3497 | 1.1762 | 4.2381 | 0 | 3.3706 | 0 | 0.033794 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 32.4342 | 23.41% | CZ 5A | 0 | 0 | 0.058775 | 0.16903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.27141 | 23.41% | CZ 5A | 43.4265 | 16.1137 | 6.4241 | 74.4812 | 12.3137 | 44.3685 | 0 | 35.2865 | 0 | 0.35379 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 369.2186 | 23.41%
CZ 5B | 0.44094 | 0.16362 | 0.057132 | 0.6198 | 0.20298 | 0.45271 | 0 | 0.40011 | 0 | 0.0028637 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.72 | 5.921% | CZ 5B | 14.1533 | 5.2519 | 5.8298 | 28.0171 | 6.5152 | 14.531 | 0 | 12.8426 | 0 | 0.09192 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 134.5112 | 5.921% | CZ 5B | 4.1481 | 1.5393 | 0 | 4.7381 | 1.9095 | 4.2588 | 0 | 3.764 | 0 | 0.02694 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 32.9632 | 5.921% | CZ 5B | 0 | 0 | 0.058298 | 0.11851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22041 | 5.921% | CZ 5B | 43.4265 | 16.1144 | 6.372 | 62.5563 | 19.9905 | 44.5852 | 0 | 39.4048 | 0 | 0.28204 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 369.1823 | 5.921%
CZ 5C | 0.44094 | 0.16336 | 0.057432 | 0.60062 | 0.0089014 | 0.32846 | 0 | 0.36167 | 0 | 0.0032821 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.3445 | 0.1093% | CZ 5C | 14.1533 | 5.2436 | 5.8604 | 28.7293 | 0.28572 | 10.543 | 0 | 11.6087 | 0 | 0.10535 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 123.8078 | 0.1093% | CZ 5C | 4.1481 | 1.5368 | 0 | 4.3792 | 0.083738 | 3.09 | 0 | 3.4023 | 0 | 0.030876 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 29.2495 | 0.1093% | CZ 5C | 0 | 0 | 0.058604 | 0.13788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24008 | 0.1093% | CZ 5C | 43.4265 | 16.0889 | 6.4054 | 60.9153 | 0.87666 | 32.3489 | 0 | 35.619 | 0 | 0.32324 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 332.4545 | 0.1093%
CZ 6A | 0.44094 | 0.16354 | 0.0588 | 0.94499 | 0.20968 | 0.47076 | 0 | 0.37902 | 0 | 0.0052875 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.0529 | 5.29% | CZ 6A | 14.1533 | 5.2494 | 6 | 50.6999 | 6.7303 | 15.1105 | 0 | 12.1656 | 0 | 0.16972 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 157.557 | 5.29% | CZ 6A | 4.1481 | 1.5385 | 0 | 6.1504 | 1.9725 | 4.4286 | 0 | 3.5655 | 0 | 0.049741 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.4319 | 5.29% | CZ 6A | 0 | 0 | 0.06 | 0.29715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.40075 | 5.29% | CZ 6A | 43.4265 | 16.1066 | 6.558 | 96.8664 | 20.6505 | 46.3634 | 0 | 37.3275 | 0 | 0.52074 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 404.2702 | 5.29%
CZ 6B | 0.44094 | 0.16342 | 0.058496 | 0.86231 | 0.26359 | 0.38383 | 0 | 0.40027 | 0 | 0.0047464 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.9574 | 0.7888% | CZ 6B | 14.1533 | 5.2454 | 5.9689 | 44.5374 | 8.4608 | 12.3203 | 0 | 12.8477 | 0 | 0.15235 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 150.9645 | 0.7888% | CZ 6B | 4.1481 | 1.5374 | 0 | 5.8445 | 2.4797 | 3.6109 | 0 | 3.7654 | 0 | 0.044651 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.0092 | 0.7888% | CZ 6B | 0 | 0 | 0.059689 | 0.24596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.34925 | 0.7888% | CZ 6B | 43.4265 | 16.0945 | 6.524 | 88.0696 | 25.9601 | 37.8021 | 0 | 39.4204 | 0 | 0.46746 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 394.2153 | 0.7888%
CZ 7 | 0.44094 | 0.16332 | 0.060333 | 1.058 | 0.27444 | 0.39396 | 0 | 0.38505 | 0 | 0.0057563 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1616 | 0.8424% | CZ 7 | 14.1533 | 5.2422 | 6.1564 | 58.2283 | 8.8088 | 12.6453 | 0 | 12.3594 | 0 | 0.18477 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 165.0568 | 0.8424% | CZ 7 | 4.1481 | 1.5364 | 0 | 6.689 | 2.5817 | 3.7061 | 0 | 3.6223 | 0 | 0.054152 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.9163 | 0.8424% | CZ 7 | 0 | 0 | 0.061564 | 0.35406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.45922 | 0.8424% | CZ 7 | 43.4265 | 16.0846 | 6.729 | 108.7249 | 27.0279 | 38.7995 | 0 | 37.9222 | 0 | 0.56691 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 415.7321 | 0.8424%
CZ 8 | 0.44094 | 0.16243 | 0.062352 | 1.3616 | 0.35677 | 0.25445 | 0 | 0.38942 | 0 | 0.0069898 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.4148 | 0.06096% | CZ 8 | 14.1533 | 5.2135 | 6.3625 | 76.2735 | 11.4515 | 8.1672 | 0 | 12.4995 | 0 | 0.22436 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 181.6237 | 0.06096% | CZ 8 | 4.1481 | 1.528 | 0 | 8.4289 | 3.3563 | 2.3937 | 0 | 3.6634 | 0 | 0.065756 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.1626 | 0.06096% | CZ 8 | 0 | 0 | 0.063625 | 0.47514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.58237 | 0.06096% | CZ 8 | 43.4265 | 15.9965 | 6.9542 | 140.1749 | 35.1366 | 25.0593 | 0 | 38.352 | 0 | 0.6884 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 442.2389 | 0.06096%
US Weighted | 0.44094 | 0.16367 | 0.056291 | 0.6029 | 0.098189 | 0.754 | 0 | 0.37155 | 0 | 0.0030606 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.8704 | 100% | US Weighted | 14.1533 | 5.2533 | 5.7439 | 29.0975 | 3.1517 | 24.2017 | 0 | 11.926 | 0 | 0.098238 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 140.9041 | 100% | US Weighted | 4.1481 | 1.5397 | 0 | 4.3609 | 0.9237 | 7.0931 | 0 | 3.4953 | 0 | 0.028792 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.1681 | 100% | US Weighted | 0 | 0 | 0.057439 | 0.14218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24323 | 100% | US Weighted | 43.4265 | 16.1186 | 6.2781 | 61.1944 | 9.6702 | 74.2579 | 0 | 36.5925 | 0 | 0.30142 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 384.2903 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 40946 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.44094 | 0.16394 | 0.054653 | 0.28581 | 0 | 2.0173 | 0 | 0.46979 | 0 | 0.0032388 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.8155 | 0% | CZ 0A | 14.1533 | 5.2621 | 5.5768 | 17.4005 | 0 | 64.7506 | 0 | 15.0792 | 0 | 0.10396 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 169.6049 | 0% | CZ 0A | 4.1481 | 1.5422 | 0 | 1.5823 | 0 | 18.9773 | 0 | 4.4195 | 0 | 0.030469 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 43.2784 | 0% | CZ 0A | 0 | 0 | 0.055768 | 0.12002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21939 | 0% | CZ 0A | 43.4265 | 16.1457 | 6.0955 | 29.6828 | 0 | 198.6736 | 0 | 46.2675 | 0 | 0.31898 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 477.061 | 0%
CZ 0B | 0.44094 | 0.16397 | 0.054653 | 0.41039 | 0.0003751 | 1.7822 | 0 | 0.45419 | 0 | 0.0026834 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.6893 | 0% | CZ 0B | 14.1533 | 5.263 | 5.5768 | 20.9971 | 0.01204 | 57.2056 | 0 | 14.5784 | 0 | 0.086131 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 165.1508 | 0% | CZ 0B | 4.1481 | 1.5425 | 0 | 2.8083 | 0.0035287 | 16.766 | 0 | 4.2727 | 0 | 0.025244 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 42.1449 | 0% | CZ 0B | 0 | 0 | 0.055768 | 0.11415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21352 | 0% | CZ 0B | 43.4265 | 16.1485 | 6.0955 | 41.8768 | 0.036942 | 175.5232 | 0 | 44.7308 | 0 | 0.26428 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 464.5531 | 0%
CZ 1A | 0.44094 | 0.16399 | 0.054653 | 0.31954 | 0 | 1.4921 | 0 | 0.43362 | 0 | 0.0031451 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.2879 | 1.601% | CZ 1A | 14.1533 | 5.2637 | 5.5768 | 17.8335 | 0 | 47.8939 | 0 | 13.9183 | 0 | 0.10095 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 152.0188 | 1.601% | CZ 1A | 4.1481 | 1.5427 | 0 | 1.987 | 0 | 14.0369 | 0 | 4.0792 | 0 | 0.029587 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 38.402 | 1.601% | CZ 1A | 0 | 0 | 0.055768 | 0.11054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.20991 | 1.601% | CZ 1A | 43.4265 | 16.1507 | 6.0955 | 32.8836 | 0 | 146.9523 | 0 | 42.7054 | 0 | 0.30974 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 424.9743 | 1.601%
CZ 1B | 0.44094 | 0.16378 | 0.054653 | 0.412 | 0.00030296 | 1.5332 | 0 | 0.43514 | 0 | 0.0018611 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.4217 | 0% | CZ 1B | 14.1533 | 5.257 | 5.5768 | 19.5276 | 0.0097245 | 49.2132 | 0 | 13.9672 | 0 | 0.059736 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 155.0429 | 0% | CZ 1B | 4.1481 | 1.5407 | 0 | 3.0281 | 0.0028501 | 14.4236 | 0 | 4.0935 | 0 | 0.017508 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 39.8329 | 0% | CZ 1B | 0 | 0 | 0.055768 | 0.091958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19133 | 0% | CZ 1B | 43.4265 | 16.1301 | 6.0955 | 41.752 | 0.029838 | 151.0003 | 0 | 42.8553 | 0 | 0.18329 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 437.9233 | 0%
CZ 2A | 0.44094 | 0.16373 | 0.054653 | 0.45459 | 0.0088293 | 1.4026 | 0 | 0.42591 | 0 | 0.0019837 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.3331 | 15.85% | CZ 2A | 14.1533 | 5.2554 | 5.5768 | 21.4297 | 0.2834 | 45.0212 | 0 | 13.6708 | 0 | 0.063672 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 152.7327 | 15.85% | CZ 2A | 4.1481 | 1.5403 | 0 | 3.3567 | 0.08306 | 13.195 | 0 | 4.0067 | 0 | 0.018661 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 38.9269 | 15.85% | CZ 2A | 0 | 0 | 0.055768 | 0.099768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.19914 | 15.85% | CZ 2A | 43.4265 | 16.1251 | 6.0955 | 46.0455 | 0.86955 | 138.1381 | 0 | 41.946 | 0 | 0.19537 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 429.2921 | 15.85%
CZ 2B | 0.44094 | 0.16385 | 0.054653 | 0.52957 | 0.145 | 1.0138 | 0 | 0.44677 | 0 | 0.0015365 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1759 | 2.601% | CZ 2B | 14.1533 | 5.2591 | 5.5768 | 21.5785 | 4.6541 | 32.5396 | 0 | 14.3404 | 0 | 0.049317 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 145.4295 | 2.601% | CZ 2B | 4.1481 | 1.5414 | 0 | 4.3658 | 1.364 | 9.5368 | 0 | 4.2029 | 0 | 0.014454 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 37.752 | 2.601% | CZ 2B | 0 | 0 | 0.055768 | 0.066824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.1662 | 2.601% | CZ 2B | 43.4265 | 16.1365 | 6.0955 | 53.0093 | 14.2801 | 99.8409 | 0 | 44.0005 | 0 | 0.15132 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 413.3911 | 2.601%
CZ 3A | 0.44094 | 0.16382 | 0.055326 | 0.61409 | 0.079023 | 0.96672 | 0 | 0.40488 | 0 | 0.0029864 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1076 | 15.52% | CZ 3A | 14.1533 | 5.2582 | 5.6456 | 28.4777 | 2.5365 | 31.0297 | 0 | 12.9959 | 0 | 0.095856 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 147.471 | 15.52% | CZ 3A | 4.1481 | 1.5411 | 0 | 4.5978 | 0.7434 | 9.0943 | 0 | 3.8089 | 0 | 0.028094 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.5402 | 15.52% | CZ 3A | 0 | 0 | 0.056456 | 0.1279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.22796 | 15.52% | CZ 3A | 43.4265 | 16.1336 | 6.1706 | 62.1139 | 7.7826 | 95.2082 | 0 | 39.8751 | 0 | 0.29411 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 407.4552 | 15.52%
CZ 3B | 0.44094 | 0.16381 | 0.055045 | 0.54938 | 0.17568 | 0.77713 | 0 | 0.4291 | 0 | 0.0020486 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.973 | 5.112% | CZ 3B | 14.1533 | 5.2579 | 5.6169 | 23.1611 | 5.6388 | 24.9441 | 0 | 13.7731 | 0 | 0.065756 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 139.8894 | 5.112% | CZ 3B | 4.1481 | 1.541 | 0 | 4.4248 | 1.6526 | 7.3107 | 0 | 4.0367 | 0 | 0.019272 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 35.7117 | 5.112% | CZ 3B | 0 | 0 | 0.056169 | 0.080638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18041 | 5.112% | CZ 3B | 43.4265 | 16.1329 | 6.1392 | 55.1366 | 17.3015 | 76.5356 | 0 | 42.26 | 0 | 0.20176 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 393.5847 | 5.112%
CZ 3C | 0.44094 | 0.16378 | 0.054802 | 0.52647 | 0.023638 | 0.78065 | 0 | 0.4175 | 0 | 0.0017889 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.7894 | 1.289% | CZ 3C | 14.1533 | 5.257 | 5.5921 | 22.9264 | 0.75874 | 25.057 | 0 | 13.4008 | 0 | 0.057421 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 134.4812 | 1.289% | CZ 3C | 4.1481 | 1.5407 | 0 | 4.142 | 0.22237 | 7.3438 | 0 | 3.9276 | 0 | 0.016829 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 33.9199 | 1.289% | CZ 3C | 0 | 0 | 0.055921 | 0.087939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.18746 | 1.289% | CZ 3C | 43.4265 | 16.1301 | 6.1122 | 52.9743 | 2.328 | 76.8822 | 0 | 41.1176 | 0 | 0.17618 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 375.5977 | 1.289%
CZ 4A | 0.44094 | 0.16356 | 0.056345 | 0.81128 | 0.12305 | 0.78513 | 0 | 0.3988 | 0 | 0.0039746 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1629 | 18.12% | CZ 4A | 14.1533 | 5.2501 | 5.7495 | 38.1762 | 3.9498 | 25.2011 | 0 | 12.8005 | 0 | 0.12758 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 152.6863 | 18.12% | CZ 4A | 4.1481 | 1.5387 | 0 | 5.9996 | 1.1576 | 7.386 | 0 | 3.7516 | 0 | 0.03739 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.5976 | 18.12% | CZ 4A | 0 | 0 | 0.057495 | 0.17705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.27815 | 18.12% | CZ 4A | 43.4265 | 16.1087 | 6.2842 | 82.1623 | 12.119 | 77.3241 | 0 | 39.2755 | 0 | 0.39144 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 413.5424 | 18.12%
CZ 4B | 0.44094 | 0.16369 | 0.05598 | 0.65191 | 0.24533 | 0.59062 | 0 | 0.44818 | 0 | 0.0026545 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.9791 | 0.607% | CZ 4B | 14.1533 | 5.254 | 5.7122 | 28.4263 | 7.8745 | 18.9577 | 0 | 14.3856 | 0 | 0.085205 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 142.1272 | 0.607% | CZ 4B | 4.1481 | 1.5399 | 0 | 5.1239 | 2.3079 | 5.5562 | 0 | 4.2162 | 0 | 0.024972 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 35.4956 | 0.607% | CZ 4B | 0 | 0 | 0.057122 | 0.10944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21016 | 0.607% | CZ 4B | 43.4265 | 16.1208 | 6.2435 | 65.603 | 24.1613 | 58.1677 | 0 | 44.139 | 0 | 0.26143 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 394.5739 | 0.607%
CZ 4C | 0.44094 | 0.16338 | 0.056549 | 0.76174 | 0.032662 | 0.43558 | 0 | 0.4027 | 0 | 0.0033543 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.6767 | 2.878% | CZ 4C | 14.1533 | 5.2441 | 5.7703 | 34.537 | 1.0484 | 13.9813 | 0 | 12.926 | 0 | 0.10766 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 135.0463 | 2.878% | CZ 4C | 4.1481 | 1.5369 | 0 | 5.8093 | 0.30727 | 4.0977 | 0 | 3.7884 | 0 | 0.031555 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 32.2978 | 2.878% | CZ 4C | 0 | 0 | 0.057703 | 0.14716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24846 | 2.878% | CZ 4C | 43.4265 | 16.0903 | 6.307 | 76.9017 | 3.2168 | 42.8986 | 0 | 39.6606 | 0 | 0.33034 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 365.2824 | 2.878%
CZ 5A | 0.44094 | 0.16362 | 0.057595 | 0.91707 | 0.15585 | 0.46257 | 0 | 0.39556 | 0 | 0.0044363 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.9775 | 23.41% | CZ 5A | 14.1533 | 5.2517 | 5.877 | 45.3231 | 5.0026 | 14.8475 | 0 | 12.6967 | 0 | 0.14239 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 150.5727 | 23.41% | CZ 5A | 4.1481 | 1.5392 | 0 | 6.4903 | 1.4662 | 4.3515 | 0 | 3.7212 | 0 | 0.041733 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.3368 | 23.41% | CZ 5A | 0 | 0 | 0.05877 | 0.23178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.33415 | 23.41% | CZ 5A | 43.4265 | 16.1137 | 6.4236 | 93.2809 | 15.3493 | 45.5563 | 0 | 38.9572 | 0 | 0.43691 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 395.9951 | 23.41%
CZ 5B | 0.44094 | 0.16362 | 0.057132 | 0.74587 | 0.23643 | 0.45467 | 0 | 0.43842 | 0 | 0.0031595 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.9201 | 5.921% | CZ 5B | 14.1533 | 5.2519 | 5.8298 | 33.5774 | 7.5888 | 14.5939 | 0 | 14.0723 | 0 | 0.10141 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 142.4473 | 5.921% | CZ 5B | 4.1481 | 1.5393 | 0 | 5.7205 | 2.2242 | 4.2772 | 0 | 4.1244 | 0 | 0.029722 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 34.6418 | 5.921% | CZ 5B | 0 | 0 | 0.058298 | 0.14059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.24249 | 5.921% | CZ 5B | 43.4265 | 16.1144 | 6.372 | 75.2543 | 23.2847 | 44.7784 | 0 | 43.1778 | 0 | 0.31116 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 389.1699 | 5.921%
CZ 5C | 0.44094 | 0.16336 | 0.057432 | 0.69346 | 0.011397 | 0.30771 | 0 | 0.4007 | 0 | 0.0027844 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 3.4576 | 0.1093% | CZ 5C | 14.1533 | 5.2436 | 5.8604 | 30.2608 | 0.36583 | 9.8769 | 0 | 12.8616 | 0 | 0.089373 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 125.9901 | 0.1093% | CZ 5C | 4.1481 | 1.5368 | 0 | 5.4473 | 0.10722 | 2.8947 | 0 | 3.7695 | 0 | 0.026194 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 30.5085 | 0.1093% | CZ 5C | 0 | 0 | 0.058604 | 0.11674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.21895 | 0.1093% | CZ 5C | 43.4265 | 16.0889 | 6.4054 | 69.7883 | 1.1225 | 30.3051 | 0 | 39.4631 | 0 | 0.27422 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 343.3245 | 0.1093%
CZ 6A | 0.44094 | 0.16354 | 0.058804 | 1.1479 | 0.25055 | 0.4776 | 0 | 0.41806 | 0 | 0.0058501 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.3431 | 5.29% | CZ 6A | 14.1533 | 5.2494 | 6.0004 | 60.9861 | 8.0422 | 15.33 | 0 | 13.4189 | 0 | 0.18778 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 170.6464 | 5.29% | CZ 6A | 4.1481 | 1.5385 | 0 | 7.5517 | 2.357 | 4.493 | 0 | 3.9329 | 0 | 0.055034 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.6547 | 5.29% | CZ 6A | 0 | 0 | 0.060004 | 0.3522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.4558 | 5.29% | CZ 6A | 43.4265 | 16.1066 | 6.5585 | 117.554 | 24.6757 | 47.0368 | 0 | 41.173 | 0 | 0.57615 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 433.5579 | 5.29%
CZ 6B | 0.44094 | 0.16342 | 0.058496 | 1.0313 | 0.30872 | 0.37869 | 0 | 0.43925 | 0 | 0.0050855 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.2057 | 0.7888% | CZ 6B | 14.1533 | 5.2454 | 5.9689 | 52.3453 | 9.9093 | 12.1552 | 0 | 14.0989 | 0 | 0.16323 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 161.318 | 0.7888% | CZ 6B | 4.1481 | 1.5374 | 0 | 7.1133 | 2.9042 | 3.5625 | 0 | 4.1322 | 0 | 0.047841 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.024 | 0.7888% | CZ 6B | 0 | 0 | 0.059689 | 0.28075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.38404 | 0.7888% | CZ 6B | 43.4265 | 16.0945 | 6.524 | 105.1547 | 30.4045 | 37.2956 | 0 | 43.2595 | 0 | 0.50085 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 419.1108 | 0.7888%
CZ 7 | 0.44094 | 0.16332 | 0.060338 | 1.286 | 0.32617 | 0.39898 | 0 | 0.42761 | 0 | 0.0065642 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.4898 | 0.8424% | CZ 7 | 14.1533 | 5.2422 | 6.1569 | 70.5616 | 10.4694 | 12.8063 | 0 | 13.7254 | 0 | 0.2107 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 180.6041 | 0.8424% | CZ 7 | 4.1481 | 1.5364 | 0 | 8.1592 | 3.0684 | 3.7533 | 0 | 4.0227 | 0 | 0.061752 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 37.3284 | 0.8424% | CZ 7 | 0 | 0 | 0.061569 | 0.42722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.5324 | 0.8424% | CZ 7 | 43.4265 | 16.0846 | 6.7295 | 132.1142 | 32.123 | 39.2933 | 0 | 42.1136 | 0 | 0.64648 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 448.9818 | 0.8424%
CZ 8 | 0.44094 | 0.16243 | 0.062354 | 1.5368 | 0.42706 | 0.24589 | 0 | 0.43418 | 0 | 0.0080646 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.6976 | 0.06096% | CZ 8 | 14.1533 | 5.2135 | 6.3627 | 88.837 | 13.7079 | 7.8926 | 0 | 13.9364 | 0 | 0.25886 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 197.6405 | 0.06096% | CZ 8 | 4.1481 | 1.528 | 0 | 9.1436 | 4.0175 | 2.3132 | 0 | 4.0845 | 0 | 0.075867 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 37.8893 | 0.06096% | CZ 8 | 0 | 0 | 0.063627 | 0.57639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.68362 | 0.06096% | CZ 8 | 43.4265 | 15.9965 | 6.9544 | 158.7236 | 42.0596 | 24.2168 | 0 | 42.7608 | 0 | 0.79425 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 471.3831 | 0.06096%
US Weighted | 0.44094 | 0.16367 | 0.05629 | 0.73425 | 0.12064 | 0.79807 | 0 | 0.41124 | 0 | 0.0034673 | 0 | 0.47033 | 0 | 0 | 0 | 0.9095 | 4.1084 | 100% | US Weighted | 14.1533 | 5.2533 | 5.7439 | 35.1462 | 3.8724 | 25.6162 | 0 | 13.1999 | 0 | 0.11129 | 0 | 15.0966 | 0 | 0 | 0 | 32.1817 | 150.3748 | 100% | US Weighted | 4.1481 | 1.5397 | 0 | 5.35 | 1.1349 | 7.5077 | 0 | 3.8687 | 0 | 0.032618 | 0 | 4.4246 | 0 | 0 | 0 | 8.154 | 36.1602 | 100% | US Weighted | 0 | 0 | 0.057439 | 0.16892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043604 | 0.26996 | 100% | US Weighted | 43.4265 | 16.1186 | 6.278 | 74.472 | 11.8816 | 78.5979 | 0 | 40.5011 | 0 | 0.34148 | 0 | 46.3207 | 0 | 0 | 0 | 90.1298 | 408.0678 | 100%
Building Type: | Outpatient Healthcare |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 40946 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 40946 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.16679 | 0.12546 | 0.0081779 | 0.14404 | 0 | 0.54672 | 0 | 0.19495 | 0 | 0.0015437 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2051 | 0% | CZ 0A | 5.3536 | 4.0271 | 0.83448 | 8.8559 | 0 | 17.5486 | 0 | 6.2575 | 0 | 0.049549 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 43.4872 | 0% | CZ 0A | 1.569 | 1.1803 | 0 | 0.78574 | 0 | 5.1432 | 0 | 1.834 | 0 | 0.014522 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 10.691 | 0% | CZ 0A | 0 | 0 | 0.0083448 | 0.06175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070094 | 0% | CZ 0A | 16.4263 | 12.3563 | 0.91209 | 14.9752 | 0 | 53.8441 | 0 | 19.1998 | 0 | 0.15203 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 119.5857 | 0%
CZ 0B | 0.16628 | 0.12483 | 0.0081779 | 0.24715 | 0 | 0.49911 | 0 | 0.19662 | 0 | 0.00083676 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2605 | 0% | CZ 0B | 5.3374 | 4.0067 | 0.83448 | 11.2702 | 0 | 16.0204 | 0 | 6.3112 | 0 | 0.026858 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 44.3678 | 0% | CZ 0B | 1.5643 | 1.1743 | 0 | 1.8761 | 0 | 4.6953 | 0 | 1.8497 | 0 | 0.0078717 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.3319 | 0% | CZ 0B | 0 | 0 | 0.0083448 | 0.048689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057034 | 0% | CZ 0B | 16.3766 | 12.2938 | 0.91209 | 24.9627 | 0 | 49.1553 | 0 | 19.3646 | 0 | 0.082409 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 124.8674 | 0%
CZ 1A | 0.16546 | 0.12468 | 0.0081779 | 0.15987 | 0 | 0.40928 | 0 | 0.18072 | 0 | 0.0012624 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.0669 | 1.601% | CZ 1A | 5.311 | 4.0019 | 0.83448 | 8.4321 | 0 | 13.1371 | 0 | 5.8007 | 0 | 0.040519 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 38.1182 | 1.601% | CZ 1A | 1.5566 | 1.1729 | 0 | 1.06 | 0 | 3.8503 | 0 | 1.7001 | 0 | 0.011875 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 9.516 | 1.601% | CZ 1A | 0 | 0 | 0.0083448 | 0.048152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056497 | 1.601% | CZ 1A | 16.2956 | 12.2789 | 0.91209 | 16.3605 | 0 | 40.3085 | 0 | 17.7981 | 0 | 0.12432 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 105.7979 | 1.601%
CZ 1B | 0.16559 | 0.1246 | 0.0079738 | 0.25895 | -0.00045445 | 0.43952 | 0 | 0.18587 | 0 | 0.00024526 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.1998 | 0% | CZ 1B | 5.3151 | 3.9993 | 0.81365 | 10.4272 | -0.014587 | 14.1077 | 0 | 5.966 | 0 | 0.0078722 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 41.1828 | 0% | CZ 1B | 1.5578 | 1.1721 | 0 | 2.1515 | -0.0042751 | 4.1347 | 0 | 1.7485 | 0 | 0.0023072 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 10.927 | 0% | CZ 1B | 0 | 0 | 0.0081365 | 0.030863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039 | 0% | CZ 1B | 16.3084 | 12.2711 | 0.88932 | 25.8972 | -0.044756 | 43.2865 | 0 | 18.3054 | 0 | 0.024154 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 118.6572 | 0%
CZ 2A | 0.1658 | 0.12441 | 0.0078377 | 0.24965 | -0.0058212 | 0.4404 | 0 | 0.18728 | 0 | 0.00016591 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.1872 | 15.85% | CZ 2A | 5.3219 | 3.9933 | 0.79976 | 10.3157 | -0.18685 | 14.1357 | 0 | 6.0114 | 0 | 0.0053253 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 40.9568 | 15.85% | CZ 2A | 1.5597 | 1.1704 | 0 | 2.0389 | -0.054762 | 4.1429 | 0 | 1.7618 | 0 | 0.0015608 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 10.7849 | 15.85% | CZ 2A | 0 | 0 | 0.0079976 | 0.03359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041588 | 15.85% | CZ 2A | 16.329 | 12.2526 | 0.87414 | 25.0166 | -0.57331 | 43.3725 | 0 | 18.4446 | 0 | 0.01634 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 117.4524 | 15.85%
CZ 2B | 0.16527 | 0.12451 | 0.0075972 | 0.3864 | 0.024381 | 0.33367 | 0 | 0.19618 | 0 | -3.6067e-05 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2554 | 2.601% | CZ 2B | 5.3047 | 3.9965 | 0.77523 | 13.1917 | 0.78259 | 10.7099 | 0 | 6.2971 | 0 | -0.0011577 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 41.6172 | 2.601% | CZ 2B | 1.5547 | 1.1713 | 0 | 3.5289 | 0.22936 | 3.1389 | 0 | 1.8456 | 0 | -0.0003393 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.6327 | 2.601% | CZ 2B | 0 | 0 | 0.0077523 | 0.011511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019264 | 2.601% | CZ 2B | 16.2764 | 12.2625 | 0.84732 | 38.2021 | 2.4012 | 32.8611 | 0 | 19.3213 | 0 | -0.0035521 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 123.8884 | 2.601%
CZ 3A | 0.16532 | 0.12418 | 0.0069779 | 0.43448 | 0.010373 | 0.36338 | 0 | 0.1654 | 0 | 0.001385 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.289 | 15.52% | CZ 3A | 5.3063 | 3.9859 | 0.71203 | 18.103 | 0.33295 | 11.6639 | 0 | 5.3089 | 0 | 0.044455 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 46.018 | 15.52% | CZ 3A | 1.5552 | 1.1682 | 0 | 3.5281 | 0.097582 | 3.4185 | 0 | 1.5559 | 0 | 0.013029 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.5009 | 15.52% | CZ 3A | 0 | 0 | 0.0071203 | 0.06065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06777 | 15.52% | CZ 3A | 16.2814 | 12.2299 | 0.77825 | 43.5651 | 1.0216 | 35.7881 | 0 | 16.2892 | 0 | 0.1364 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 127.8098 | 15.52%
CZ 3B | 0.16551 | 0.1248 | 0.0071322 | 0.40888 | 0.071096 | 0.25287 | 0 | 0.18176 | 0 | 0.00043281 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2299 | 5.112% | CZ 3B | 5.3124 | 4.0058 | 0.72777 | 14.5828 | 2.282 | 8.1165 | 0 | 5.834 | 0 | 0.013892 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 41.4357 | 5.112% | CZ 3B | 1.557 | 1.174 | 0 | 3.6503 | 0.66882 | 2.3788 | 0 | 1.7099 | 0 | 0.0040716 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.3071 | 5.112% | CZ 3B | 0 | 0 | 0.0072777 | 0.02128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028558 | 5.112% | CZ 3B | 16.2999 | 12.291 | 0.79546 | 40.5408 | 7.0019 | 24.9037 | 0 | 17.9004 | 0 | 0.042625 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 121.4956 | 5.112%
CZ 3C | 0.16563 | 0.12489 | 0.0065038 | 0.36976 | -0.0030441 | 0.31341 | 0 | 0.18526 | 0 | -7.2134e-05 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.1798 | 1.289% | CZ 3C | 5.3163 | 4.0086 | 0.66365 | 13.1737 | -0.097708 | 10.0598 | 0 | 5.9465 | 0 | -0.0023154 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 39.6291 | 1.289% | CZ 3C | 1.5581 | 1.1748 | 0 | 3.3028 | -0.028637 | 2.9484 | 0 | 1.7428 | 0 | -0.00067859 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 10.862 | 1.289% | CZ 3C | 0 | 0 | 0.0066365 | 0.019044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02568 | 1.289% | CZ 3C | 16.3119 | 12.2995 | 0.72537 | 36.659 | -0.2998 | 30.8663 | 0 | 18.2457 | 0 | -0.0071042 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 116.5208 | 1.289%
CZ 4A | 0.16631 | 0.12425 | 0.0063745 | 0.5717 | 0.01152 | 0.34114 | 0 | 0.15151 | 0 | 0.0013994 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.3917 | 18.12% | CZ 4A | 5.3383 | 3.9882 | 0.65046 | 22.6355 | 0.36976 | 10.9498 | 0 | 4.8632 | 0 | 0.044918 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 49.4007 | 18.12% | CZ 4A | 1.5646 | 1.1689 | 0 | 4.8018 | 0.10837 | 3.2092 | 0 | 1.4253 | 0 | 0.013165 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 12.4556 | 18.12% | CZ 4A | 0 | 0 | 0.0065046 | 0.062518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069023 | 18.12% | CZ 4A | 16.3794 | 12.237 | 0.71095 | 57.1032 | 1.1345 | 33.5971 | 0 | 14.9216 | 0 | 0.13782 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 137.9416 | 18.12%
CZ 4B | 0.16652 | 0.1246 | 0.0065514 | 0.50134 | 0.10959 | 0.19201 | 0 | 0.18977 | 0 | 0.00079348 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.3086 | 0.607% | CZ 4B | 5.345 | 3.9993 | 0.66851 | 18.385 | 3.5177 | 6.163 | 0 | 6.0912 | 0 | 0.025469 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 44.7558 | 0.607% | CZ 4B | 1.5665 | 1.1721 | 0 | 4.4079 | 1.031 | 1.8063 | 0 | 1.7852 | 0 | 0.0074645 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.9408 | 0.607% | CZ 4B | 0 | 0 | 0.0066851 | 0.033453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040139 | 0.607% | CZ 4B | 16.4 | 12.2711 | 0.73069 | 49.8024 | 10.7934 | 18.9099 | 0 | 18.6897 | 0 | 0.078146 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 129.3953 | 0.607%
CZ 4C | 0.16548 | 0.12355 | 0.0059979 | 0.56867 | -0.002164 | 0.17079 | 0 | 0.16199 | 0 | 0.00094496 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2127 | 2.878% | CZ 4C | 5.3117 | 3.9657 | 0.61203 | 21.762 | -0.069461 | 5.4818 | 0 | 5.1994 | 0 | 0.030331 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 42.8541 | 2.878% | CZ 4C | 1.5568 | 1.1623 | 0 | 4.8777 | -0.020358 | 1.6066 | 0 | 1.5238 | 0 | 0.0088896 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 10.88 | 2.878% | CZ 4C | 0 | 0 | 0.0061203 | 0.051194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057314 | 2.878% | CZ 4C | 16.2977 | 12.1681 | 0.66895 | 56.6597 | -0.21313 | 16.8199 | 0 | 15.9532 | 0 | 0.093065 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 120.1674 | 2.878%
CZ 5A | 0.16637 | 0.12404 | 0.0059276 | 0.61891 | 0.023364 | 0.14695 | 0 | 0.15248 | 0 | 0.0012624 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2568 | 23.41% | CZ 5A | 5.3401 | 3.9815 | 0.60486 | 24.98 | 0.74994 | 4.7166 | 0 | 4.8944 | 0 | 0.040519 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 45.8686 | 23.41% | CZ 5A | 1.5651 | 1.1669 | 0 | 5.1344 | 0.2198 | 1.3824 | 0 | 1.4345 | 0 | 0.011875 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.0793 | 23.41% | CZ 5A | 0 | 0 | 0.0060486 | 0.074613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080661 | 23.41% | CZ 5A | 16.3851 | 12.2164 | 0.66111 | 61.9076 | 2.301 | 14.4719 | 0 | 15.0175 | 0 | 0.12432 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 124.805 | 23.41%
CZ 5B | 0.16658 | 0.12435 | 0.0059662 | 0.55647 | 0.11816 | 0.13934 | 0 | 0.17187 | 0 | 0.0011253 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.3013 | 5.921% | CZ 5B | 5.3469 | 3.9912 | 0.60879 | 20.9323 | 3.7928 | 4.4726 | 0 | 5.5166 | 0 | 0.03612 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 45.2578 | 5.921% | CZ 5B | 1.5671 | 1.1698 | 0 | 4.8219 | 1.1116 | 1.3108 | 0 | 1.6168 | 0 | 0.010586 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.7728 | 5.921% | CZ 5B | 0 | 0 | 0.0060879 | 0.044801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050889 | 5.921% | CZ 5B | 16.4057 | 12.2462 | 0.66541 | 55.3769 | 11.6374 | 13.7232 | 0 | 16.9264 | 0 | 0.11083 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 128.812 | 5.921%
CZ 5C | 0.16589 | 0.12347 | 0.0059525 | 0.50679 | -0.021691 | 0.10175 | 0 | 0.15134 | 0 | 0.00033182 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.0513 | 0.1093% | CZ 5C | 5.3249 | 3.963 | 0.6074 | 17.7724 | -0.69623 | 3.266 | 0 | 4.8576 | 0 | 0.010651 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 35.6663 | 0.1093% | CZ 5C | 1.5606 | 1.1615 | 0 | 4.565 | -0.20405 | 0.95722 | 0 | 1.4237 | 0 | 0.0031215 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 9.6314 | 0.1093% | CZ 5C | 0 | 0 | 0.006074 | 0.021965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028039 | 0.1093% | CZ 5C | 16.3382 | 12.1595 | 0.66389 | 50.1921 | -2.1362 | 10.0212 | 0 | 14.9046 | 0 | 0.032679 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 103.8959 | 0.1093%
CZ 6A | 0.16633 | 0.12396 | 0.0058754 | 0.74908 | 0.082067 | 0.16247 | 0 | 0.1734 | 0 | 0.0013273 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.482 | 5.29% | CZ 6A | 5.3388 | 3.9787 | 0.59953 | 32.7889 | 2.6342 | 5.2149 | 0 | 5.5659 | 0 | 0.042603 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 56.724 | 5.29% | CZ 6A | 1.5647 | 1.1661 | 0 | 5.8706 | 0.77204 | 1.5284 | 0 | 1.6313 | 0 | 0.012486 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 12.7099 | 5.29% | CZ 6A | 0 | 0 | 0.0059953 | 0.12758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13358 | 5.29% | CZ 6A | 16.3808 | 12.2078 | 0.65529 | 75.4045 | 8.0824 | 16.0008 | 0 | 17.0778 | 0 | 0.13072 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 147.6601 | 5.29%
CZ 6B | 0.1662 | 0.1235 | 0.0058936 | 0.73613 | 0.14056 | 0.14287 | 0 | 0.1855 | 0 | 0.0011686 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.5193 | 0.7888% | CZ 6B | 5.3346 | 3.9641 | 0.60138 | 31.3674 | 4.5117 | 4.5858 | 0 | 5.9542 | 0 | 0.037509 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 56.9172 | 0.7888% | CZ 6B | 1.5635 | 1.1618 | 0 | 5.8841 | 1.3223 | 1.344 | 0 | 1.7451 | 0 | 0.010993 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 13.1961 | 0.7888% | CZ 6B | 0 | 0 | 0.0060138 | 0.11291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11892 | 0.7888% | CZ 6B | 16.3681 | 12.1631 | 0.65731 | 73.9418 | 13.8432 | 14.0706 | 0 | 18.2691 | 0 | 0.11509 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 151.1482 | 0.7888%
CZ 7 | 0.16624 | 0.1234 | 0.00588 | 0.80806 | 0.096307 | 0.14862 | 0 | 0.17842 | 0 | 0.0011758 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.5456 | 0.8424% | CZ 7 | 5.336 | 3.9609 | 0.6 | 34.5583 | 3.0912 | 4.7703 | 0 | 5.727 | 0 | 0.03774 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 58.6421 | 0.8424% | CZ 7 | 1.5639 | 1.1609 | 0 | 6.4422 | 0.90599 | 1.3981 | 0 | 1.6785 | 0 | 0.011061 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 13.3249 | 0.8424% | CZ 7 | 0 | 0 | 0.006 | 0.12578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13178 | 0.8424% | CZ 7 | 16.3723 | 12.1531 | 0.6558 | 81.1903 | 9.4848 | 14.6368 | 0 | 17.5722 | 0 | 0.1158 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 153.9011 | 0.8424%
CZ 8 | 0.16403 | 0.11979 | 0.0058482 | 0.89843 | 0.10848 | 0.10157 | 0 | 0.18106 | 0 | 0.0011109 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.5978 | 0.06096% | CZ 8 | 5.2651 | 3.8451 | 0.59675 | 38.8723 | 3.4818 | 3.26 | 0 | 5.8118 | 0 | 0.035657 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 61.7291 | 0.06096% | CZ 8 | 1.5431 | 1.1269 | 0 | 7.1022 | 1.0205 | 0.95546 | 0 | 1.7033 | 0 | 0.01045 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 13.6263 | 0.06096% | CZ 8 | 0 | 0 | 0.0059675 | 0.14639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15236 | 0.06096% | CZ 8 | 16.1549 | 11.7979 | 0.65225 | 90.3541 | 10.6833 | 10.0027 | 0 | 17.8322 | 0 | 0.1094 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 159.3067 | 0.06096%
US Weighted | 0.16599 | 0.12422 | 0.0066274 | 0.49946 | 0.026377 | 0.28008 | 0 | 0.16658 | 0 | 0.0010198 | 0 | 0.0091971 | 0 | 0 | 0 | 0.0082666 | 1.2878 | 100% | US Weighted | 5.3279 | 3.9872 | 0.67626 | 20.0811 | 0.84665 | 8.9899 | 0 | 5.347 | 0 | 0.032734 | 0 | 0.29521 | 0 | 0 | 0 | 0.26534 | 45.8493 | 100% | US Weighted | 1.5615 | 1.1686 | 0 | 4.154 | 0.24814 | 2.6348 | 0 | 1.5671 | 0 | 0.0095938 | 0 | 0.086521 | 0 | 0 | 0 | 0.077767 | 11.508 | 100% | US Weighted | 0 | 0 | 0.0067626 | 0.059078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065841 | 100% | US Weighted | 16.3477 | 12.234 | 0.73916 | 49.945 | 2.5978 | 27.5835 | 0 | 16.4061 | 0 | 0.10044 | 0 | 0.90578 | 0 | 0 | 0 | 0.81414 | 127.6735 | 100%
Building Type: | Outpatient Healthcare |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Outpatient Healthcare |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Outpatient Healthcare |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 40946 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 40946 | [17 empty] | Prototype Floor Area: | 40946 | Building Type: | Outpatient Healthcare | [15 empty] | Prototype Floor Area: | 40946 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 37.83% | 76.53% | 14.96% | 50.4% |  | 27.1% |  | 41.5% |  | 47.66% |  | 1.955% |  |  |  | 0.9089% | 25.03% | 0% | CZ 0A | 37.83% | 76.53% | 14.96% | 50.89% |  | 27.1% |  | 41.5% |  | 47.66% |  | 1.955% |  |  |  | 0.8245% | 25.64% | 0% | CZ 0A | 37.83% | 76.53% |  | 49.66% |  | 27.1% |  | 41.5% |  | 47.66% |  | 1.955% |  |  |  | 0.9537% | 24.7% | 0% | CZ 0A |  |  | 14.96% | 51.45% | [11 empty] | 0% | 31.95% | 0% | CZ 0A | 37.83% | 76.53% | 14.96% | 50.45% |  | 27.1% |  | 41.5% |  | 47.66% |  | 1.955% |  |  |  | 0.9033% | 25.07% | 0%
CZ 0B | 37.71% | 76.13% | 14.96% | 60.22% | 0% | 28.01% |  | 43.29% |  | 31.18% |  | 1.955% |  |  |  | 0.9089% | 26.88% | 0% | CZ 0B | 37.71% | 76.13% | 14.96% | 53.68% | 0% | 28.01% |  | 43.29% |  | 31.18% |  | 1.955% |  |  |  | 0.8245% | 26.87% | 0% | CZ 0B | 37.71% | 76.13% |  | 66.81% | 0% | 28.01% |  | 43.29% |  | 31.18% |  | 1.955% |  |  |  | 0.9537% | 26.89% | 0% | CZ 0B |  |  | 14.96% | 42.65% | [11 empty] | 0% | 26.71% | 0% | CZ 0B | 37.71% | 76.13% | 14.96% | 59.61% | 0% | 28.01% |  | 43.29% |  | 31.18% |  | 1.955% |  |  |  | 0.9033% | 26.88% | 0%
CZ 1A | 37.52% | 76.03% | 14.96% | 50.03% |  | 27.43% |  | 41.68% |  | 40.14% |  | 1.955% |  |  |  | 0.9089% | 24.88% | 1.601% | CZ 1A | 37.52% | 76.03% | 14.96% | 47.28% |  | 27.43% |  | 41.68% |  | 40.14% |  | 1.955% |  |  |  | 0.8245% | 25.07% | 1.601% | CZ 1A | 37.52% | 76.03% |  | 53.35% |  | 27.43% |  | 41.68% |  | 40.14% |  | 1.955% |  |  |  | 0.9537% | 24.78% | 1.601% | CZ 1A |  |  | 14.96% | 43.56% | [11 empty] | 0% | 26.91% | 1.601% | CZ 1A | 37.52% | 76.03% | 14.96% | 49.75% |  | 27.43% |  | 41.68% |  | 40.14% |  | 1.955% |  |  |  | 0.9033% | 24.9% | 1.601%
CZ 1B | 37.55% | 76.08% | 14.59% | 62.85% | -150% | 28.67% |  | 42.71% |  | 13.18% |  | 1.955% |  |  |  | 0.9089% | 27.13% | 0% | CZ 1B | 37.55% | 76.08% | 14.59% | 53.4% | -150% | 28.67% |  | 42.71% |  | 13.18% |  | 1.955% |  |  |  | 0.8245% | 26.56% | 0% | CZ 1B | 37.55% | 76.08% |  | 71.05% | -150% | 28.67% |  | 42.71% |  | 13.18% |  | 1.955% |  |  |  | 0.9537% | 27.43% | 0% | CZ 1B |  |  | 14.59% | 33.56% | [11 empty] | 0% | 20.38% | 0% | CZ 1B | 37.55% | 76.08% | 14.59% | 62.03% | -150% | 28.67% |  | 42.71% |  | 13.18% |  | 1.955% |  |  |  | 0.9033% | 27.1% | 0%
CZ 2A | 37.6% | 75.98% | 14.34% | 54.92% | -65.93% | 31.4% |  | 43.97% |  | 8.364% |  | 1.955% |  |  |  | 0.9089% | 27.4% | 15.85% | CZ 2A | 37.6% | 75.98% | 14.34% | 48.14% | -65.93% | 31.4% |  | 43.97% |  | 8.364% |  | 1.955% |  |  |  | 0.8245% | 26.82% | 15.85% | CZ 2A | 37.6% | 75.98% |  | 60.74% | -65.93% | 31.4% |  | 43.97% |  | 8.364% |  | 1.955% |  |  |  | 0.9537% | 27.71% | 15.85% | CZ 2A |  |  | 14.34% | 33.67% | [11 empty] | 0% | 20.88% | 15.85% | CZ 2A | 37.6% | 75.98% | 14.34% | 54.33% | -65.93% | 31.4% |  | 43.97% |  | 8.364% |  | 1.955% |  |  |  | 0.9033% | 27.36% | 15.85%
CZ 2B | 37.48% | 75.99% | 13.9% | 72.97% | 16.82% | 32.91% |  | 43.91% |  | -2.347% |  | 1.955% |  |  |  | 0.9089% | 30.06% | 2.601% | CZ 2B | 37.48% | 75.99% | 13.9% | 61.13% | 16.82% | 32.91% |  | 43.91% |  | -2.347% |  | 1.955% |  |  |  | 0.8245% | 28.62% | 2.601% | CZ 2B | 37.48% | 75.99% |  | 80.83% | 16.82% | 32.91% |  | 43.91% |  | -2.347% |  | 1.955% |  |  |  | 0.9537% | 30.81% | 2.601% | CZ 2B |  |  | 13.9% | 17.23% | [11 empty] | 0% | 11.59% | 2.601% | CZ 2B | 37.48% | 75.99% | 13.9% | 72.07% | 16.82% | 32.91% |  | 43.91% |  | -2.347% |  | 1.955% |  |  |  | 0.9033% | 29.97% | 2.601%
CZ 3A | 37.49% | 75.8% | 12.61% | 70.75% | 13.13% | 37.59% |  | 40.85% |  | 46.38% |  | 1.955% |  |  |  | 0.9089% | 31.38% | 15.52% | CZ 3A | 37.49% | 75.8% | 12.61% | 63.57% | 13.13% | 37.59% |  | 40.85% |  | 46.38% |  | 1.955% |  |  |  | 0.8245% | 31.2% | 15.52% | CZ 3A | 37.49% | 75.8% |  | 76.74% | 13.13% | 37.59% |  | 40.85% |  | 46.38% |  | 1.955% |  |  |  | 0.9537% | 31.47% | 15.52% | CZ 3A |  |  | 12.61% | 47.42% | [11 empty] | 0% | 29.73% | 15.52% | CZ 3A | 37.49% | 75.8% | 12.61% | 70.14% | 13.13% | 37.59% |  | 40.85% |  | 46.38% |  | 1.955% |  |  |  | 0.9033% | 31.37% | 15.52%
CZ 3B | 37.53% | 76.19% | 12.96% | 74.43% | 40.47% | 32.54% |  | 42.36% |  | 21.13% |  | 1.955% |  |  |  | 0.9089% | 30.96% | 5.112% | CZ 3B | 37.53% | 76.19% | 12.96% | 62.96% | 40.47% | 32.54% |  | 42.36% |  | 21.13% |  | 1.955% |  |  |  | 0.8245% | 29.62% | 5.112% | CZ 3B | 37.53% | 76.19% |  | 82.5% | 40.47% | 32.54% |  | 42.36% |  | 21.13% |  | 1.955% |  |  |  | 0.9537% | 31.66% | 5.112% | CZ 3B |  |  | 12.96% | 26.39% | [11 empty] | 0% | 15.83% | 5.112% | CZ 3B | 37.53% | 76.19% | 12.96% | 73.53% | 40.47% | 32.54% |  | 42.36% |  | 21.13% |  | 1.955% |  |  |  | 0.9033% | 30.87% | 5.112%
CZ 3C | 37.56% | 76.25% | 11.87% | 70.23% | -12.88% | 40.15% |  | 44.37% |  | -4.032% |  | 1.955% |  |  |  | 0.9089% | 31.13% | 1.289% | CZ 3C | 37.56% | 76.25% | 11.87% | 57.46% | -12.88% | 40.15% |  | 44.37% |  | -4.032% |  | 1.955% |  |  |  | 0.8245% | 29.47% | 1.289% | CZ 3C | 37.56% | 76.25% |  | 79.74% | -12.88% | 40.15% |  | 44.37% |  | -4.032% |  | 1.955% |  |  |  | 0.9537% | 32.02% | 1.289% | CZ 3C |  |  | 11.87% | 21.66% | [11 empty] | 0% | 13.7% | 1.289% | CZ 3C | 37.56% | 76.25% | 11.87% | 69.2% | -12.88% | 40.15% |  | 44.37% |  | -4.032% |  | 1.955% |  |  |  | 0.9033% | 31.02% | 1.289%
CZ 4A | 37.72% | 75.96% | 11.31% | 70.47% | 9.362% | 43.45% |  | 37.99% |  | 35.21% |  | 1.955% |  |  |  | 0.9089% | 33.43% | 18.12% | CZ 4A | 37.72% | 75.96% | 11.31% | 59.29% | 9.362% | 43.45% |  | 37.99% |  | 35.21% |  | 1.955% |  |  |  | 0.8245% | 32.35% | 18.12% | CZ 4A | 37.72% | 75.96% |  | 80.03% | 9.362% | 43.45% |  | 37.99% |  | 35.21% |  | 1.955% |  |  |  | 0.9537% | 34.03% | 18.12% | CZ 4A |  |  | 11.31% | 35.31% | [11 empty] | 0% | 24.81% | 18.12% | CZ 4A | 37.72% | 75.96% | 11.31% | 69.5% | 9.362% | 43.45% |  | 37.99% |  | 35.21% |  | 1.955% |  |  |  | 0.9033% | 33.36% | 18.12%
CZ 4B | 37.77% | 76.12% | 11.7% | 76.9% | 44.67% | 32.51% |  | 42.34% |  | 29.89% |  | 1.955% |  |  |  | 0.9089% | 32.89% | 0.607% | CZ 4B | 37.77% | 76.12% | 11.7% | 64.68% | 44.67% | 32.51% |  | 42.34% |  | 29.89% |  | 1.955% |  |  |  | 0.8245% | 31.49% | 0.607% | CZ 4B | 37.77% | 76.12% |  | 86.03% | 44.67% | 32.51% |  | 42.34% |  | 29.89% |  | 1.955% |  |  |  | 0.9537% | 33.64% | 0.607% | CZ 4B |  |  | 11.7% | 30.57% | [11 empty] | 0% | 19.1% | 0.607% | CZ 4B | 37.77% | 76.12% | 11.7% | 75.91% | 44.67% | 32.51% |  | 42.34% |  | 29.89% |  | 1.955% |  |  |  | 0.9033% | 32.79% | 0.607%
CZ 4C | 37.53% | 75.62% | 10.61% | 74.65% | -6.625% | 39.21% |  | 40.22% |  | 28.17% |  | 1.955% |  |  |  | 0.9089% | 32.98% | 2.878% | CZ 4C | 37.53% | 75.62% | 10.61% | 63.01% | -6.625% | 39.21% |  | 40.22% |  | 28.17% |  | 1.955% |  |  |  | 0.8245% | 31.73% | 2.878% | CZ 4C | 37.53% | 75.62% |  | 83.96% | -6.625% | 39.21% |  | 40.22% |  | 28.17% |  | 1.955% |  |  |  | 0.9537% | 33.69% | 2.878% | CZ 4C |  |  | 10.61% | 34.79% | [11 empty] | 0% | 23.07% | 2.878% | CZ 4C | 37.53% | 75.62% | 10.61% | 73.68% | -6.625% | 39.21% |  | 40.22% |  | 28.17% |  | 1.955% |  |  |  | 0.9033% | 32.9% | 2.878%
CZ 5A | 37.73% | 75.81% | 10.29% | 67.49% | 14.99% | 31.77% |  | 38.55% |  | 28.46% |  | 1.955% |  |  |  | 0.9089% | 31.6% | 23.41% | CZ 5A | 37.73% | 75.81% | 10.29% | 55.12% | 14.99% | 31.77% |  | 38.55% |  | 28.46% |  | 1.955% |  |  |  | 0.8245% | 30.46% | 23.41% | CZ 5A | 37.73% | 75.81% |  | 79.11% | 14.99% | 31.77% |  | 38.55% |  | 28.46% |  | 1.955% |  |  |  | 0.9537% | 32.27% | 23.41% | CZ 5A |  |  | 10.29% | 32.19% | [11 empty] | 0% | 24.14% | 23.41% | CZ 5A | 37.73% | 75.81% | 10.29% | 66.37% | 14.99% | 31.77% |  | 38.55% |  | 28.46% |  | 1.955% |  |  |  | 0.9033% | 31.52% | 23.41%
CZ 5B | 37.78% | 76% | 10.44% | 74.61% | 49.98% | 30.65% |  | 39.2% |  | 35.62% |  | 1.955% |  |  |  | 0.9089% | 33.2% | 5.921% | CZ 5B | 37.78% | 76% | 10.44% | 62.34% | 49.98% | 30.65% |  | 39.2% |  | 35.62% |  | 1.955% |  |  |  | 0.8245% | 31.77% | 5.921% | CZ 5B | 37.78% | 76% |  | 84.29% | 49.98% | 30.65% |  | 39.2% |  | 35.62% |  | 1.955% |  |  |  | 0.9537% | 33.98% | 5.921% | CZ 5B |  |  | 10.44% | 31.87% | [11 empty] | 0% | 20.99% | 5.921% | CZ 5B | 37.78% | 76% | 10.44% | 73.59% | 49.98% | 30.65% |  | 39.2% |  | 35.62% |  | 1.955% |  |  |  | 0.9033% | 33.1% | 5.921%
CZ 5C | 37.62% | 75.58% | 10.36% | 73.08% | -190.3% | 33.07% |  | 37.77% |  | 11.92% |  | 1.955% |  |  |  | 0.9089% | 30.41% | 0.1093% | CZ 5C | 37.62% | 75.58% | 10.36% | 58.73% | -190.3% | 33.07% |  | 37.77% |  | 11.92% |  | 1.955% |  |  |  | 0.8245% | 28.31% | 0.1093% | CZ 5C | 37.62% | 75.58% |  | 83.8% | -190.3% | 33.07% |  | 37.77% |  | 11.92% |  | 1.955% |  |  |  | 0.9537% | 31.57% | 0.1093% | CZ 5C |  |  | 10.36% | 18.81% | [11 empty] | 0% | 12.81% | 0.1093% | CZ 5C | 37.62% | 75.58% | 10.36% | 71.92% | -190.3% | 33.07% |  | 37.77% |  | 11.92% |  | 1.955% |  |  |  | 0.9033% | 30.26% | 0.1093%
CZ 6A | 37.72% | 75.79% | 9.992% | 65.26% | 32.75% | 34.02% |  | 41.48% |  | 22.69% |  | 1.955% |  |  |  | 0.9089% | 34.12% | 5.29% | CZ 6A | 37.72% | 75.79% | 9.992% | 53.76% | 32.75% | 34.02% |  | 41.48% |  | 22.69% |  | 1.955% |  |  |  | 0.8245% | 33.24% | 5.29% | CZ 6A | 37.72% | 75.79% |  | 77.74% | 32.75% | 34.02% |  | 41.48% |  | 22.69% |  | 1.955% |  |  |  | 0.9537% | 34.67% | 5.29% | CZ 6A |  |  | 9.992% | 36.22% | [11 empty] | 0% | 29.31% | 5.29% | CZ 6A | 37.72% | 75.79% | 9.992% | 64.14% | 32.75% | 34.02% |  | 41.48% |  | 22.69% |  | 1.955% |  |  |  | 0.9033% | 34.06% | 5.29%
CZ 6B | 37.69% | 75.57% | 10.08% | 71.38% | 45.53% | 37.73% |  | 42.23% |  | 22.98% |  | 1.955% |  |  |  | 0.9089% | 36.12% | 0.7888% | CZ 6B | 37.69% | 75.57% | 10.08% | 59.92% | 45.53% | 37.73% |  | 42.23% |  | 22.98% |  | 1.955% |  |  |  | 0.8245% | 35.28% | 0.7888% | CZ 6B | 37.69% | 75.57% |  | 82.72% | 45.53% | 37.73% |  | 42.23% |  | 22.98% |  | 1.955% |  |  |  | 0.9537% | 36.63% | 0.7888% | CZ 6B |  |  | 10.08% | 40.22% | [11 empty] | 0% | 30.97% | 0.7888% | CZ 6B | 37.69% | 75.57% | 10.08% | 70.32% | 45.53% | 37.73% |  | 42.23% |  | 22.98% |  | 1.955% |  |  |  | 0.9033% | 36.06% | 0.7888%
CZ 7 | 37.7% | 75.56% | 9.745% | 62.84% | 29.53% | 37.25% |  | 41.73% |  | 17.91% |  | 1.955% |  |  |  | 0.9089% | 34.42% | 0.8424% | CZ 7 | 37.7% | 75.56% | 9.745% | 48.98% | 29.53% | 37.25% |  | 41.73% |  | 17.91% |  | 1.955% |  |  |  | 0.8245% | 32.47% | 0.8424% | CZ 7 | 37.7% | 75.56% |  | 78.96% | 29.53% | 37.25% |  | 41.73% |  | 17.91% |  | 1.955% |  |  |  | 0.9537% | 35.7% | 0.8424% | CZ 7 |  |  | 9.745% | 29.44% | [11 empty] | 0% | 24.75% | 0.8424% | CZ 7 | 37.7% | 75.56% | 9.745% | 61.45% | 29.53% | 37.25% |  | 41.73% |  | 17.91% |  | 1.955% |  |  |  | 0.9033% | 34.28% | 0.8424%
CZ 8 | 37.2% | 73.75% | 9.379% | 58.46% | 25.4% | 41.3% |  | 41.7% |  | 13.77% |  | 1.955% |  |  |  | 0.9089% | 34.01% | 0.06096% | CZ 8 | 37.2% | 73.75% | 9.379% | 43.76% | 25.4% | 41.3% |  | 41.7% |  | 13.77% |  | 1.955% |  |  |  | 0.8245% | 31.23% | 0.06096% | CZ 8 | 37.2% | 73.75% |  | 77.67% | 25.4% | 41.3% |  | 41.7% |  | 13.77% |  | 1.955% |  |  |  | 0.9537% | 35.96% | 0.06096% | CZ 8 |  |  | 9.379% | 25.4% | [11 empty] | 0% | 22.29% | 0.06096% | CZ 8 | 37.2% | 73.75% | 9.379% | 56.93% | 25.4% | 41.3% |  | 41.7% |  | 13.77% |  | 1.955% |  |  |  | 0.9033% | 33.8% | 0.06096%
US Weighted | 37.64% | 75.9% | 11.81% | 67.35% | 4.321% | 35.21% | 0% | 40.45% | 0% | 27.83% | 0% | 1.955% | 0% | 0% | 0% | 0.9089% | 31.38% | 100% | US Weighted | 37.64% | 75.9% | 11.81% | 57.17% | 4.321% | 35.21% | 0% | 40.45% | 0% | 27.83% | 0% | 1.955% | 0% | 0% | 0% | 0.8245% | 30.47% | 100% | US Weighted | 37.64% | 75.9% | 0% | 76.26% | 4.321% | 35.21% | 0% | 40.45% | 0% | 27.83% | 0% | 1.955% | 0% | 0% | 0% | 0.9537% | 31.89% | 100% | US Weighted | 0% | 0% | 11.81% | 34.99% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 23.84% | 100% | US Weighted | 37.64% | 75.9% | 11.81% | 66.47% | 4.321% | 35.21% | 0% | 40.45% | 0% | 27.83% | 0% | 1.955% | 0% | 0% | 0% | 0.9033% | 31.32% | 100%

## MedHos
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Hospital |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 241501 |  | Building Type: | Hospital |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 |  | Building Type: | Hospital |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Hospital |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Hospital | [14 empty] | Prototype Floor Area: | 241501 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.40087 | 0.018951 | 0.049217 | 0.10909 | 0.092557 | 0.34032 | 0.031314 | 0.35447 | 0.020866 | 0.045344 | 0.017611 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.7423 |  | STD2019 | 12.8669 | 0.60829 | 4.7963 | 10.1423 | 2.9709 | 10.9237 | 1.0051 | 11.3778 | 0.66975 | 1.4554 | 0.56526 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 105.3915 |  | STD2019 | 3.7711 | 0.17828 | 0.030374 | 0.13307 | 0.87072 | 3.2015 | 0.29458 | 3.3347 | 0.19629 | 0.42656 | 0.16567 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 23.4622 |  | STD2019 | 0 | 0 | 0.046927 | 0.096883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.25339 |  | STD2019 | 39.4794 | 1.8664 | 5.4471 | 11.9824 | 9.1155 | 33.517 | 3.084 | 34.9105 | 2.055 | 4.4657 | 1.7344 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 273.3206
STD2016 | 0.41562 | 0.018951 | 0.049212 | 0.25392 | 0.095501 | 0.29975 | 0.034393 | 0.35574 | 0.022002 | 0.058956 | 0.026377 | 0.30666 | 0.008691 | 0.27812 | 0 | 0.66831 | 2.8922 |  | STD2016 | 13.3404 | 0.60829 | 4.7958 | 24.91 | 3.0654 | 9.6213 | 1.104 | 11.4184 | 0.70621 | 1.8924 | 0.84664 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 120.3198 |  | STD2016 | 3.9098 | 0.17828 | 0.030374 | 0.13458 | 0.89841 | 2.8199 | 0.32355 | 3.3465 | 0.20698 | 0.55462 | 0.24814 | 2.8848 | 0.08176 | 1.6061 | 0 | 6.287 | 23.5109 |  | STD2016 | 0 | 0 | 0.046922 | 0.24451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40101 |  | STD2016 | 40.9322 | 1.8664 | 5.4466 | 28.1337 | 9.4054 | 29.5211 | 3.3872 | 35.0349 | 2.1668 | 5.8063 | 2.5977 | 30.2012 | 0.85594 | 28.7914 | 0 | 65.8187 | 289.9656
STD2013 | 0.42419 | 0.025952 | 0.050961 | 0.25448 | 0.096107 | 0.30176 | 0.034464 | 0.35742 | 0.027714 | 0.066849 | 0.026374 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.932 |  | STD2013 | 13.6155 | 0.83301 | 4.9742 | 24.9616 | 3.0848 | 9.686 | 1.1062 | 11.4725 | 0.88956 | 2.1457 | 0.84654 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 121.7524 |  | STD2013 | 3.9905 | 0.24414 | 0.030374 | 0.1353 | 0.90411 | 2.8388 | 0.32422 | 3.3624 | 0.26072 | 0.62887 | 0.24811 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.8641 |  | STD2013 | 0 | 0 | 0.048706 | 0.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40328 |  | STD2013 | 41.7761 | 2.5559 | 5.6416 | 28.1949 | 9.4652 | 29.7193 | 3.3942 | 35.2008 | 2.7294 | 6.5836 | 2.5974 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 293.9117
STD2010 | 0.43859 | 0.025952 | 0.050961 | 0.32757 | 0.16688 | 0.31666 | 0.037045 | 0.36452 | 0.022874 | 0.07887 | 0.03342 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.132 |  | STD2010 | 14.0778 | 0.83301 | 4.9743 | 28.322 | 5.3565 | 10.164 | 1.1891 | 11.7002 | 0.7342 | 2.5316 | 1.0727 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 129.1862 |  | STD2010 | 4.126 | 0.24414 | 0.030374 | 0.68644 | 1.5699 | 2.9789 | 0.34849 | 3.4291 | 0.21518 | 0.74196 | 0.3144 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 25.609 |  | STD2010 | 0 | 0 | 0.048707 | 0.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41808 |  | STD2010 | 43.1947 | 2.5559 | 5.6416 | 35.5823 | 16.4353 | 31.1861 | 3.6484 | 35.8997 | 2.2527 | 7.7676 | 3.2914 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 313.7972
STD2007 | 0.51158 | 0.031966 | 0.05144 | 0.58097 | 0.20535 | 0.49352 | 0.089247 | 0.52758 | 0 | 0.15279 | 0.033431 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9775 |  | STD2007 | 16.4205 | 1.026 | 5.0042 | 51.688 | 6.5912 | 15.8408 | 2.8646 | 16.9342 | 0 | 4.9041 | 1.0731 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 171.5735 |  | STD2007 | 4.8126 | 0.30071 | 0.032918 | 1.0214 | 1.9318 | 4.6427 | 0.83958 | 4.9631 | 0 | 1.4373 | 0.3145 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.5126 |  | STD2007 | 0 | 0 | 0.048919 | 0.48203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64052 |  | STD2007 | 50.3828 | 3.1481 | 5.6915 | 63.379 | 20.2238 | 48.6041 | 8.7895 | 51.9591 | 0 | 15.0471 | 3.2925 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 399.915
STD2004 | 0.51158 | 0.031966 | 0.051436 | 0.55488 | 0.20542 | 0.49096 | 0.08713 | 0.54439 | 0 | 0.1493 | 0.033431 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9602 |  | STD2004 | 16.4205 | 1.026 | 5.0038 | 49.0222 | 6.5935 | 15.7588 | 2.7967 | 17.4738 | 0 | 4.7924 | 1.0731 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 169.1875 |  | STD2004 | 4.8126 | 0.30071 | 0.032918 | 1.022 | 1.9324 | 4.6186 | 0.81966 | 5.1213 | 0 | 1.4046 | 0.3145 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.5953 |  | STD2004 | 0 | 0 | 0.048915 | 0.45535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.61384 |  | STD2004 | 50.3828 | 3.1481 | 5.6911 | 60.4693 | 20.2308 | 48.3525 | 8.581 | 53.6148 | 0 | 14.7043 | 3.2925 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 397.8647
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | -3.8178e-06 | -0.026081 | 7.1043e-05 | -0.002555 | -0.0021171 | 0.016812 | 0 | -0.003481 | 5.0966e-08 | 0 | 0 | 0 | 0 | 0 | -0.017355 |  | 2004-2007 | 0 | 0 | -0.00038957 | -2.6658 | 0.0022803 | -0.082011 | -0.067954 | 0.53963 | 0 | -0.11173 | 1.6359e-06 | 0 | 0 | 0 | 0 | 0 | -2.3859 |  | 2004-2007 | 0 | 0 | 0 | 0.00059305 | 0.00066832 | -0.024036 | -0.019916 | 0.15816 | 0 | -0.032747 | 4.7946e-07 | 0 | 0 | 0 | 0 | 0 | 0.082719 |  | 2004-2007 | 0 | 0 | -3.8957e-06 | -0.026678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.026682 |  | 2004-2007 | 0 | 0 | -0.0004258 | -2.9097 | 0.0069967 | -0.25163 | -0.2085 | 1.6557 | 0 | -0.34283 | 5.0194e-06 | 0 | 0 | 0 | 0 | 0 | -2.0503
2007-2010 | 0.072987 | 0.0060134 | 0.00047848 | 0.25339 | 0.038467 | 0.17686 | 0.052202 | 0.16306 | -0.022874 | 0.073915 | 1.0696e-05 | 0.0033596 | 0.0085355 | 0 | 0 | 0.019135 | 0.84555 |  | 2007-2010 | 2.3427 | 0.19302 | 0.029914 | 23.366 | 1.2347 | 5.6768 | 1.6756 | 5.234 | -0.7342 | 2.3725 | 0.00034332 | 0.10784 | 0.27397 | 0 | 0 | 0.61421 | 42.3873 |  | 2007-2010 | 0.68661 | 0.05657 | 0.0025435 | 0.33498 | 0.36187 | 1.6638 | 0.49109 | 1.534 | -0.21518 | 0.69535 | 0.00010062 | 0.031605 | 0.080296 | 0 | 0 | 0.18001 | 5.9036 |  | 2007-2010 | 0 | 0 | 0.00021236 | 0.22223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22244 |  | 2007-2010 | 7.1882 | 0.59223 | 0.049838 | 27.7967 | 3.7884 | 17.418 | 5.1412 | 16.0593 | -2.2527 | 7.2796 | 0.0010534 | 0.33088 | 0.84062 | 0 | 0 | 1.8846 | 86.1178
2010-2013 | 0.014403 | 0 | 7.8415e-07 | 0.073089 | 0.070774 | 0.014893 | 0.0025804 | 0.0070965 | -0.0048402 | 0.012022 | 0.0070466 | 0.00066899 | 8.3165e-05 | 0 | 0 | 0.0021745 | 0.19999 |  | 2010-2013 | 0.46231 | 0 | 8.0016e-05 | 3.3604 | 2.2717 | 0.47804 | 0.082826 | 0.22778 | -0.15536 | 0.38586 | 0.22618 | 0.021473 | 0.0026694 | 0 | 0 | 0.069798 | 7.4337 |  | 2010-2013 | 0.1355 | 0 | 0 | 0.55114 | 0.66579 | 0.14011 | 0.024275 | 0.066759 | -0.045534 | 0.11309 | 0.06629 | 0.0062935 | 0.00078236 | 0 | 0 | 0.020457 | 1.7449 |  | 2010-2013 | 0 | 0 | 8.0016e-07 | 0.014799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0148 |  | 2010-2013 | 1.4185 | 0 | 8.7457e-05 | 7.3874 | 6.9702 | 1.4668 | 0.25413 | 0.6989 | -0.47669 | 1.1839 | 0.69399 | 0.065886 | 0.0081905 | 0 | 0 | 0.21416 | 19.8855
2013-2016 | 0.0085696 | 0.007001 | 0.0017484 | 0.00055774 | 0.00060632 | 0.0020132 | 7.0955e-05 | 0.0016851 | 0.0057125 | 0.0078927 | -2.942e-06 | 0 | 0.0039183 | 0 | 0 | 0 | 0.039773 |  | 2013-2016 | 0.27507 | 0.22472 | 0.1784 | 0.051602 | 0.019462 | 0.064618 | 0.0022775 | 0.054088 | 0.18336 | 0.25334 | -9.4432e-05 | 0 | 0.12577 | 0 | 0 | 0 | 1.4326 |  | 2013-2016 | 0.080617 | 0.06586 | 0 | 0.00071425 | 0.0057039 | 0.018938 | 0.0006675 | 0.015852 | 0.053739 | 0.074249 | -2.7676e-05 | 0 | 0.036861 | 0 | 0 | 0 | 0.35318 |  | 2013-2016 | 0 | 0 | 0.001784 | 0.00049165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022757 |  | 2013-2016 | 0.84398 | 0.68949 | 0.195 | 0.061215 | 0.059714 | 0.19827 | 0.006988 | 0.16596 | 0.56259 | 0.77732 | -0.00028975 | 0 | 0.3859 | 0 | 0 | 0 | 3.9461
2016-2019 | 0.014751 | 0 | -4.7279e-06 | 0.14483 | 0.0029438 | -0.040573 | 0.0030793 | 0.0012628 | 0.0011357 | 0.013612 | 0.0087662 | 0 | 4.0597e-05 | 0 | 0 | 0 | 0.14985 |  | 2016-2019 | 0.47347 | 0 | -0.00048244 | 14.7677 | 0.094489 | -1.3023 | 0.098839 | 0.040532 | 0.036455 | 0.43693 | 0.28138 | 0 | 0.0013031 | 0 | 0 | 0 | 14.9283 |  | 2016-2019 | 0.13877 | 0 | 0 | 0.0015124 | 0.027693 | -0.38169 | 0.028968 | 0.011879 | 0.010684 | 0.12806 | 0.082467 | 0 | 0.00038191 | 0 | 0 | 0 | 0.048721 |  | 2016-2019 | 0 | 0 | -4.8244e-06 | 0.14763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14762 |  | 2016-2019 | 1.4527 | 0 | -0.00052731 | 16.1513 | 0.28992 | -3.9959 | 0.30327 | 0.12436 | 0.11185 | 1.3406 | 0.86335 | 0 | 0.0039982 | 0 | 0 | 0 | 16.645
2004-2019 | 0.11071 | 0.013014 | 0.0022191 | 0.44579 | 0.11286 | 0.15064 | 0.055816 | 0.18992 | -0.020866 | 0.10396 | 0.015821 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2178 |  | 2004-2019 | 3.5536 | 0.41773 | 0.20753 | 38.8799 | 3.6226 | 4.8351 | 1.7916 | 6.096 | -0.66975 | 3.3369 | 0.50781 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 63.796 |  | 2004-2019 | 1.0415 | 0.12243 | 0.0025435 | 0.88895 | 1.0617 | 1.4171 | 0.52508 | 1.7866 | -0.19629 | 0.978 | 0.14883 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.1332 |  | 2004-2019 | 0 | 0 | 0.0019885 | 0.35847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36046 |  | 2004-2019 | 10.9034 | 1.2817 | 0.24397 | 48.4869 | 11.1153 | 14.8355 | 5.4971 | 18.7043 | -2.055 | 10.2386 | 1.5581 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 124.5441
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.007422% | -4.7% | 0.03458% | -0.5204% | -2.43% | 3.088% |  | -2.332% | 0.0001525% | 0% | 0% | 0% |  | 0% | -0.4382% |  | 2004-2007 | 0% | 0% | -0.007785% | -5.438% | 0.03458% | -0.5204% | -2.43% | 3.088% |  | -2.332% | 0.0001525% | 0% | 0% | 0% |  | 0% | -1.41% |  | 2004-2007 | 0% | 0% | 0% | 0.05803% | 0.03458% | -0.5204% | -2.43% | 3.088% |  | -2.332% | 0.0001525% | 0% | 0% | 0% |  | 0% | 0.2618% |  | 2004-2007 |  |  | -0.007964% | -5.859% | [9 empty] | 0% |  |  | -4.347% |  | 2004-2007 | 0% | 0% | -0.007482% | -4.812% | 0.03458% | -0.5204% | -2.43% | 3.088% |  | -2.332% | 0.0001525% | 0% | 0% | 0% |  | 0% | -0.5153%
2007-2010 | 14.27% | 18.81% | 0.9302% | 43.62% | 18.73% | 35.84% | 58.49% | 30.91% |  | 48.38% | 0.03199% | 1.081% | 40.21% | 0% |  | 2.775% | 21.26% |  | 2007-2010 | 14.27% | 18.81% | 0.5978% | 45.21% | 18.73% | 35.84% | 58.49% | 30.91% |  | 48.38% | 0.03199% | 1.081% | 40.21% | 0% |  | 2.775% | 24.71% |  | 2007-2010 | 14.27% | 18.81% | 7.727% | 32.8% | 18.73% | 35.84% | 58.49% | 30.91% |  | 48.38% | 0.03199% | 1.081% | 40.21% | 0% |  | 2.775% | 18.73% |  | 2007-2010 |  |  | 0.4341% | 46.1% | [9 empty] | 0% |  |  | 34.73% |  | 2007-2010 | 14.27% | 18.81% | 0.8757% | 43.86% | 18.73% | 35.84% | 58.49% | 30.91% |  | 48.38% | 0.03199% | 1.081% | 40.21% | 0% |  | 2.775% | 21.53%
2010-2013 | 3.284% | 0% | 0.001539% | 22.31% | 42.41% | 4.703% | 6.966% | 1.947% | -21.16% | 15.24% | 21.08% | 0.2177% | 0.6552% | 0% |  | 0.3243% | 6.386% |  | 2010-2013 | 3.284% | 0% | 0.001609% | 11.86% | 42.41% | 4.703% | 6.966% | 1.947% | -21.16% | 15.24% | 21.08% | 0.2177% | 0.6552% | 0% |  | 0.3243% | 5.754% |  | 2010-2013 | 3.284% | 0% | 0% | 80.29% | 42.41% | 4.703% | 6.966% | 1.947% | -21.16% | 15.24% | 21.08% | 0.2177% | 0.6552% | 0% |  | 0.3243% | 6.814% |  | 2010-2013 |  |  | 0.001643% | 5.696% | [9 empty] | 0% |  |  | 3.54% |  | 2010-2013 | 3.284% | 0% | 0.00155% | 20.76% | 42.41% | 4.703% | 6.966% | 1.947% | -21.16% | 15.24% | 21.08% | 0.2177% | 0.6552% | 0% |  | 0.3243% | 6.337%
2013-2016 | 2.02% | 26.98% | 3.431% | 0.2192% | 0.6309% | 0.6671% | 0.2059% | 0.4715% | 20.61% | 11.81% | -0.01116% | 0% | 31.07% | 0% |  | 0% | 1.357% |  | 2013-2016 | 2.02% | 26.98% | 3.587% | 0.2067% | 0.6309% | 0.6671% | 0.2059% | 0.4715% | 20.61% | 11.81% | -0.01116% | 0% | 31.07% | 0% |  | 0% | 1.177% |  | 2013-2016 | 2.02% | 26.98% | 0% | 0.5279% | 0.6309% | 0.6671% | 0.2059% | 0.4715% | 20.61% | 11.81% | -0.01116% | 0% | 31.07% | 0% |  | 0% | 1.48% |  | 2013-2016 |  |  | 3.663% | 0.2007% | [9 empty] | 0% |  |  | 0.5643% |  | 2013-2016 | 2.02% | 26.98% | 3.456% | 0.2171% | 0.6309% | 0.6671% | 0.2059% | 0.4715% | 20.61% | 11.81% | -0.01116% | 0% | 31.07% | 0% |  | 0% | 1.343%
2016-2019 | 3.549% | 0% | -0.009607% | 57.04% | 3.082% | -13.54% | 8.953% | 0.355% | 5.162% | 23.09% | 33.23% | 0% | 0.4671% | 0% |  | 0% | 5.181% |  | 2016-2019 | 3.549% | 0% | -0.01006% | 59.28% | 3.082% | -13.54% | 8.953% | 0.355% | 5.162% | 23.09% | 33.23% | 0% | 0.4671% | 0% |  | 0% | 12.41% |  | 2016-2019 | 3.549% | 0% | 0% | 1.124% | 3.082% | -13.54% | 8.953% | 0.355% | 5.162% | 23.09% | 33.23% | 0% | 0.4671% | 0% |  | 0% | 0.2072% |  | 2016-2019 |  |  | -0.01028% | 60.38% | [9 empty] | 0% |  |  | 36.81% |  | 2016-2019 | 3.549% | 0% | -0.009682% | 57.41% | 3.082% | -13.54% | 8.953% | 0.355% | 5.162% | 23.09% | 33.23% | 0% | 0.4671% | 0% |  | 0% | 5.74%
2004-2019 | 21.64% | 40.71% | 4.314% | 80.34% | 54.94% | 30.68% | 64.06% | 34.89% |  | 69.63% | 47.32% | 1.297% | 59.25% | 0% |  | 3.09% | 30.75% |  | 2004-2019 | 21.64% | 40.71% | 4.147% | 79.31% | 54.94% | 30.68% | 64.06% | 34.89% |  | 69.63% | 47.32% | 1.297% | 59.25% | 0% |  | 3.09% | 37.71% |  | 2004-2019 | 21.64% | 40.71% | 7.727% | 86.98% | 54.94% | 30.68% | 64.06% | 34.89% |  | 69.63% | 47.32% | 1.297% | 59.25% | 0% |  | 3.09% | 25.74% |  | 2004-2019 |  |  | 4.065% | 78.72% | [9 empty] | 0% |  |  | 58.72% |  | 2004-2019 | 21.64% | 40.71% | 4.287% | 80.18% | 54.94% | 30.68% | 64.06% | 34.89% |  | 69.63% | 47.32% | 1.297% | 59.25% | 0% |  | 3.09% | 31.3%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.40073 | 0.018983 | 0.04142 | 0.021353 | 0 | 0.80116 | 0.11683 | 0.34034 | 0.023612 | 0.09046 | 0.019619 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 3.1362 | 0% | CZ 0A | 12.8626 | 0.6093 | 4.0007 | 2.1789 | 0 | 25.7156 | 3.75 | 10.9241 | 0.75788 | 2.9036 | 0.62971 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 112.3421 | 0% | CZ 0A | 3.7698 | 0.17858 | 0.030374 | 0 | 0 | 7.5368 | 1.0991 | 3.2017 | 0.22212 | 0.85099 | 0.18456 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 27.9333 | 0% | CZ 0A | 0 | 0 | 0.038971 | 0.021789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.17034 | 0% | CZ 0A | 39.4663 | 1.8695 | 4.5775 | 2.3815 | 0 | 78.9029 | 11.5061 | 33.5182 | 2.3254 | 8.909 | 1.9321 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 311.0518 | 0%
CZ 0B | 0.40079 | 0.018986 | 0.041445 | 0.024577 | 0.0003559 | 0.70435 | 0.079439 | 0.34068 | 0.023612 | 0.080706 | 0.019541 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.9962 | 0% | CZ 0B | 12.8646 | 0.60942 | 4.0033 | 2.4976 | 0.011424 | 22.6081 | 2.5498 | 10.9351 | 0.75788 | 2.5905 | 0.62724 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 108.0647 | 0% | CZ 0B | 3.7704 | 0.17861 | 0.030374 | 0.0013691 | 0.0033481 | 6.6261 | 0.74731 | 3.2049 | 0.22212 | 0.75923 | 0.18383 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 26.5869 | 0% | CZ 0B | 0 | 0 | 0.038996 | 0.02493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.1735 | 0% | CZ 0B | 39.4722 | 1.8699 | 4.5803 | 2.7391 | 0.035051 | 69.3682 | 7.8236 | 33.552 | 2.3254 | 7.9484 | 1.9246 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 297.3019 | 0%
CZ 1A | 0.40099 | 0.018989 | 0.042298 | 0.029482 | 0 | 0.63659 | 0.092891 | 0.33438 | 0.023612 | 0.07317 | 0.019219 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.9334 | 2.054% | CZ 1A | 12.8708 | 0.6095 | 4.0903 | 3.0084 | 0 | 20.4333 | 2.9816 | 10.7328 | 0.75788 | 2.3486 | 0.61688 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 106.4597 | 2.054% | CZ 1A | 3.7722 | 0.17863 | 0.030374 | 0 | 0 | 5.9887 | 0.87386 | 3.1456 | 0.22212 | 0.68833 | 0.1808 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 25.9399 | 2.054% | CZ 1A | 0 | 0 | 0.039867 | 0.030084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.17953 | 2.054% | CZ 1A | 39.4914 | 1.8701 | 4.6754 | 3.2881 | 0 | 62.6952 | 9.1484 | 32.9313 | 2.3254 | 7.2062 | 1.8928 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 291.1875 | 2.054%
CZ 1B | 0.40092 | 0.018964 | 0.042751 | 0.031326 | 0.0010579 | 0.63332 | 0.059452 | 0.34867 | 0.023612 | 0.074328 | 0.019084 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.9152 | 0% | CZ 1B | 12.8688 | 0.60871 | 4.1365 | 3.1672 | 0.033957 | 20.3281 | 1.9083 | 11.1915 | 0.75788 | 2.3858 | 0.61256 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 106.009 | 0% | CZ 1B | 3.7716 | 0.1784 | 0.030374 | 0.0039464 | 0.0099522 | 5.9578 | 0.55929 | 3.28 | 0.22212 | 0.69923 | 0.17953 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 25.7517 | 0% | CZ 1B | 0 | 0 | 0.040329 | 0.031538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.18144 | 0% | CZ 1B | 39.4852 | 1.8677 | 4.7259 | 3.4884 | 0.10419 | 62.3725 | 5.8552 | 34.3386 | 2.3254 | 7.3202 | 1.8795 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 289.4262 | 0%
CZ 2A | 0.40089 | 0.018958 | 0.043935 | 0.045678 | 0.017695 | 0.57301 | 0.069678 | 0.33381 | 0.022247 | 0.068058 | 0.018705 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.8744 | 16.55% | CZ 2A | 12.8677 | 0.60851 | 4.2573 | 4.4051 | 0.56796 | 18.3924 | 2.2365 | 10.7145 | 0.71407 | 2.1845 | 0.60039 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 105.5587 | 16.55% | CZ 2A | 3.7713 | 0.17835 | 0.030374 | 0.034424 | 0.16646 | 5.3905 | 0.65549 | 3.1402 | 0.20928 | 0.64024 | 0.17596 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 25.252 | 16.55% | CZ 2A | 0 | 0 | 0.041537 | 0.042876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.19399 | 16.55% | CZ 2A | 39.4818 | 1.8671 | 4.8579 | 5.0468 | 1.7427 | 56.4332 | 6.8623 | 32.875 | 2.191 | 6.7027 | 1.8422 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 285.5659 | 16.55%
CZ 2B | 0.40096 | 0.018972 | 0.044207 | 0.048922 | 0.1365 | 0.36423 | 0.025266 | 0.36441 | 0.021252 | 0.052327 | 0.018432 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.7572 | 2.4% | CZ 2B | 12.87 | 0.60895 | 4.2851 | 3.7056 | 4.3815 | 11.6909 | 0.811 | 11.6969 | 0.68216 | 1.6796 | 0.59163 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 101.0131 | 2.4% | CZ 2B | 3.772 | 0.17847 | 0.030374 | 0.17303 | 1.2841 | 3.4264 | 0.23769 | 3.4282 | 0.19993 | 0.49226 | 0.1734 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 24.2552 | 2.4% | CZ 2B | 0 | 0 | 0.041815 | 0.031152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.18254 | 2.4% | CZ 2B | 39.4888 | 1.8684 | 4.8884 | 5.2164 | 13.4436 | 35.8711 | 2.4884 | 35.8895 | 2.0931 | 5.1535 | 1.8153 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 273.8797 | 2.4%
CZ 3A | 0.40102 | 0.018968 | 0.047254 | 0.079228 | 0.073131 | 0.38577 | 0.038386 | 0.35339 | 0.021369 | 0.050439 | 0.017892 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.7486 | 13.96% | CZ 3A | 12.872 | 0.60883 | 4.596 | 7.2945 | 2.3473 | 12.3823 | 1.2321 | 11.3432 | 0.68589 | 1.619 | 0.57428 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 103.5651 | 13.96% | CZ 3A | 3.7726 | 0.17844 | 0.030374 | 0.10625 | 0.68797 | 3.6291 | 0.36111 | 3.3245 | 0.20102 | 0.47449 | 0.16831 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 23.7934 | 13.96% | CZ 3A | 0 | 0 | 0.044923 | 0.069319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.22382 | 13.96% | CZ 3A | 39.4949 | 1.8681 | 5.2281 | 8.689 | 7.2023 | 37.9926 | 3.7804 | 34.8042 | 2.1045 | 4.9675 | 1.7621 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 273.5568 | 13.96%
CZ 3B | 0.40088 | 0.018968 | 0.046326 | 0.06119 | 0.14047 | 0.31688 | 0.021489 | 0.37129 | 0.020697 | 0.04388 | 0.017945 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.7217 | 6.966% | CZ 3B | 12.8673 | 0.60883 | 4.5013 | 5.0499 | 4.5088 | 10.1711 | 0.68974 | 11.9175 | 0.66434 | 1.4084 | 0.57601 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 100.9731 | 6.966% | CZ 3B | 3.7712 | 0.17844 | 0.030374 | 0.16059 | 1.3215 | 2.981 | 0.20215 | 3.4928 | 0.19471 | 0.41279 | 0.16882 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 23.7737 | 6.966% | CZ 3B | 0 | 0 | 0.043977 | 0.04502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.19857 | 6.966% | CZ 3B | 39.4806 | 1.8681 | 5.1246 | 6.6019 | 13.8344 | 31.2078 | 2.1163 | 36.5665 | 2.0384 | 4.3215 | 1.7674 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 270.5907 | 6.966%
CZ 3C | 0.40082 | 0.018964 | 0.047429 | 0.059446 | 0.032173 | 0.28829 | 0.015997 | 0.33837 | 0 | 0.045313 | 0.017749 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.5263 | 2.177% | CZ 3C | 12.8654 | 0.60871 | 4.6139 | 5.7509 | 1.0327 | 9.2534 | 0.51347 | 10.861 | 0 | 1.4545 | 0.56969 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 95.5332 | 2.177% | CZ 3C | 3.7706 | 0.1784 | 0.030374 | 0.042374 | 0.30266 | 2.712 | 0.15049 | 3.1832 | 0 | 0.42628 | 0.16697 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 21.8227 | 2.177% | CZ 3C | 0 | 0 | 0.045102 | 0.056063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.21074 | 2.177% | CZ 3C | 39.4746 | 1.8677 | 5.2477 | 6.5713 | 3.1686 | 28.3921 | 1.5755 | 33.3247 | 0 | 4.4627 | 1.748 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 251.496 | 2.177%
CZ 4A | 0.40082 | 0.01894 | 0.050336 | 0.12362 | 0.10919 | 0.30853 | 0.026293 | 0.34819 | 0.021369 | 0.041667 | 0.017327 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.728 | 20.37% | CZ 4A | 12.8653 | 0.60793 | 4.9105 | 11.4139 | 3.5048 | 9.9033 | 0.84393 | 11.176 | 0.68589 | 1.3374 | 0.55615 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 105.8149 | 20.37% | CZ 4A | 3.7706 | 0.17817 | 0.030374 | 0.16142 | 1.0272 | 2.9025 | 0.24734 | 3.2755 | 0.20102 | 0.39198 | 0.163 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 23.2085 | 20.37% | CZ 4A | 0 | 0 | 0.048068 | 0.10863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.26628 | 20.37% | CZ 4A | 39.4745 | 1.8653 | 5.5719 | 13.5633 | 10.7538 | 30.3862 | 2.5894 | 34.2912 | 2.1045 | 4.1036 | 1.7064 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 272.0733 | 20.37%
CZ 4B | 0.40071 | 0.018954 | 0.049406 | 0.081587 | 0.19604 | 0.245 | 0.0085379 | 0.38958 | 0.020504 | 0.035681 | 0.017355 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.7251 | 0.5664% | CZ 4B | 12.8619 | 0.6084 | 4.8156 | 6.9442 | 6.2926 | 7.864 | 0.27405 | 12.5047 | 0.65813 | 1.1453 | 0.55705 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 102.5356 | 0.5664% | CZ 4B | 3.7696 | 0.17831 | 0.030374 | 0.18575 | 1.8442 | 2.3048 | 0.080319 | 3.6649 | 0.19289 | 0.33566 | 0.16326 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 23.6095 | 0.5664% | CZ 4B | 0 | 0 | 0.047119 | 0.063104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.2198 | 0.5664% | CZ 4B | 39.4639 | 1.8667 | 5.4681 | 8.8419 | 19.3074 | 24.129 | 0.84086 | 38.3682 | 2.0193 | 3.514 | 1.7092 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 271.192 | 0.5664%
CZ 4C | 0.40101 | 0.018918 | 0.051188 | 0.10594 | 0.036928 | 0.19057 | 0.0035076 | 0.34992 | 0.019652 | 0.03723 | 0.017023 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.4936 | 2.852% | CZ 4C | 12.8714 | 0.60722 | 4.9975 | 10.1157 | 1.1853 | 6.1169 | 0.11259 | 11.2317 | 0.63077 | 1.195 | 0.54641 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 97.6202 | 2.852% | CZ 4C | 3.7724 | 0.17797 | 0.030374 | 0.09347 | 0.34739 | 1.7928 | 0.032997 | 3.2918 | 0.18487 | 0.35024 | 0.16014 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 21.0938 | 2.852% | CZ 4C | 0 | 0 | 0.048938 | 0.097968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.25648 | 2.852% | CZ 4C | 39.4933 | 1.8631 | 5.6669 | 11.6864 | 3.6369 | 18.7685 | 0.34545 | 34.462 | 1.9354 | 3.6666 | 1.6765 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 248.8644 | 2.852%
CZ 5A | 0.4008 | 0.018945 | 0.053143 | 0.16167 | 0.11557 | 0.23479 | 0.015965 | 0.36047 | 0.020947 | 0.033042 | 0.016935 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.694 | 20.94% | CZ 5A | 12.8649 | 0.60808 | 5.1969 | 15.147 | 3.7097 | 7.5363 | 0.51245 | 11.5704 | 0.67235 | 1.0606 | 0.54358 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 107.4319 | 20.94% | CZ 5A | 3.7705 | 0.17822 | 0.030374 | 0.18153 | 1.0872 | 2.2088 | 0.15019 | 3.3911 | 0.19705 | 0.31084 | 0.15932 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 22.5245 | 20.94% | CZ 5A | 0 | 0 | 0.050933 | 0.14528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30578 | 20.94% | CZ 5A | 39.4733 | 1.8658 | 5.8849 | 17.7791 | 11.3823 | 23.1234 | 1.5724 | 35.5013 | 2.0629 | 3.2542 | 1.6679 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 269.2308 | 20.94%
CZ 5B | 0.40072 | 0.018946 | 0.052302 | 0.11525 | 0.16576 | 0.20234 | 0.0069272 | 0.39631 | 0.020805 | 0.033028 | 0.016977 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.6911 | 5.178% | CZ 5B | 12.8622 | 0.60812 | 5.1111 | 10.3982 | 5.3205 | 6.4947 | 0.22235 | 12.7208 | 0.66779 | 1.0601 | 0.54492 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 104.0206 | 5.178% | CZ 5B | 3.7697 | 0.17823 | 0.030374 | 0.18324 | 1.5593 | 1.9035 | 0.065167 | 3.7282 | 0.19572 | 0.3107 | 0.15971 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 22.9433 | 5.178% | CZ 5B | 0 | 0 | 0.050075 | 0.09773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.25738 | 5.178% | CZ 5B | 39.465 | 1.8659 | 5.7912 | 12.6002 | 16.3247 | 19.9277 | 0.68223 | 39.031 | 2.049 | 3.2528 | 1.672 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 268.3249 | 5.178%
CZ 5C | 0.40098 | 0.018917 | 0.052871 | 0.25524 | 0.034412 | 0.11905 | 0.0045631 | 0.3548 | 0.019689 | 0.034456 | 0.016748 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.5734 | 0.1506% | CZ 5C | 12.8705 | 0.60718 | 5.1691 | 25.1816 | 1.1046 | 3.8211 | 0.14647 | 11.3883 | 0.63199 | 1.106 | 0.53758 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 110.5742 | 0.1506% | CZ 5C | 3.7721 | 0.17795 | 0.030374 | 0.11604 | 0.32373 | 1.1199 | 0.042927 | 3.3377 | 0.18523 | 0.32414 | 0.15756 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 20.4471 | 0.1506% | CZ 5C | 0 | 0 | 0.050655 | 0.24786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40809 | 0.1506% | CZ 5C | 39.4904 | 1.863 | 5.8546 | 28.3056 | 3.3891 | 11.7244 | 0.4494 | 34.9427 | 1.9391 | 3.3934 | 1.6494 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 258.6644 | 0.1506%
CZ 6A | 0.40081 | 0.018936 | 0.055377 | 0.21131 | 0.13128 | 0.22543 | 0.016425 | 0.36401 | 0.021326 | 0.027769 | 0.016839 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.7512 | 4.352% | CZ 6A | 12.865 | 0.60781 | 5.4249 | 20.1025 | 4.2137 | 7.2358 | 0.52721 | 11.6838 | 0.68451 | 0.89132 | 0.54048 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 112.7868 | 4.352% | CZ 6A | 3.7705 | 0.17814 | 0.030374 | 0.19637 | 1.235 | 2.1207 | 0.15452 | 3.4243 | 0.20062 | 0.26123 | 0.15841 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 22.5895 | 4.352% | CZ 6A | 0 | 0 | 0.053213 | 0.19432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.35711 | 4.352% | CZ 6A | 39.4737 | 1.8649 | 6.1341 | 23.2955 | 12.929 | 22.2015 | 1.6176 | 35.8493 | 2.1003 | 2.7348 | 1.6584 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 275.5224 | 4.352%
CZ 6B | 0.40081 | 0.018923 | 0.054794 | 0.29498 | 0.18237 | 0.14087 | 0.0065004 | 0.38308 | 0.02084 | 0.037361 | 0.016713 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.819 | 0.7088% | CZ 6B | 12.8652 | 0.60738 | 5.3654 | 28.392 | 5.8538 | 4.5215 | 0.20865 | 12.296 | 0.66893 | 1.1992 | 0.53644 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 120.5242 | 0.7088% | CZ 6B | 3.7706 | 0.17801 | 0.030374 | 0.22972 | 1.7157 | 1.3252 | 0.061151 | 3.6038 | 0.19605 | 0.35147 | 0.15722 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 22.4785 | 0.7088% | CZ 6B | 0 | 0 | 0.052617 | 0.27608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.43828 | 0.7088% | CZ 6B | 39.474 | 1.8636 | 6.069 | 32.5807 | 17.9613 | 13.8733 | 0.64019 | 37.7277 | 2.0525 | 3.6795 | 1.646 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 283.231 | 0.7088%
CZ 7 | 0.40081 | 0.018912 | 0.058061 | 0.37715 | 0.17811 | 0.15679 | 0.012457 | 0.36728 | 0.021382 | 0.043515 | 0.016623 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.9128 | 0.728% | CZ 7 | 12.8653 | 0.60702 | 5.6988 | 36.7666 | 5.7169 | 5.0325 | 0.39983 | 11.7889 | 0.68632 | 1.3967 | 0.53357 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 129.5022 | 0.728% | CZ 7 | 3.7706 | 0.17791 | 0.030374 | 0.23107 | 1.6755 | 1.4749 | 0.11718 | 3.4551 | 0.20115 | 0.40936 | 0.15638 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 22.559 | 0.728% | CZ 7 | 0 | 0 | 0.055952 | 0.35978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.52531 | 0.728% | CZ 7 | 39.4744 | 1.8625 | 6.4335 | 41.7433 | 17.5411 | 15.4411 | 1.2268 | 36.1718 | 2.1058 | 4.2856 | 1.6372 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 293.5863 | 0.728%
CZ 8 | 0.40152 | 0.018806 | 0.061706 | 0.46035 | 0.22698 | 0.09079 | 0.0036715 | 0.35867 | 0.021589 | 0.032404 | 0.016296 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.9545 | 0.05054% | CZ 8 | 12.8878 | 0.60365 | 6.0707 | 44.8029 | 7.2854 | 2.9142 | 0.11785 | 11.5127 | 0.69295 | 1.0401 | 0.52305 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 136.4609 | 0.05054% | CZ 8 | 3.7772 | 0.17692 | 0.030374 | 0.29202 | 2.1352 | 0.85409 | 0.034539 | 3.3742 | 0.20309 | 0.30484 | 0.1533 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 22.1951 | 0.05054% | CZ 8 | 0 | 0 | 0.05967 | 0.43807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.60731 | 0.05054% | CZ 8 | 39.5435 | 1.8522 | 6.8399 | 50.9377 | 22.3537 | 8.9415 | 0.36159 | 35.3242 | 2.1262 | 3.1913 | 1.6049 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 298.7399 | 0.05054%
US Weighted | 0.40087 | 0.018951 | 0.049217 | 0.10909 | 0.092557 | 0.34032 | 0.031314 | 0.35447 | 0.020866 | 0.045344 | 0.017611 | 0.30666 | 0.0086505 | 0.27812 | 0 | 0.66831 | 2.7423 | 100% | US Weighted | 12.8669 | 0.60829 | 4.7963 | 10.1423 | 2.9709 | 10.9237 | 1.0051 | 11.3778 | 0.66975 | 1.4554 | 0.56526 | 9.843 | 0.27766 | 16.4378 | 0 | 21.4513 | 105.3915 | 100% | US Weighted | 3.7711 | 0.17828 | 0.030374 | 0.13307 | 0.87072 | 3.2015 | 0.29458 | 3.3347 | 0.19629 | 0.42656 | 0.16567 | 2.8848 | 0.081378 | 1.6061 | 0 | 6.287 | 23.4622 | 100% | US Weighted | 0 | 0 | 0.046927 | 0.096883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.25339 | 100% | US Weighted | 39.4794 | 1.8664 | 5.4471 | 11.9824 | 9.1155 | 33.517 | 3.084 | 34.9105 | 2.055 | 4.4657 | 1.7344 | 30.2012 | 0.85194 | 28.7914 | 0 | 65.8187 | 273.3206 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.41557 | 0.018983 | 0.041418 | 0.14727 | 0 | 0.75371 | 0.12288 | 0.34726 | 0.024854 | 0.098944 | 0.028896 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 3.2616 | 0% | CZ 0A | 13.3389 | 0.6093 | 4.0005 | 15.0273 | 0 | 24.1923 | 3.9443 | 11.1463 | 0.79777 | 3.1759 | 0.92751 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 125.1711 | 0% | CZ 0A | 3.9094 | 0.17858 | 0.030374 | 0 | 0 | 7.0904 | 1.156 | 3.2668 | 0.23381 | 0.9308 | 0.27184 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 27.9277 | 0% | CZ 0A | 0 | 0 | 0.038969 | 0.15027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.29882 | 0% | CZ 0A | 40.9275 | 1.8695 | 4.5773 | 16.4248 | 0 | 74.229 | 12.1021 | 34.2001 | 2.4478 | 9.7445 | 2.8459 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 325.0358 | 0%
CZ 0B | 0.41558 | 0.018986 | 0.041447 | 0.1523 | 0.00035712 | 0.62593 | 0.087388 | 0.34791 | 0.024854 | 0.087165 | 0.028768 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 3.0925 | 0% | CZ 0B | 13.3391 | 0.60942 | 4.0034 | 15.531 | 0.011463 | 20.0909 | 2.805 | 11.1671 | 0.79777 | 2.7978 | 0.92339 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 120.0873 | 0% | CZ 0B | 3.9095 | 0.17861 | 0.030374 | 0.0013691 | 0.0033596 | 5.8883 | 0.82208 | 3.2729 | 0.23381 | 0.81999 | 0.27063 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 26.2906 | 0% | CZ 0B | 0 | 0 | 0.038998 | 0.15526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30384 | 0% | CZ 0B | 40.9282 | 1.8699 | 4.5804 | 16.9846 | 0.035171 | 61.6445 | 8.6064 | 34.264 | 2.4478 | 8.5845 | 2.8332 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 308.4459 | 0%
CZ 1A | 0.41575 | 0.018989 | 0.042296 | 0.16494 | 0 | 0.61917 | 0.10144 | 0.34166 | 0.024854 | 0.082876 | 0.02843 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 3.1022 | 2.054% | CZ 1A | 13.3448 | 0.6095 | 4.0901 | 16.8303 | 0 | 19.8739 | 3.256 | 10.9665 | 0.79777 | 2.6601 | 0.91256 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 121.3526 | 2.054% | CZ 1A | 3.9111 | 0.17863 | 0.030374 | 0 | 0 | 5.8247 | 0.95428 | 3.2141 | 0.23381 | 0.77964 | 0.26745 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 26.2539 | 2.054% | CZ 1A | 0 | 0 | 0.039864 | 0.1683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.31774 | 2.054% | CZ 1A | 40.9457 | 1.8701 | 4.6752 | 18.3955 | 0 | 60.9788 | 9.9904 | 33.6485 | 2.4478 | 8.1621 | 2.8 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 309.5811 | 2.054%
CZ 1B | 0.41561 | 0.018964 | 0.042753 | 0.16799 | 0.0010628 | 0.58774 | 0.063737 | 0.3513 | 0.024854 | 0.080013 | 0.028183 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 3.044 | 0% | CZ 1B | 13.3401 | 0.60871 | 4.1367 | 17.1123 | 0.034114 | 18.8652 | 2.0458 | 11.276 | 0.79777 | 2.5682 | 0.90463 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 119.7006 | 0% | CZ 1B | 3.9098 | 0.1784 | 0.030374 | 0.0039579 | 0.0099982 | 5.5291 | 0.59959 | 3.3048 | 0.23381 | 0.75271 | 0.26513 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 25.6773 | 0% | CZ 1B | 0 | 0 | 0.040331 | 0.17099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.3209 | 0% | CZ 1B | 40.9313 | 1.8677 | 4.7261 | 18.7305 | 0.10467 | 57.8837 | 6.2771 | 34.5981 | 2.4478 | 7.8801 | 2.7757 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 303.89 | 0%
CZ 2A | 0.4157 | 0.018958 | 0.043933 | 0.20178 | 0.017796 | 0.50716 | 0.074581 | 0.33677 | 0.023279 | 0.078902 | 0.027759 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 3.0084 | 16.55% | CZ 2A | 13.3431 | 0.60851 | 4.2572 | 20.3333 | 0.57122 | 16.2787 | 2.3939 | 10.8096 | 0.74721 | 2.5326 | 0.891 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 120.7774 | 16.55% | CZ 2A | 3.9106 | 0.17835 | 0.030374 | 0.034505 | 0.16742 | 4.771 | 0.70161 | 3.1681 | 0.21899 | 0.74226 | 0.26114 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 25.0441 | 16.55% | CZ 2A | 0 | 0 | 0.041535 | 0.20216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.35327 | 16.55% | CZ 2A | 40.9405 | 1.8671 | 4.8578 | 22.4569 | 1.7527 | 49.9479 | 7.3452 | 33.1669 | 2.2926 | 7.7707 | 2.7339 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 300.7993 | 16.55%
CZ 2B | 0.41588 | 0.018972 | 0.044205 | 0.17675 | 0.13721 | 0.32819 | 0.027552 | 0.36122 | 0.022049 | 0.060225 | 0.027198 | 0.30666 | 0.008692 | 0.27812 | 0 | 0.66831 | 2.8812 | 2.4% | CZ 2B | 13.349 | 0.60895 | 4.2849 | 16.7409 | 4.404 | 10.534 | 0.88437 | 11.5944 | 0.70772 | 1.9331 | 0.87298 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 113.9254 | 2.4% | CZ 2B | 3.9124 | 0.17847 | 0.030374 | 0.17416 | 1.2907 | 3.0873 | 0.25919 | 3.3981 | 0.20742 | 0.56656 | 0.25586 | 2.8848 | 0.081769 | 1.6061 | 0 | 6.287 | 24.2203 | 2.4% | CZ 2B | 0 | 0 | 0.041813 | 0.16147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.31286 | 2.4% | CZ 2B | 40.9584 | 1.8684 | 4.8881 | 19.4715 | 13.5128 | 32.3215 | 2.7135 | 35.5748 | 2.1715 | 5.9313 | 2.6786 | 30.2012 | 0.85604 | 28.7914 | 0 | 65.8187 | 287.7578 | 2.4%
CZ 3A | 0.41589 | 0.018968 | 0.047254 | 0.23723 | 0.07469 | 0.34669 | 0.042806 | 0.34468 | 0.022402 | 0.066073 | 0.026728 | 0.30666 | 0.008692 | 0.27812 | 0 | 0.66831 | 2.9052 | 13.96% | CZ 3A | 13.3493 | 0.60883 | 4.596 | 23.4112 | 2.3974 | 11.128 | 1.374 | 11.0636 | 0.71906 | 2.1208 | 0.85791 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 119.6371 | 13.96% | CZ 3A | 3.9124 | 0.17844 | 0.030374 | 0.10708 | 0.70264 | 3.2614 | 0.40269 | 3.2426 | 0.21074 | 0.62157 | 0.25144 | 2.8848 | 0.081769 | 1.6061 | 0 | 6.287 | 23.7812 | 13.96% | CZ 3A | 0 | 0 | 0.044923 | 0.23046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.38496 | 13.96% | CZ 3A | 40.9594 | 1.8681 | 5.2281 | 26.3101 | 7.3559 | 34.144 | 4.2158 | 33.9463 | 2.2063 | 6.5072 | 2.6323 | 30.2012 | 0.85604 | 28.7914 | 0 | 65.8187 | 291.0408 | 13.96%
CZ 3B | 0.41573 | 0.018968 | 0.046322 | 0.18924 | 0.14096 | 0.28085 | 0.024385 | 0.37499 | 0.0215 | 0.055061 | 0.026667 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.8565 | 6.966% | CZ 3B | 13.3441 | 0.60883 | 4.5009 | 18.1132 | 4.5246 | 9.0148 | 0.78269 | 12.0363 | 0.69009 | 1.7673 | 0.85595 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 114.2498 | 6.966% | CZ 3B | 3.9109 | 0.17844 | 0.030374 | 0.16104 | 1.3261 | 2.6421 | 0.22939 | 3.5276 | 0.20225 | 0.51797 | 0.25086 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 23.8368 | 6.966% | CZ 3B | 0 | 0 | 0.043973 | 0.17564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32919 | 6.966% | CZ 3B | 40.9435 | 1.8681 | 5.1242 | 20.8831 | 13.8827 | 27.6599 | 2.4015 | 36.931 | 2.1174 | 5.4227 | 2.6263 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 285.5276 | 6.966%
CZ 3C | 0.4156 | 0.018964 | 0.047422 | 0.20654 | 0.032312 | 0.2417 | 0.020214 | 0.34382 | 0 | 0.045179 | 0.026554 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.6601 | 2.177% | CZ 3C | 13.3398 | 0.60871 | 4.6131 | 20.76 | 1.0372 | 7.7579 | 0.64883 | 11.0358 | 0 | 1.4501 | 0.85234 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 110.1148 | 2.177% | CZ 3C | 3.9097 | 0.1784 | 0.030374 | 0.042478 | 0.30397 | 2.2737 | 0.19016 | 3.2344 | 0 | 0.42501 | 0.24981 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 21.6977 | 2.177% | CZ 3C | 0 | 0 | 0.045095 | 0.20615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.36082 | 2.177% | CZ 3C | 40.9304 | 1.8677 | 5.2468 | 22.977 | 3.1823 | 23.8035 | 1.9908 | 33.8609 | 0 | 4.4494 | 2.6152 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 266.5913 | 2.177%
CZ 4A | 0.41551 | 0.01894 | 0.050327 | 0.28109 | 0.11224 | 0.27162 | 0.02925 | 0.3536 | 0.022938 | 0.056891 | 0.026046 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.9002 | 20.37% | CZ 4A | 13.337 | 0.60793 | 4.9095 | 27.4716 | 3.6026 | 8.7185 | 0.93886 | 11.3499 | 0.73625 | 1.8261 | 0.83601 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 122.3453 | 20.37% | CZ 4A | 3.9088 | 0.17817 | 0.030374 | 0.16294 | 1.0559 | 2.5553 | 0.27516 | 3.3265 | 0.21578 | 0.5352 | 0.24502 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 23.3488 | 20.37% | CZ 4A | 0 | 0 | 0.048059 | 0.26916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.42679 | 20.37% | CZ 4A | 40.9217 | 1.8653 | 5.5708 | 31.1246 | 11.0537 | 26.751 | 2.8807 | 34.8249 | 2.259 | 5.603 | 2.5651 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 291.087 | 20.37%
CZ 4B | 0.41537 | 0.018954 | 0.049407 | 0.20209 | 0.19744 | 0.20449 | 0.010213 | 0.39424 | 0.020684 | 0.047688 | 0.025964 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.8483 | 0.5664% | CZ 4B | 13.3325 | 0.6084 | 4.8157 | 19.2352 | 6.3373 | 6.5638 | 0.32783 | 12.6541 | 0.6639 | 1.5307 | 0.83337 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 114.9139 | 0.5664% | CZ 4B | 3.9075 | 0.17831 | 0.030374 | 0.18649 | 1.8574 | 1.9237 | 0.096082 | 3.7087 | 0.19458 | 0.44862 | 0.24425 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 23.6358 | 0.5664% | CZ 4B | 0 | 0 | 0.047121 | 0.18599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.34269 | 0.5664% | CZ 4B | 40.908 | 1.8667 | 5.4683 | 22.281 | 19.4447 | 20.1396 | 1.0059 | 38.8265 | 2.0371 | 4.6966 | 2.557 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 284.8986 | 0.5664%
CZ 4C | 0.41582 | 0.018918 | 0.051183 | 0.25356 | 0.037648 | 0.1451 | 0.0053886 | 0.35773 | 0.021441 | 0.04377 | 0.025643 | 0.30666 | 0.008692 | 0.27812 | 0 | 0.66831 | 2.638 | 2.852% | CZ 4C | 13.3469 | 0.60722 | 4.9969 | 25.1758 | 1.2084 | 4.6575 | 0.17296 | 11.4825 | 0.6882 | 1.4049 | 0.82309 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 112.5755 | 2.852% | CZ 4C | 3.9118 | 0.17797 | 0.030374 | 0.093896 | 0.35417 | 1.365 | 0.050693 | 3.3653 | 0.2017 | 0.41176 | 0.24123 | 2.8848 | 0.081769 | 1.6061 | 0 | 6.287 | 21.0637 | 2.852% | CZ 4C | 0 | 0 | 0.048933 | 0.24855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40706 | 2.852% | CZ 4C | 40.9522 | 1.8631 | 5.6664 | 28.1499 | 3.7078 | 14.2906 | 0.5307 | 35.2316 | 2.1116 | 4.3107 | 2.5255 | 30.2012 | 0.85604 | 28.7914 | 0 | 65.8187 | 265.0074 | 2.852%
CZ 5A | 0.41548 | 0.018945 | 0.053134 | 0.3053 | 0.12259 | 0.20026 | 0.018397 | 0.36037 | 0.02223 | 0.05025 | 0.025565 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.8543 | 20.94% | CZ 5A | 13.3362 | 0.60808 | 5.196 | 29.7774 | 3.9348 | 6.4279 | 0.5905 | 11.5669 | 0.71353 | 1.6129 | 0.82058 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 122.5959 | 20.94% | CZ 5A | 3.9086 | 0.17822 | 0.030374 | 0.18502 | 1.1532 | 1.8839 | 0.17306 | 3.3901 | 0.20912 | 0.47272 | 0.2405 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 22.6846 | 20.94% | CZ 5A | 0 | 0 | 0.050924 | 0.29146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.45196 | 20.94% | CZ 5A | 40.9192 | 1.8658 | 5.884 | 33.7937 | 12.0731 | 19.7227 | 1.8118 | 35.4907 | 2.1893 | 4.9489 | 2.5178 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 286.8842 | 20.94%
CZ 5B | 0.41535 | 0.018946 | 0.052303 | 0.23278 | 0.17 | 0.16599 | 0.004376 | 0.3992 | 0.020949 | 0.040606 | 0.025526 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.8078 | 5.178% | CZ 5B | 13.3318 | 0.60812 | 5.1112 | 22.3749 | 5.4566 | 5.328 | 0.14046 | 12.8134 | 0.67242 | 1.3034 | 0.81932 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 115.9706 | 5.178% | CZ 5B | 3.9073 | 0.17823 | 0.030374 | 0.18542 | 1.5993 | 1.5615 | 0.041166 | 3.7554 | 0.19708 | 0.38199 | 0.24013 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 22.9376 | 5.178% | CZ 5B | 0 | 0 | 0.050076 | 0.21742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.37707 | 5.178% | CZ 5B | 40.9057 | 1.8659 | 5.7912 | 25.7054 | 16.7426 | 16.3478 | 0.43097 | 39.3151 | 2.0632 | 3.9991 | 2.5139 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 281.3481 | 5.178%
CZ 5C | 0.41573 | 0.018917 | 0.052867 | 0.25812 | 0.034546 | 0.116 | 0.0045399 | 0.36198 | 0.02177 | 0.035185 | 0.02533 | 0.30666 | 0.008692 | 0.27812 | 0 | 0.66831 | 2.6067 | 0.1506% | CZ 5C | 13.344 | 0.60718 | 5.1688 | 25.4743 | 1.1088 | 3.7232 | 0.14572 | 11.6187 | 0.69876 | 1.1294 | 0.81304 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 111.843 | 0.1506% | CZ 5C | 3.9109 | 0.17795 | 0.030374 | 0.11623 | 0.32498 | 1.0912 | 0.042708 | 3.4052 | 0.2048 | 0.331 | 0.23829 | 2.8848 | 0.081769 | 1.6061 | 0 | 6.287 | 20.7334 | 0.1506% | CZ 5C | 0 | 0 | 0.050651 | 0.25078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41101 | 0.1506% | CZ 5C | 40.9432 | 1.863 | 5.8542 | 28.6268 | 3.4022 | 11.424 | 0.44711 | 35.6495 | 2.144 | 3.4652 | 2.4946 | 30.2012 | 0.85604 | 28.7914 | 0 | 65.8187 | 261.9811 | 0.1506%
CZ 6A | 0.41543 | 0.018936 | 0.055372 | 0.34357 | 0.1383 | 0.19592 | 0.018855 | 0.36455 | 0.022511 | 0.052974 | 0.025466 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.9137 | 4.352% | CZ 6A | 13.3345 | 0.60781 | 5.4243 | 33.5737 | 4.4393 | 6.2887 | 0.60522 | 11.7014 | 0.72255 | 1.7004 | 0.8174 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 127.2262 | 4.352% | CZ 6A | 3.9081 | 0.17814 | 0.030374 | 0.19963 | 1.3011 | 1.8431 | 0.17738 | 3.4295 | 0.21177 | 0.49835 | 0.23957 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 22.8767 | 4.352% | CZ 6A | 0 | 0 | 0.053207 | 0.32893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.49171 | 4.352% | CZ 6A | 40.9141 | 1.8649 | 6.1335 | 38.0415 | 13.621 | 19.2955 | 1.857 | 35.9033 | 2.217 | 5.2172 | 2.508 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 293.2402 | 4.352%
CZ 6B | 0.41542 | 0.018923 | 0.054791 | 0.29735 | 0.18317 | 0.13807 | 0.0032887 | 0.3851 | 0.022137 | 0.038519 | 0.025221 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.8438 | 0.7088% | CZ 6B | 13.334 | 0.60738 | 5.3651 | 28.6296 | 5.8794 | 4.4317 | 0.10556 | 12.361 | 0.71054 | 1.2364 | 0.80955 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 121.4811 | 0.7088% | CZ 6B | 3.908 | 0.17801 | 0.030374 | 0.23035 | 1.7231 | 1.2988 | 0.030938 | 3.6228 | 0.20825 | 0.36236 | 0.23726 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 22.69 | 0.7088% | CZ 6B | 0 | 0 | 0.052614 | 0.27844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.44063 | 0.7088% | CZ 6B | 40.9126 | 1.8636 | 6.0687 | 32.8446 | 18.0396 | 13.5976 | 0.32389 | 37.9271 | 2.1801 | 3.7936 | 2.4839 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 285.7026 | 0.7088%
CZ 7 | 0.41536 | 0.018912 | 0.058057 | 0.38502 | 0.17893 | 0.15561 | 0.012652 | 0.36818 | 0.022488 | 0.045243 | 0.025194 | 0.30666 | 0.0086908 | 0.27812 | 0 | 0.66831 | 2.9474 | 0.728% | CZ 7 | 13.3322 | 0.60702 | 5.6983 | 37.5631 | 5.7433 | 4.9948 | 0.40611 | 11.8178 | 0.72181 | 1.4522 | 0.80868 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 131.1564 | 0.728% | CZ 7 | 3.9075 | 0.17791 | 0.030374 | 0.23202 | 1.6833 | 1.4639 | 0.11902 | 3.4636 | 0.21155 | 0.42562 | 0.23701 | 2.8848 | 0.081757 | 1.6061 | 0 | 6.287 | 22.8114 | 0.728% | CZ 7 | 0 | 0 | 0.055947 | 0.36772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.53324 | 0.728% | CZ 7 | 40.9071 | 1.8625 | 6.433 | 42.6202 | 17.6221 | 15.3255 | 1.2461 | 36.2603 | 2.2147 | 4.4558 | 2.4813 | 30.2012 | 0.85592 | 28.7914 | 0 | 65.8187 | 297.0958 | 0.728%
CZ 8 | 0.41629 | 0.018806 | 0.061696 | 0.47421 | 0.22774 | 0.089694 | 0.0036825 | 0.36537 | 0.022369 | 0.033407 | 0.024776 | 0.30666 | 0.008692 | 0.27812 | 0 | 0.66831 | 2.9998 | 0.05054% | CZ 8 | 13.362 | 0.60365 | 6.0697 | 46.2085 | 7.31 | 2.879 | 0.1182 | 11.7277 | 0.718 | 1.0723 | 0.79526 | 9.843 | 0.279 | 16.4378 | 0 | 21.4513 | 138.8754 | 0.05054% | CZ 8 | 3.9162 | 0.17692 | 0.030374 | 0.29324 | 2.1424 | 0.84378 | 0.034643 | 3.4372 | 0.21043 | 0.31427 | 0.23308 | 2.8848 | 0.081769 | 1.6061 | 0 | 6.287 | 22.4923 | 0.05054% | CZ 8 | 0 | 0 | 0.059661 | 0.45208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.62132 | 0.05054% | CZ 8 | 40.9983 | 1.8522 | 6.8389 | 52.4822 | 22.4293 | 8.8336 | 0.36268 | 35.9841 | 2.203 | 3.2901 | 2.4401 | 30.2012 | 0.85604 | 28.7914 | 0 | 65.8187 | 303.3818 | 0.05054%
US Weighted | 0.41562 | 0.018951 | 0.049212 | 0.25392 | 0.095501 | 0.29975 | 0.034393 | 0.35574 | 0.022002 | 0.058956 | 0.026377 | 0.30666 | 0.008691 | 0.27812 | 0 | 0.66831 | 2.8922 | 100% | US Weighted | 13.3404 | 0.60829 | 4.7958 | 24.91 | 3.0654 | 9.6213 | 1.104 | 11.4184 | 0.70621 | 1.8924 | 0.84664 | 9.843 | 0.27896 | 16.4378 | 0 | 21.4513 | 120.3198 | 100% | US Weighted | 3.9098 | 0.17828 | 0.030374 | 0.13458 | 0.89841 | 2.8199 | 0.32355 | 3.3465 | 0.20698 | 0.55462 | 0.24814 | 2.8848 | 0.08176 | 1.6061 | 0 | 6.287 | 23.5109 | 100% | US Weighted | 0 | 0 | 0.046922 | 0.24451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40101 | 100% | US Weighted | 40.9322 | 1.8664 | 5.4466 | 28.1337 | 9.4054 | 29.5211 | 3.3872 | 35.0349 | 2.1668 | 5.8063 | 2.5977 | 30.2012 | 0.85594 | 28.7914 | 0 | 65.8187 | 289.9656 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.42397 | 0.025995 | 0.044922 | 0.14633 | 0 | 0.77402 | 0.12319 | 0.35025 | 0.033721 | 0.11156 | 0.028887 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 3.3285 | 0% | CZ 0A | 13.6085 | 0.8344 | 4.3581 | 14.9316 | 0 | 24.8444 | 3.9543 | 11.2424 | 1.0824 | 3.5807 | 0.9272 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 127.5007 | 0% | CZ 0A | 3.9884 | 0.24455 | 0.030374 | 0 | 0 | 7.2815 | 1.1589 | 3.295 | 0.31723 | 1.0495 | 0.27175 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 28.5337 | 0% | CZ 0A | 0 | 0 | 0.042544 | 0.14932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30144 | 0% | CZ 0A | 41.7547 | 2.5602 | 4.9681 | 16.3203 | 0 | 76.2297 | 12.1328 | 34.4949 | 3.321 | 10.9867 | 2.8449 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 331.6665 | 0%
CZ 0B | 0.424 | 0.026 | 0.044874 | 0.15159 | 0.00036568 | 0.63862 | 0.087203 | 0.35113 | 0.033721 | 0.095418 | 0.028764 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 3.1474 | 0% | CZ 0B | 13.6096 | 0.83455 | 4.3532 | 15.4578 | 0.011738 | 20.4985 | 2.799 | 11.2706 | 1.0824 | 3.0627 | 0.92327 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 122.0401 | 0% | CZ 0B | 3.9887 | 0.24459 | 0.030374 | 0.0013922 | 0.0034401 | 6.0078 | 0.82035 | 3.3032 | 0.31723 | 0.89763 | 0.2706 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 26.7819 | 0% | CZ 0B | 0 | 0 | 0.042495 | 0.15453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.3066 | 0% | CZ 0B | 41.7581 | 2.5606 | 4.9627 | 16.9047 | 0.036015 | 62.8952 | 8.5882 | 34.5816 | 3.321 | 9.3973 | 2.8329 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 313.8915 | 0%
CZ 1A | 0.42437 | 0.026003 | 0.045799 | 0.16528 | 0 | 0.61119 | 0.10159 | 0.34401 | 0.033721 | 0.09021 | 0.028422 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 3.1363 | 2.054% | CZ 1A | 13.6214 | 0.83463 | 4.4476 | 16.8651 | 0 | 19.618 | 3.2608 | 11.042 | 1.0824 | 2.8956 | 0.91228 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 122.7165 | 2.054% | CZ 1A | 3.9922 | 0.24462 | 0.030374 | 0 | 0 | 5.7497 | 0.95568 | 3.2362 | 0.31723 | 0.84864 | 0.26737 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 26.5386 | 2.054% | CZ 1A | 0 | 0 | 0.043439 | 0.16865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32167 | 2.054% | CZ 1A | 41.7943 | 2.5609 | 5.0659 | 18.4335 | 0 | 60.1937 | 10.0051 | 33.8801 | 3.321 | 8.8844 | 2.7991 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 312.9912 | 2.054%
CZ 1B | 0.42422 | 0.025971 | 0.0459 | 0.16776 | 0.001075 | 0.59748 | 0.063323 | 0.35353 | 0.033721 | 0.086116 | 0.028204 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 3.093 | 0% | CZ 1B | 13.6166 | 0.83361 | 4.4579 | 17.0882 | 0.034506 | 19.1779 | 2.0325 | 11.3475 | 1.0824 | 2.7641 | 0.90529 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 121.4774 | 0% | CZ 1B | 3.9908 | 0.24432 | 0.030374 | 0.0039924 | 0.010113 | 5.6207 | 0.5957 | 3.3258 | 0.31723 | 0.81012 | 0.26533 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 26.1111 | 0% | CZ 1B | 0 | 0 | 0.043542 | 0.17075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32386 | 0% | CZ 1B | 41.7798 | 2.5578 | 5.0772 | 18.7043 | 0.10588 | 58.8432 | 6.2364 | 34.8174 | 3.321 | 8.4811 | 2.7777 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 308.7551 | 0%
CZ 2A | 0.42432 | 0.025961 | 0.046921 | 0.20161 | 0.01796 | 0.50864 | 0.074772 | 0.33879 | 0.03017 | 0.086619 | 0.027753 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 3.0492 | 16.55% | CZ 2A | 13.6197 | 0.8333 | 4.562 | 20.3147 | 0.57648 | 16.3263 | 2.4 | 10.8744 | 0.96838 | 2.7803 | 0.89081 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 122.2831 | 16.55% | CZ 2A | 3.9917 | 0.24423 | 0.030374 | 0.034689 | 0.16896 | 4.785 | 0.70341 | 3.1871 | 0.28382 | 0.81486 | 0.26108 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 25.4018 | 16.55% | CZ 2A | 0 | 0 | 0.044584 | 0.20196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.35612 | 16.55% | CZ 2A | 41.7891 | 2.5568 | 5.191 | 22.4377 | 1.7688 | 50.0937 | 7.364 | 33.3658 | 2.9713 | 8.5308 | 2.7333 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 304.8553 | 16.55%
CZ 2B | 0.4245 | 0.025981 | 0.04712 | 0.19194 | 0.13732 | 0.33704 | 0.027721 | 0.36227 | 0.026823 | 0.063475 | 0.027195 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.9371 | 2.4% | CZ 2B | 13.6254 | 0.83392 | 4.5823 | 18.2836 | 4.4077 | 10.8181 | 0.88979 | 11.628 | 0.86097 | 2.0374 | 0.87291 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 116.977 | 2.4% | CZ 2B | 3.9934 | 0.24441 | 0.030374 | 0.17512 | 1.2918 | 3.1706 | 0.26078 | 3.408 | 0.25234 | 0.59713 | 0.25583 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 24.5764 | 2.4% | CZ 2B | 0 | 0 | 0.044787 | 0.17686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.33122 | 2.4% | CZ 2B | 41.8068 | 2.5587 | 5.2132 | 21.1643 | 13.524 | 33.1932 | 2.7301 | 35.678 | 2.6417 | 6.2514 | 2.6783 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 293.4928 | 2.4%
CZ 3A | 0.42451 | 0.025976 | 0.049442 | 0.23811 | 0.075247 | 0.34932 | 0.043005 | 0.34647 | 0.028517 | 0.071491 | 0.026723 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.9445 | 13.96% | CZ 3A | 13.6258 | 0.83377 | 4.8193 | 23.4969 | 2.4153 | 11.2123 | 1.3804 | 11.121 | 0.91534 | 2.2947 | 0.85775 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 121.1092 | 13.96% | CZ 3A | 3.9935 | 0.24436 | 0.030374 | 0.1076 | 0.70787 | 3.2862 | 0.40456 | 3.2594 | 0.26827 | 0.67254 | 0.25139 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 24.1226 | 13.96% | CZ 3A | 0 | 0 | 0.047156 | 0.2313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.38803 | 13.96% | CZ 3A | 41.8077 | 2.5582 | 5.4722 | 26.4073 | 7.4107 | 34.4027 | 4.2354 | 34.1224 | 2.8085 | 7.0408 | 2.6318 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 294.9509 | 13.96%
CZ 3B | 0.42435 | 0.025975 | 0.048763 | 0.19501 | 0.14251 | 0.28223 | 0.024149 | 0.37716 | 0.025931 | 0.058461 | 0.026667 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.8969 | 6.966% | CZ 3B | 13.6206 | 0.83373 | 4.75 | 18.6939 | 4.5744 | 9.0589 | 0.77512 | 12.1061 | 0.83232 | 1.8765 | 0.85595 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 116.1142 | 6.966% | CZ 3B | 3.992 | 0.24435 | 0.030374 | 0.16205 | 1.3407 | 2.655 | 0.22717 | 3.5481 | 0.24394 | 0.54996 | 0.25086 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 24.1411 | 6.966% | CZ 3B | 0 | 0 | 0.046463 | 0.18141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.33745 | 6.966% | CZ 3B | 41.7921 | 2.5581 | 5.3964 | 21.5246 | 14.0354 | 27.7953 | 2.3783 | 37.1449 | 2.5538 | 5.7575 | 2.6263 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 289.6159 | 6.966%
CZ 3C | 0.42422 | 0.025971 | 0.049537 | 0.21606 | 0.032583 | 0.24889 | 0.02018 | 0.34552 | 0 | 0.052524 | 0.026531 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.7077 | 2.177% | CZ 3C | 13.6164 | 0.83361 | 4.829 | 21.7292 | 1.0458 | 7.9888 | 0.64773 | 11.0905 | 0 | 1.6859 | 0.85159 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 112.4554 | 2.177% | CZ 3C | 3.9908 | 0.24432 | 0.030374 | 0.042685 | 0.30652 | 2.3414 | 0.18984 | 3.2504 | 0 | 0.49411 | 0.24959 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 22.0366 | 2.177% | CZ 3C | 0 | 0 | 0.047254 | 0.21584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.37267 | 2.177% | CZ 3C | 41.7792 | 2.5578 | 5.4828 | 24.0377 | 3.2089 | 24.5121 | 1.9874 | 34.0288 | 0 | 5.1728 | 2.6129 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 271.4336 | 2.177%
CZ 4A | 0.424 | 0.025935 | 0.051717 | 0.27789 | 0.11299 | 0.27533 | 0.029459 | 0.35535 | 0.029151 | 0.067111 | 0.026044 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.9407 | 20.37% | CZ 4A | 13.6095 | 0.83247 | 5.0514 | 27.139 | 3.6266 | 8.8374 | 0.94557 | 11.4061 | 0.93568 | 2.1541 | 0.83597 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 123.5106 | 20.37% | CZ 4A | 3.9887 | 0.24398 | 0.030374 | 0.16371 | 1.0629 | 2.5901 | 0.27713 | 3.3429 | 0.27423 | 0.63134 | 0.24501 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.747 | 20.37% | CZ 4A | 0 | 0 | 0.049478 | 0.2658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.42486 | 20.37% | CZ 4A | 41.758 | 2.5543 | 5.7259 | 30.7663 | 11.1274 | 27.1156 | 2.9013 | 34.9971 | 2.8709 | 6.6095 | 2.565 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 295.0444 | 20.37%
CZ 4B | 0.42386 | 0.025955 | 0.050981 | 0.20283 | 0.20038 | 0.20669 | 0.010347 | 0.3975 | 0.025558 | 0.050907 | 0.025964 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.8866 | 0.5664% | CZ 4B | 13.6048 | 0.8331 | 4.9763 | 19.2956 | 6.4317 | 6.6341 | 0.33211 | 12.7588 | 0.82034 | 1.634 | 0.83337 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 116.291 | 0.5664% | CZ 4B | 3.9873 | 0.24417 | 0.030374 | 0.18852 | 1.885 | 1.9444 | 0.097336 | 3.7394 | 0.24043 | 0.4789 | 0.24425 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.9767 | 0.5664% | CZ 4B | 0 | 0 | 0.048727 | 0.18652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.34483 | 0.5664% | CZ 4B | 41.7435 | 2.5562 | 5.6439 | 22.3606 | 19.7342 | 20.3555 | 1.019 | 39.1476 | 2.517 | 5.0136 | 2.557 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 288.7012 | 0.5664%
CZ 4C | 0.42429 | 0.025906 | 0.052389 | 0.25879 | 0.037958 | 0.1494 | 0.0051648 | 0.35949 | 0.025653 | 0.046913 | 0.025635 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.6773 | 2.852% | CZ 4C | 13.6189 | 0.83153 | 5.1199 | 25.7047 | 1.2184 | 4.7955 | 0.16578 | 11.5388 | 0.8234 | 1.5058 | 0.82281 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 114.2823 | 2.852% | CZ 4C | 3.9915 | 0.24371 | 0.030374 | 0.094517 | 0.35708 | 1.4055 | 0.048587 | 3.3818 | 0.24133 | 0.44132 | 0.24115 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 21.3735 | 2.852% | CZ 4C | 0 | 0 | 0.050163 | 0.25382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41356 | 2.852% | CZ 4C | 41.7867 | 2.5514 | 5.8008 | 28.7322 | 3.7383 | 14.7141 | 0.50866 | 35.4044 | 2.5264 | 4.6202 | 2.5246 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 268.9609 | 2.852%
CZ 5A | 0.42404 | 0.025944 | 0.053995 | 0.30324 | 0.12292 | 0.2009 | 0.018318 | 0.3618 | 0.027353 | 0.059878 | 0.025565 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.8897 | 20.94% | CZ 5A | 13.6108 | 0.83275 | 5.2839 | 29.5615 | 3.9454 | 6.4485 | 0.58798 | 11.6132 | 0.87797 | 1.922 | 0.82058 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 123.6413 | 20.94% | CZ 5A | 3.9891 | 0.24406 | 0.030374 | 0.18584 | 1.1563 | 1.8899 | 0.17233 | 3.4036 | 0.25732 | 0.56329 | 0.2405 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.0293 | 20.94% | CZ 5A | 0 | 0 | 0.051802 | 0.28927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.45065 | 20.94% | CZ 5A | 41.7617 | 2.5551 | 5.98 | 33.5632 | 12.1057 | 19.7859 | 1.8041 | 35.6325 | 2.6939 | 5.8971 | 2.5178 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 290.3501 | 20.94%
CZ 5B | 0.42391 | 0.025945 | 0.053302 | 0.23226 | 0.17211 | 0.16717 | 0.0044102 | 0.40026 | 0.026644 | 0.048061 | 0.025526 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.8453 | 5.178% | CZ 5B | 13.6065 | 0.83279 | 5.2131 | 22.308 | 5.5242 | 5.3656 | 0.14156 | 12.8474 | 0.8552 | 1.5427 | 0.81932 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 117.1932 | 5.178% | CZ 5B | 3.9878 | 0.24408 | 0.030374 | 0.18718 | 1.6191 | 1.5726 | 0.041488 | 3.7654 | 0.25065 | 0.45213 | 0.24013 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.2874 | 5.178% | CZ 5B | 0 | 0 | 0.051095 | 0.21669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.37736 | 5.178% | CZ 5B | 41.7486 | 2.5552 | 5.9026 | 25.6442 | 16.9499 | 16.4634 | 0.43434 | 39.4196 | 2.624 | 4.7333 | 2.5139 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 285.0422 | 5.178%
CZ 5C | 0.42428 | 0.025904 | 0.053617 | 0.26899 | 0.034755 | 0.12131 | 0.0045386 | 0.36182 | 0.027152 | 0.042718 | 0.025321 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.6561 | 0.1506% | CZ 5C | 13.6184 | 0.83145 | 5.2453 | 26.5787 | 1.1156 | 3.8938 | 0.14568 | 11.6135 | 0.87153 | 1.3711 | 0.81277 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 114.2348 | 0.1506% | CZ 5C | 3.9913 | 0.24368 | 0.030374 | 0.11688 | 0.32695 | 1.1412 | 0.042697 | 3.4037 | 0.25543 | 0.40186 | 0.23821 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 21.089 | 0.1506% | CZ 5C | 0 | 0 | 0.051417 | 0.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.42279 | 0.1506% | CZ 5C | 41.7852 | 2.5511 | 5.9379 | 29.8383 | 3.4228 | 11.9474 | 0.44699 | 35.6337 | 2.6741 | 4.2071 | 2.4938 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 266.9916 | 0.1506%
CZ 6A | 0.42405 | 0.025932 | 0.055943 | 0.34938 | 0.13861 | 0.19529 | 0.018839 | 0.36562 | 0.028008 | 0.063844 | 0.025466 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.9567 | 4.352% | CZ 6A | 13.611 | 0.83235 | 5.4827 | 34.1592 | 4.4492 | 6.2684 | 0.60471 | 11.7356 | 0.89901 | 2.0493 | 0.8174 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 129.0456 | 4.352% | CZ 6A | 3.9892 | 0.24395 | 0.030374 | 0.20063 | 1.304 | 1.8372 | 0.17723 | 3.4395 | 0.26349 | 0.60061 | 0.23957 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.2223 | 4.352% | CZ 6A | 0 | 0 | 0.05379 | 0.33475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.49811 | 4.352% | CZ 6A | 41.7625 | 2.5539 | 6.1973 | 38.6882 | 13.6515 | 19.2333 | 1.8554 | 36.0083 | 2.7584 | 6.2877 | 2.508 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 297.5576 | 4.352%
CZ 6B | 0.42403 | 0.025913 | 0.055399 | 0.30463 | 0.1847 | 0.1391 | 0.003345 | 0.38625 | 0.027508 | 0.047484 | 0.025221 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.8893 | 0.7088% | CZ 6B | 13.6105 | 0.83177 | 5.4272 | 29.361 | 5.9284 | 4.4648 | 0.10737 | 12.3978 | 0.88296 | 1.5241 | 0.80955 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 123.4821 | 0.7088% | CZ 6B | 3.989 | 0.24378 | 0.030374 | 0.23188 | 1.7375 | 1.3085 | 0.031467 | 3.6336 | 0.25878 | 0.4467 | 0.23726 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.0455 | 0.7088% | CZ 6B | 0 | 0 | 0.053235 | 0.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.44851 | 0.7088% | CZ 6B | 41.7609 | 2.5521 | 6.1366 | 33.6543 | 18.19 | 13.6991 | 0.32943 | 38.0399 | 2.7092 | 4.6765 | 2.4839 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 290.2852 | 0.7088%
CZ 7 | 0.42397 | 0.025898 | 0.058291 | 0.39976 | 0.17941 | 0.15943 | 0.012623 | 0.3687 | 0.028441 | 0.057244 | 0.025194 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 3.0047 | 0.728% | CZ 7 | 13.6087 | 0.83126 | 5.7222 | 39.0581 | 5.7587 | 5.1175 | 0.40517 | 11.8344 | 0.91291 | 1.8374 | 0.80868 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 134.0317 | 0.728% | CZ 7 | 3.9885 | 0.24363 | 0.030374 | 0.2332 | 1.6878 | 1.4999 | 0.11875 | 3.4685 | 0.26756 | 0.53851 | 0.23701 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.2102 | 0.728% | CZ 7 | 0 | 0 | 0.056186 | 0.38262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.54839 | 0.728% | CZ 7 | 41.7553 | 2.5505 | 6.4591 | 44.2622 | 17.6693 | 15.702 | 1.2432 | 36.3112 | 2.8011 | 5.6377 | 2.4813 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 302.926 | 0.728%
CZ 8 | 0.4249 | 0.025754 | 0.061737 | 0.49774 | 0.22865 | 0.090867 | 0.003263 | 0.36603 | 0.02929 | 0.047179 | 0.024775 | 0.30666 | 0.012611 | 0.27812 | 0 | 0.66831 | 3.0659 | 0.05054% | CZ 8 | 13.6384 | 0.82666 | 6.0739 | 48.5971 | 7.3391 | 2.9166 | 0.10474 | 11.7488 | 0.94015 | 1.5144 | 0.79522 | 9.843 | 0.40477 | 16.4378 | 0 | 21.4513 | 142.632 | 0.05054% | CZ 8 | 3.9972 | 0.24228 | 0.030374 | 0.29491 | 2.151 | 0.85482 | 0.030696 | 3.4434 | 0.27554 | 0.44383 | 0.23306 | 2.8848 | 0.11863 | 1.6061 | 0 | 6.287 | 22.8937 | 0.05054% | CZ 8 | 0 | 0 | 0.059702 | 0.47591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64519 | 0.05054% | CZ 8 | 41.8465 | 2.5364 | 6.8435 | 55.1042 | 22.5186 | 8.9491 | 0.32136 | 36.0488 | 2.8847 | 4.6465 | 2.44 | 30.2012 | 1.242 | 28.7914 | 0 | 65.8187 | 310.1929 | 0.05054%
US Weighted | 0.42419 | 0.025952 | 0.050961 | 0.25448 | 0.096107 | 0.30176 | 0.034464 | 0.35742 | 0.027714 | 0.066849 | 0.026374 | 0.30666 | 0.012609 | 0.27812 | 0 | 0.66831 | 2.932 | 100% | US Weighted | 13.6155 | 0.83301 | 4.9742 | 24.9616 | 3.0848 | 9.686 | 1.1062 | 11.4725 | 0.88956 | 2.1457 | 0.84654 | 9.843 | 0.40473 | 16.4378 | 0 | 21.4513 | 121.7524 | 100% | US Weighted | 3.9905 | 0.24414 | 0.030374 | 0.1353 | 0.90411 | 2.8388 | 0.32422 | 3.3624 | 0.26072 | 0.62887 | 0.24811 | 2.8848 | 0.11862 | 1.6061 | 0 | 6.287 | 23.8641 | 100% | US Weighted | 0 | 0 | 0.048706 | 0.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.40328 | 100% | US Weighted | 41.7761 | 2.5559 | 5.6416 | 28.1949 | 9.4652 | 29.7193 | 3.3942 | 35.2008 | 2.7294 | 6.5836 | 2.5974 | 30.2012 | 1.2418 | 28.7914 | 0 | 65.8187 | 293.9117 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.43856 | 0.025995 | 0.044922 | 0.14732 | 0 | 0.82526 | 0.12918 | 0.36627 | 0.033721 | 0.12364 | 0.036102 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.4396 | 0% | CZ 0A | 14.0767 | 0.8344 | 4.3581 | 15.0331 | 0 | 26.489 | 4.1465 | 11.7565 | 1.0824 | 3.9684 | 1.1588 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 131.1346 | 0% | CZ 0A | 4.1256 | 0.24455 | 0.030374 | 0 | 0 | 7.7635 | 1.2153 | 3.4456 | 0.31723 | 1.1631 | 0.33963 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 29.569 | 0% | CZ 0A | 0 | 0 | 0.042544 | 0.15033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30245 | 0% | CZ 0A | 43.1914 | 2.5602 | 4.9681 | 16.4312 | 0 | 81.2757 | 12.7225 | 36.0724 | 3.321 | 12.1763 | 3.5556 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 342.6158 | 0%
CZ 0B | 0.43857 | 0.026 | 0.044874 | 0.15512 | 0.0036911 | 0.69057 | 0.092684 | 0.37498 | 0 | 0.11277 | 0.035985 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.2439 | 0% | CZ 0B | 14.0772 | 0.83455 | 4.3531 | 15.5443 | 0.11848 | 22.1658 | 2.975 | 12.0359 | 0 | 3.6196 | 1.155 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 125.1099 | 0% | CZ 0B | 4.1258 | 0.24459 | 0.030374 | 0.038267 | 0.034723 | 6.4964 | 0.87191 | 3.5275 | 0 | 1.0609 | 0.33852 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 27.6931 | 0% | CZ 0B | 0 | 0 | 0.042495 | 0.15414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.30621 | 0% | CZ 0B | 43.193 | 2.5606 | 4.9627 | 17.2479 | 0.36352 | 68.0112 | 9.1281 | 36.9296 | 0 | 11.1061 | 3.544 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 323.3881 | 0%
CZ 1A | 0.43859 | 0.026003 | 0.045799 | 0.16821 | 0 | 0.62255 | 0.1028 | 0.3594 | 0.033721 | 0.10366 | 0.035596 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.2049 | 2.054% | CZ 1A | 14.0777 | 0.83463 | 4.4476 | 17.1639 | 0 | 19.9826 | 3.2997 | 11.5359 | 1.0824 | 3.3272 | 1.1426 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 125.1249 | 2.054% | CZ 1A | 4.1259 | 0.24462 | 0.030374 | 0 | 0 | 5.8566 | 0.96708 | 3.381 | 0.31723 | 0.97515 | 0.33486 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 27.1569 | 2.054% | CZ 1A | 0 | 0 | 0.043439 | 0.17164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32465 | 2.054% | CZ 1A | 43.1944 | 2.5609 | 5.0659 | 18.7602 | 0 | 61.3125 | 10.1243 | 35.3956 | 3.321 | 10.2089 | 3.5057 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 319.7907 | 2.054%
CZ 1B | 0.43859 | 0.025971 | 0.0459 | 0.18033 | 0.0097377 | 0.64938 | 0.071081 | 0.37356 | 0 | 0.10103 | 0.035376 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.1996 | 0% | CZ 1B | 14.0779 | 0.83361 | 4.4578 | 17.4711 | 0.31256 | 20.8438 | 2.2815 | 11.9906 | 0 | 3.2428 | 1.1355 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 124.878 | 0% | CZ 1B | 4.126 | 0.24432 | 0.030374 | 0.12513 | 0.091606 | 6.109 | 0.66868 | 3.5142 | 0 | 0.9504 | 0.33279 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 27.1167 | 0% | CZ 1B | 0 | 0 | 0.043542 | 0.17044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.32356 | 0% | CZ 1B | 43.1951 | 2.5578 | 5.0771 | 19.9393 | 0.95902 | 63.9548 | 7.0004 | 36.7906 | 0 | 9.9498 | 3.484 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 319.2494 | 0%
CZ 2A | 0.43859 | 0.025961 | 0.04692 | 0.2265 | 0.03533 | 0.53376 | 0.079072 | 0.35158 | 0.030093 | 0.10069 | 0.034882 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.172 | 16.55% | CZ 2A | 14.0777 | 0.8333 | 4.562 | 21.5498 | 1.134 | 17.1325 | 2.538 | 11.285 | 0.9659 | 3.2319 | 1.1196 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 126.6605 | 16.55% | CZ 2A | 4.1259 | 0.24423 | 0.030374 | 0.21015 | 0.33236 | 5.0213 | 0.74386 | 3.3074 | 0.28309 | 0.94721 | 0.32815 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 26.4982 | 16.55% | CZ 2A | 0 | 0 | 0.044583 | 0.20833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.36249 | 16.55% | CZ 2A | 43.1945 | 2.5568 | 5.1909 | 24.9702 | 3.4794 | 52.5675 | 7.7875 | 34.6257 | 2.9637 | 9.9163 | 3.4354 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 317.0292 | 16.55%
CZ 2B | 0.43859 | 0.025981 | 0.047119 | 0.28452 | 0.31755 | 0.36343 | 0.034263 | 0.37752 | 0 | 0.074855 | 0.034316 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.2668 | 2.4% | CZ 2B | 14.0776 | 0.83392 | 4.5822 | 21.7417 | 10.1925 | 11.6654 | 1.0998 | 12.1175 | 0 | 2.4027 | 1.1015 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 128.0455 | 2.4% | CZ 2B | 4.1259 | 0.24441 | 0.030374 | 0.98059 | 2.9873 | 3.4189 | 0.32232 | 3.5514 | 0 | 0.70419 | 0.32282 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 27.6124 | 2.4% | CZ 2B | 0 | 0 | 0.044785 | 0.18396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.33832 | 2.4% | CZ 2B | 43.1942 | 2.5587 | 5.213 | 30.3726 | 31.2737 | 35.7928 | 3.3744 | 37.1799 | 0 | 7.3721 | 3.3796 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 326.0525 | 2.4%
CZ 3A | 0.43862 | 0.025976 | 0.049442 | 0.29313 | 0.12737 | 0.35633 | 0.045286 | 0.35312 | 0.028359 | 0.084397 | 0.033786 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.1044 | 13.96% | CZ 3A | 14.0788 | 0.83377 | 4.8192 | 25.9035 | 4.0884 | 11.4375 | 1.4536 | 11.3344 | 0.91028 | 2.709 | 1.0845 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 126.8835 | 13.96% | CZ 3A | 4.1263 | 0.24436 | 0.030374 | 0.53905 | 1.1982 | 3.3521 | 0.42602 | 3.3219 | 0.26679 | 0.79395 | 0.31784 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 25.541 | 13.96% | CZ 3A | 0 | 0 | 0.047156 | 0.24064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.39737 | 13.96% | CZ 3A | 43.1977 | 2.5582 | 5.4721 | 31.9455 | 12.5443 | 35.0935 | 4.46 | 34.7771 | 2.793 | 8.3119 | 3.3274 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 310.8222 | 13.96%
CZ 3B | 0.43858 | 0.025975 | 0.048764 | 0.28097 | 0.30192 | 0.29929 | 0.029431 | 0.38668 | 0 | 0.069162 | 0.033744 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.1831 | 6.966% | CZ 3B | 14.0774 | 0.83373 | 4.7501 | 22.0365 | 9.6911 | 9.6067 | 0.94467 | 12.4117 | 0 | 2.22 | 1.0831 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 125.8858 | 6.966% | CZ 3B | 4.1258 | 0.24435 | 0.030374 | 0.89223 | 2.8403 | 2.8156 | 0.27687 | 3.6377 | 0 | 0.65063 | 0.31745 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 26.7554 | 6.966% | CZ 3B | 0 | 0 | 0.046464 | 0.18992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.34596 | 6.966% | CZ 3B | 43.1935 | 2.5581 | 5.3966 | 30.0993 | 29.7351 | 29.4761 | 2.8985 | 38.0828 | 0 | 6.8115 | 3.3233 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 317.9162 | 6.966%
CZ 3C | 0.43858 | 0.025971 | 0.049537 | 0.24946 | 0.059512 | 0.24517 | 0.023109 | 0.35931 | 0 | 0.061984 | 0.033563 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 2.8148 | 2.177% | CZ 3C | 14.0774 | 0.83361 | 4.829 | 23.4614 | 1.9102 | 7.8694 | 0.74175 | 11.533 | 0 | 1.9896 | 1.0773 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 116.5535 | 2.177% | CZ 3C | 4.1259 | 0.24432 | 0.030374 | 0.26811 | 0.55985 | 2.3064 | 0.21739 | 3.3801 | 0 | 0.58311 | 0.31574 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 22.9554 | 2.177% | CZ 3C | 0 | 0 | 0.047253 | 0.22547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.3823 | 2.177% | CZ 3C | 43.1936 | 2.5578 | 5.4828 | 27.4503 | 5.8611 | 24.1455 | 2.2759 | 35.3867 | 0 | 6.1045 | 3.3055 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 282.1051 | 2.177%
CZ 4A | 0.43858 | 0.025935 | 0.051722 | 0.35369 | 0.17151 | 0.28587 | 0.031207 | 0.35968 | 0.02913 | 0.079241 | 0.033068 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.1283 | 20.37% | CZ 4A | 14.0775 | 0.83247 | 5.0519 | 30.3752 | 5.5051 | 9.1759 | 1.0017 | 11.545 | 0.93501 | 2.5435 | 1.0614 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 130.3354 | 20.37% | CZ 4A | 4.1259 | 0.24398 | 0.030374 | 0.7687 | 1.6134 | 2.6893 | 0.29357 | 3.3837 | 0.27404 | 0.74545 | 0.31108 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 25.4036 | 20.37% | CZ 4A | 0 | 0 | 0.049483 | 0.27752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.43658 | 20.37% | CZ 4A | 43.1938 | 2.5543 | 5.7264 | 38.3809 | 16.8912 | 28.1544 | 3.0734 | 35.4235 | 2.8689 | 7.8041 | 3.2567 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 313.6689 | 20.37%
CZ 4B | 0.43855 | 0.025955 | 0.050985 | 0.30188 | 0.38088 | 0.21835 | 0.01537 | 0.40355 | 0 | 0.060585 | 0.032997 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.1977 | 0.5664% | CZ 4B | 14.0767 | 0.8331 | 4.9767 | 23.4728 | 12.2254 | 7.0085 | 0.49334 | 12.9531 | 0 | 1.9446 | 1.0591 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 127.2742 | 0.5664% | CZ 4B | 4.1256 | 0.24417 | 0.030374 | 0.98611 | 3.583 | 2.0541 | 0.14459 | 3.7963 | 0 | 0.56994 | 0.31042 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 26.7688 | 0.5664% | CZ 4B | 0 | 0 | 0.048731 | 0.20108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.35939 | 0.5664% | CZ 4B | 43.1912 | 2.5562 | 5.6443 | 32.3018 | 37.5109 | 21.5042 | 1.5137 | 39.7439 | 0 | 5.9667 | 3.2497 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 319.5242 | 0.5664%
CZ 4C | 0.43862 | 0.025906 | 0.052387 | 0.35299 | 0.099711 | 0.15502 | 0.0079191 | 0.36373 | 0 | 0.056773 | 0.032618 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 2.8543 | 2.852% | CZ 4C | 14.0787 | 0.83153 | 5.1197 | 30.6583 | 3.2005 | 4.9757 | 0.25419 | 11.6751 | 0 | 1.8223 | 1.047 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 121.8938 | 2.852% | CZ 4C | 4.1262 | 0.24371 | 0.030374 | 0.72108 | 0.93801 | 1.4583 | 0.074497 | 3.4218 | 0 | 0.53408 | 0.30685 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 22.779 | 2.852% | CZ 4C | 0 | 0 | 0.050161 | 0.28198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.44172 | 2.852% | CZ 4C | 43.1976 | 2.5514 | 5.8006 | 38.3694 | 9.8201 | 15.2669 | 0.77991 | 35.8225 | 0 | 5.5913 | 3.2124 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 286.7534 | 2.852%
CZ 5A | 0.43859 | 0.025944 | 0.053996 | 0.39013 | 0.19366 | 0.21384 | 0.018784 | 0.36555 | 0.027134 | 0.071176 | 0.032562 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.1 | 20.94% | CZ 5A | 14.0776 | 0.83275 | 5.2839 | 33.1895 | 6.216 | 6.8637 | 0.60294 | 11.7333 | 0.87094 | 2.2846 | 1.0452 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 131.2313 | 20.94% | CZ 5A | 4.1259 | 0.24406 | 0.030374 | 0.89032 | 1.8218 | 2.0116 | 0.17671 | 3.4388 | 0.25526 | 0.66958 | 0.30632 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 24.895 | 20.94% | CZ 5A | 0 | 0 | 0.051803 | 0.30152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.4629 | 20.94% | CZ 5A | 43.1942 | 2.5551 | 5.98 | 42.2767 | 19.0725 | 21.0599 | 1.85 | 36.0011 | 2.6723 | 7.0098 | 3.2069 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 311.2199 | 20.94%
CZ 5B | 0.43857 | 0.025945 | 0.053301 | 0.35787 | 0.3663 | 0.18191 | 0.0096594 | 0.40797 | 0 | 0.056972 | 0.032535 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.1996 | 5.178% | CZ 5B | 14.0771 | 0.83279 | 5.213 | 28.1725 | 11.7573 | 5.839 | 0.31005 | 13.0948 | 0 | 1.8287 | 1.0443 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 130.4003 | 5.178% | CZ 5B | 4.1258 | 0.24408 | 0.030374 | 1.1224 | 3.4459 | 1.7113 | 0.09087 | 3.8379 | 0 | 0.53596 | 0.30607 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 26.3747 | 5.178% | CZ 5B | 0 | 0 | 0.051094 | 0.24343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.4041 | 5.178% | CZ 5B | 43.1927 | 2.5552 | 5.9026 | 38.3573 | 36.0748 | 17.9156 | 0.95131 | 40.1787 | 0 | 5.6109 | 3.2042 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 320.2847 | 5.178%
CZ 5C | 0.43863 | 0.025904 | 0.053619 | 0.37724 | 0.10123 | 0.12719 | 0.0078408 | 0.36781 | 0 | 0.05226 | 0.032284 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 2.8526 | 0.1506% | CZ 5C | 14.0792 | 0.83145 | 5.2455 | 32.4331 | 3.2492 | 4.0827 | 0.25167 | 11.8061 | 0 | 1.6774 | 1.0363 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 122.9233 | 0.1506% | CZ 5C | 4.1264 | 0.24368 | 0.030374 | 0.81515 | 0.95229 | 1.1966 | 0.073761 | 3.4602 | 0 | 0.49163 | 0.30371 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 22.6178 | 0.1506% | CZ 5C | 0 | 0 | 0.051419 | 0.29652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.45751 | 0.1506% | CZ 5C | 43.1989 | 2.5511 | 5.938 | 40.9432 | 9.9695 | 12.5268 | 0.77221 | 36.2244 | 0 | 5.1468 | 3.1795 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 286.792 | 0.1506%
CZ 6A | 0.43859 | 0.025932 | 0.055942 | 0.49291 | 0.21232 | 0.22914 | 0.020402 | 0.3691 | 0.027863 | 0.077002 | 0.03246 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.2503 | 4.352% | CZ 6A | 14.0777 | 0.83235 | 5.4825 | 43.5495 | 6.815 | 7.3549 | 0.65488 | 11.8474 | 0.89434 | 2.4716 | 1.0419 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 143.253 | 4.352% | CZ 6A | 4.1259 | 0.24395 | 0.030374 | 0.90747 | 1.9974 | 2.1556 | 0.19193 | 3.4723 | 0.26212 | 0.72438 | 0.30536 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 25.3409 | 4.352% | CZ 6A | 0 | 0 | 0.053789 | 0.40453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.5679 | 4.352% | CZ 6A | 43.1945 | 2.5539 | 6.1971 | 53.7156 | 20.9105 | 22.567 | 2.0093 | 36.3514 | 2.7441 | 7.5835 | 3.1969 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 327.3653 | 4.352%
CZ 6B | 0.4386 | 0.025913 | 0.055401 | 0.47247 | 0.3394 | 0.16438 | 0.0066043 | 0.38973 | 0.027319 | 0.05835 | 0.032207 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.279 | 0.7088% | CZ 6B | 14.078 | 0.83177 | 5.4273 | 39.0757 | 10.8941 | 5.2762 | 0.21198 | 12.5096 | 0.87687 | 1.8729 | 1.0338 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 140.319 | 0.7088% | CZ 6B | 4.126 | 0.24378 | 0.030374 | 1.2287 | 3.1929 | 1.5464 | 0.062129 | 3.6664 | 0.257 | 0.54892 | 0.30298 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 26.1297 | 0.7088% | CZ 6B | 0 | 0 | 0.053236 | 0.34883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.51165 | 0.7088% | CZ 6B | 43.1954 | 2.5521 | 6.1367 | 50.991 | 33.4262 | 16.1889 | 0.65043 | 38.3831 | 2.6905 | 5.7467 | 3.1719 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 329.4744 | 0.7088%
CZ 7 | 0.43859 | 0.025898 | 0.058292 | 0.56475 | 0.25968 | 0.19445 | 0.013528 | 0.3689 | 0.028353 | 0.069242 | 0.032177 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.3225 | 0.728% | CZ 7 | 14.0778 | 0.83126 | 5.7223 | 49.9349 | 8.3353 | 6.2413 | 0.43422 | 11.8408 | 0.91008 | 2.2225 | 1.0328 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 149.814 | 0.728% | CZ 7 | 4.126 | 0.24363 | 0.030374 | 1.0347 | 2.4429 | 1.8292 | 0.12726 | 3.4703 | 0.26673 | 0.65138 | 0.3027 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 25.4494 | 0.728% | CZ 7 | 0 | 0 | 0.056187 | 0.46405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.62981 | 0.728% | CZ 7 | 43.1947 | 2.5505 | 6.4592 | 61.5524 | 25.575 | 19.1502 | 1.3323 | 36.3309 | 2.7924 | 6.8193 | 3.1689 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 335.2674 | 0.728%
CZ 8 | 0.43884 | 0.025754 | 0.06174 | 0.711 | 0.31831 | 0.13007 | 0.0068012 | 0.3646 | 0.02924 | 0.058286 | 0.031736 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.445 | 0.05054% | CZ 8 | 14.0859 | 0.82666 | 6.0742 | 63.0912 | 10.217 | 4.1749 | 0.21831 | 11.7028 | 0.93854 | 1.8708 | 1.0187 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 162.4498 | 0.05054% | CZ 8 | 4.1283 | 0.24228 | 0.030374 | 1.2724 | 2.9944 | 1.2236 | 0.063982 | 3.4299 | 0.27507 | 0.54831 | 0.29855 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 25.4313 | 0.05054% | CZ 8 | 0 | 0 | 0.059706 | 0.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.75678 | 0.05054% | CZ 8 | 43.2197 | 2.5364 | 6.8438 | 77.534 | 31.3488 | 12.8099 | 0.66982 | 35.9075 | 2.8797 | 5.7403 | 3.1256 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 348.9568 | 0.05054%
US Weighted | 0.43859 | 0.025952 | 0.050961 | 0.32757 | 0.16688 | 0.31666 | 0.037045 | 0.36452 | 0.022874 | 0.07887 | 0.03342 | 0.30733 | 0.012693 | 0.27812 | 0 | 0.67048 | 3.132 | 100% | US Weighted | 14.0778 | 0.83301 | 4.9743 | 28.322 | 5.3565 | 10.164 | 1.1891 | 11.7002 | 0.7342 | 2.5316 | 1.0727 | 9.8645 | 0.4074 | 16.4378 | 0 | 21.5211 | 129.1862 | 100% | US Weighted | 4.126 | 0.24414 | 0.030374 | 0.68644 | 1.5699 | 2.9789 | 0.34849 | 3.4291 | 0.21518 | 0.74196 | 0.3144 | 2.8911 | 0.1194 | 1.6061 | 0 | 6.3075 | 25.609 | 100% | US Weighted | 0 | 0 | 0.048707 | 0.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.41808 | 100% | US Weighted | 43.1947 | 2.5559 | 5.6416 | 35.5823 | 16.4353 | 31.1861 | 3.6484 | 35.8997 | 2.2527 | 7.7676 | 3.2914 | 30.2671 | 1.25 | 28.7914 | 0 | 66.0329 | 313.7972 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.51158 | 0.032019 | 0.045501 | 0.32031 | 0 | 1.2226 | 0.26548 | 0.5493 | 0 | 0.23541 | 0.036132 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.518 | 0% | CZ 0A | 16.4205 | 1.0277 | 4.3984 | 32.6847 | 0 | 39.2442 | 8.5213 | 17.6314 | 0 | 7.5562 | 1.1598 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 177.8709 | 0% | CZ 0A | 4.8126 | 0.30121 | 0.032905 | 0 | 0 | 11.5018 | 2.4975 | 5.1675 | 0 | 2.2146 | 0.3399 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 38.084 | 0% | CZ 0A | 0 | 0 | 0.042861 | 0.32685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.47928 | 0% | CZ 0A | 50.3828 | 3.1534 | 5.0292 | 35.7244 | 0 | 120.4126 | 26.1459 | 54.0981 | 0 | 23.1846 | 3.5585 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 451.0868 | 0%
CZ 0B | 0.51158 | 0.032025 | 0.045451 | 0.32239 | 0.0034673 | 0.93458 | 0.20967 | 0.56146 | 0 | 0.2161 | 0.035991 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.1724 | 0% | CZ 0B | 16.4205 | 1.0279 | 4.3932 | 32.5317 | 0.11129 | 29.998 | 6.73 | 18.0217 | 0 | 6.9362 | 1.1552 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 166.5526 | 0% | CZ 0B | 4.8126 | 0.30127 | 0.032905 | 0.049059 | 0.032618 | 8.7919 | 1.9725 | 5.2818 | 0 | 2.0329 | 0.33858 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 34.8622 | 0% | CZ 0B | 0 | 0 | 0.04281 | 0.32364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.47603 | 0% | CZ 0B | 50.3828 | 3.154 | 5.0236 | 35.8878 | 0.34148 | 92.0427 | 20.6497 | 55.2956 | 0 | 21.2823 | 3.5446 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 417.002 | 0%
CZ 1A | 0.51158 | 0.032029 | 0.04638 | 0.35122 | 0 | 0.87203 | 0.22609 | 0.52721 | 0 | 0.20018 | 0.035597 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.102 | 2.054% | CZ 1A | 16.4205 | 1.028 | 4.4879 | 35.8392 | 0 | 27.9902 | 7.2569 | 16.9222 | 0 | 6.4255 | 1.1426 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 166.7398 | 2.054% | CZ 1A | 4.8126 | 0.3013 | 0.032917 | 0 | 0 | 8.2034 | 2.1269 | 4.9596 | 0 | 1.8832 | 0.33488 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 33.8709 | 2.054% | CZ 1A | 0 | 0 | 0.043756 | 0.35839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.51172 | 2.054% | CZ 1A | 50.3828 | 3.1543 | 5.1271 | 39.1723 | 0 | 85.8819 | 22.2664 | 51.9221 | 0 | 19.7153 | 3.5058 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 410.5254 | 2.054%
CZ 1B | 0.51158 | 0.031988 | 0.046446 | 0.33331 | 0.0096729 | 0.79143 | 0.15586 | 0.56052 | 0 | 0.18792 | 0.035378 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9637 | 0% | CZ 1B | 16.4205 | 1.0268 | 4.4948 | 32.6817 | 0.31048 | 25.4032 | 5.0027 | 17.9915 | 0 | 6.0317 | 1.1356 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 159.7256 | 0% | CZ 1B | 4.8126 | 0.30092 | 0.032905 | 0.17882 | 0.090996 | 7.4453 | 1.4662 | 5.273 | 0 | 1.7678 | 0.33282 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 32.9173 | 0% | CZ 1B | 0 | 0 | 0.043825 | 0.32072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.47412 | 0% | CZ 1B | 50.3828 | 3.1504 | 5.1346 | 36.9263 | 0.95264 | 77.9443 | 15.3498 | 55.203 | 0 | 18.507 | 3.4843 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 396.4325 | 0%
CZ 2A | 0.51158 | 0.031977 | 0.047481 | 0.42705 | 0.039855 | 0.7962 | 0.1771 | 0.5261 | 0 | 0.199 | 0.034911 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.0909 | 16.55% | CZ 2A | 16.4205 | 1.0264 | 4.6003 | 41.2291 | 1.2792 | 25.5562 | 5.6845 | 16.8866 | 0 | 6.3875 | 1.1206 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 169.4177 | 16.55% | CZ 2A | 4.8126 | 0.30082 | 0.032917 | 0.3158 | 0.37493 | 7.4901 | 1.666 | 4.9492 | 0 | 1.8721 | 0.32842 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 33.3589 | 16.55% | CZ 2A | 0 | 0 | 0.04488 | 0.40152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.55597 | 16.55% | CZ 2A | 50.3828 | 3.1493 | 5.25 | 47.1918 | 3.9251 | 78.4138 | 17.4417 | 51.8129 | 0 | 19.5988 | 3.4382 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 410.0019 | 16.55%
CZ 2B | 0.51158 | 0.032 | 0.047662 | 0.50063 | 0.33198 | 0.55635 | 0.084194 | 0.5469 | 0 | 0.14571 | 0.034321 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.091 | 2.4% | CZ 2B | 16.4205 | 1.0271 | 4.6187 | 40.3415 | 10.6558 | 17.8575 | 2.7025 | 17.5545 | 0 | 4.677 | 1.1016 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 166.1834 | 2.4% | CZ 2B | 4.8126 | 0.30104 | 0.032917 | 1.4449 | 3.123 | 5.2337 | 0.79204 | 5.1449 | 0 | 1.3707 | 0.32286 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 33.7948 | 2.4% | CZ 2B | 0 | 0 | 0.045064 | 0.35411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.50875 | 2.4% | CZ 2B | 50.3828 | 3.1516 | 5.2701 | 53.8315 | 32.695 | 54.792 | 8.2919 | 53.8621 | 0 | 14.3503 | 3.3801 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 409.4049 | 2.4%
CZ 3A | 0.51158 | 0.031994 | 0.04995 | 0.52259 | 0.15294 | 0.59218 | 0.10981 | 0.52807 | 0 | 0.16853 | 0.033822 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.0011 | 13.96% | CZ 3A | 16.4205 | 1.0269 | 4.8522 | 47.3049 | 4.9091 | 19.0077 | 3.5248 | 16.9499 | 0 | 5.4095 | 1.0856 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 169.7179 | 13.96% | CZ 3A | 4.8126 | 0.30098 | 0.032917 | 0.80974 | 1.4388 | 5.5708 | 1.033 | 4.9677 | 0 | 1.5854 | 0.31817 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 32.0862 | 13.96% | CZ 3A | 0 | 0 | 0.047399 | 0.44542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.6024 | 13.96% | CZ 3A | 50.3828 | 3.151 | 5.5254 | 57.1616 | 15.0626 | 58.3211 | 10.815 | 52.0072 | 0 | 16.5978 | 3.3309 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 401.7528 | 13.96%
CZ 3B | 0.51158 | 0.031993 | 0.049303 | 0.48991 | 0.32513 | 0.43277 | 0.06998 | 0.55209 | 0 | 0.13378 | 0.033735 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9299 | 6.966% | CZ 3B | 16.4205 | 1.0269 | 4.7862 | 40.1879 | 10.4361 | 13.891 | 2.2462 | 17.7209 | 0 | 4.294 | 1.0828 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 161.3192 | 6.966% | CZ 3B | 4.8126 | 0.30097 | 0.032917 | 1.3184 | 3.0586 | 4.0712 | 0.65833 | 5.1937 | 0 | 1.2585 | 0.31735 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 32.2387 | 6.966% | CZ 3B | 0 | 0 | 0.046738 | 0.35689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.51321 | 6.966% | CZ 3B | 50.3828 | 3.1509 | 5.4531 | 52.8112 | 32.0209 | 42.6216 | 6.892 | 54.3727 | 0 | 13.1753 | 3.3224 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 393.6005 | 6.966%
CZ 3C | 0.51158 | 0.031988 | 0.050044 | 0.48064 | 0.064441 | 0.37094 | 0.064625 | 0.52374 | 0 | 0.12706 | 0.033563 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.5583 | 2.177% | CZ 3C | 16.4205 | 1.0268 | 4.8618 | 46.0332 | 2.0684 | 11.9064 | 2.0743 | 16.8108 | 0 | 4.0783 | 1.0773 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 155.5846 | 2.177% | CZ 3C | 4.8126 | 0.30092 | 0.032917 | 0.40507 | 0.60622 | 3.4896 | 0.60795 | 4.927 | 0 | 1.1953 | 0.31574 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 27.9093 | 2.177% | CZ 3C | 0 | 0 | 0.047495 | 0.44651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.60358 | 2.177% | CZ 3C | 50.3828 | 3.1504 | 5.5358 | 53.0443 | 6.3465 | 36.5324 | 6.3646 | 51.5805 | 0 | 12.5133 | 3.3055 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 358.1535 | 2.177%
CZ 4A | 0.51158 | 0.031945 | 0.052178 | 0.63114 | 0.21653 | 0.47574 | 0.077897 | 0.51456 | 0 | 0.15385 | 0.033099 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9982 | 20.37% | CZ 4A | 16.4205 | 1.0254 | 5.0796 | 55.8246 | 6.95 | 15.2702 | 2.5003 | 16.5161 | 0 | 4.9383 | 1.0624 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 174.8142 | 20.37% | CZ 4A | 4.8126 | 0.30052 | 0.032917 | 1.1536 | 2.0369 | 4.4755 | 0.7328 | 4.8406 | 0 | 1.4473 | 0.31137 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.3602 | 20.37% | CZ 4A | 0 | 0 | 0.049673 | 0.51888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.67813 | 20.37% | CZ 4A | 50.3828 | 3.1462 | 5.7739 | 68.7915 | 21.3246 | 46.8535 | 7.6717 | 50.6762 | 0 | 15.152 | 3.2597 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 402.4296 | 20.37%
CZ 4B | 0.51158 | 0.03197 | 0.051471 | 0.51669 | 0.41675 | 0.31462 | 0.039218 | 0.563 | 0 | 0.11281 | 0.032989 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.8907 | 0.5664% | CZ 4B | 16.4205 | 1.0262 | 5.0074 | 41.9833 | 13.3766 | 10.0987 | 1.2588 | 18.071 | 0 | 3.6211 | 1.0589 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 161.1492 | 0.5664% | CZ 4B | 4.8126 | 0.30075 | 0.032917 | 1.4445 | 3.9205 | 2.9598 | 0.36893 | 5.2963 | 0 | 1.0613 | 0.31034 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.7239 | 0.5664% | CZ 4B | 0 | 0 | 0.048951 | 0.37055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.52907 | 0.5664% | CZ 4B | 50.3828 | 3.1486 | 5.695 | 55.6232 | 41.0434 | 30.9857 | 3.8624 | 55.447 | 0 | 11.1106 | 3.2489 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 389.9448 | 0.5664%
CZ 4C | 0.51158 | 0.031909 | 0.052857 | 0.59308 | 0.11482 | 0.23801 | 0.023065 | 0.5189 | 0 | 0.10901 | 0.032617 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.5255 | 2.852% | CZ 4C | 16.4205 | 1.0242 | 5.1489 | 52.4478 | 3.6856 | 7.6395 | 0.74034 | 16.6556 | 0 | 3.499 | 1.0469 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 157.5352 | 2.852% | CZ 4C | 4.8126 | 0.30018 | 0.032917 | 1.0855 | 1.0802 | 2.239 | 0.21698 | 4.8815 | 0 | 1.0255 | 0.30684 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 27.1972 | 2.852% | CZ 4C | 0 | 0 | 0.050366 | 0.48744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64738 | 2.852% | CZ 4C | 50.3828 | 3.1425 | 5.8496 | 64.6415 | 11.3085 | 23.4401 | 2.2716 | 51.1043 | 0 | 10.7361 | 3.2123 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 355.4867 | 2.852%
CZ 5A | 0.51158 | 0.031955 | 0.054408 | 0.69209 | 0.2586 | 0.33194 | 0.05055 | 0.52229 | 0 | 0.13318 | 0.032554 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9188 | 20.94% | CZ 5A | 16.4205 | 1.0257 | 5.3071 | 60.8116 | 8.3003 | 10.6547 | 1.6225 | 16.7642 | 0 | 4.2748 | 1.0449 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 175.4532 | 20.94% | CZ 5A | 4.8126 | 0.30061 | 0.032917 | 1.3194 | 2.4327 | 3.1227 | 0.47554 | 4.9133 | 0 | 1.2529 | 0.30625 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 30.1849 | 20.94% | CZ 5A | 0 | 0 | 0.051948 | 0.5631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.72462 | 20.94% | CZ 5A | 50.3828 | 3.1471 | 6.0225 | 75.3595 | 25.4678 | 32.6916 | 4.9784 | 51.4375 | 0 | 13.1163 | 3.2061 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 395.2072 | 20.94%
CZ 5B | 0.51158 | 0.031956 | 0.05373 | 0.58859 | 0.41884 | 0.29844 | 0.028903 | 0.56456 | 0 | 0.10802 | 0.032537 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9368 | 5.178% | CZ 5B | 16.4205 | 1.0257 | 5.238 | 47.8338 | 13.4438 | 9.5794 | 0.92771 | 18.1211 | 0 | 3.4672 | 1.0444 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 166.3284 | 5.178% | CZ 5B | 4.8126 | 0.30062 | 0.032917 | 1.6445 | 3.9402 | 2.8076 | 0.2719 | 5.311 | 0 | 1.0162 | 0.30609 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.6595 | 5.178% | CZ 5B | 0 | 0 | 0.051256 | 0.42223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.58306 | 5.178% | CZ 5B | 50.3828 | 3.1472 | 5.9469 | 63.3658 | 41.2496 | 29.3923 | 2.8465 | 55.6008 | 0 | 10.6384 | 3.2045 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 395.1723 | 5.178%
CZ 5C | 0.51158 | 0.031906 | 0.054073 | 0.62304 | 0.12018 | 0.203 | 0.014028 | 0.51868 | 0 | 0.098712 | 0.032284 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.5071 | 0.1506% | CZ 5C | 16.4205 | 1.0241 | 5.2729 | 54.3854 | 3.8576 | 6.5158 | 0.45027 | 16.6485 | 0 | 3.1684 | 1.0363 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 158.0065 | 0.1506% | CZ 5C | 4.8126 | 0.30015 | 0.032917 | 1.2361 | 1.1306 | 1.9097 | 0.13197 | 4.8794 | 0 | 0.92861 | 0.30371 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 26.8817 | 0.1506% | CZ 5C | 0 | 0 | 0.051606 | 0.50168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.66286 | 0.1506% | CZ 5C | 50.3828 | 3.1423 | 5.9851 | 67.7741 | 11.8363 | 19.9923 | 1.3816 | 51.0825 | 0 | 9.7216 | 3.1795 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 353.8756 | 0.1506%
CZ 6A | 0.51158 | 0.031941 | 0.056334 | 0.8252 | 0.3093 | 0.33817 | 0.054866 | 0.52572 | 0 | 0.14168 | 0.032405 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.1268 | 4.352% | CZ 6A | 16.4205 | 1.0252 | 5.5036 | 74.2398 | 9.9277 | 10.8544 | 1.7611 | 16.8744 | 0 | 4.5477 | 1.0401 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 191.4213 | 4.352% | CZ 6A | 4.8126 | 0.30048 | 0.032928 | 1.3402 | 2.9096 | 3.1813 | 0.51614 | 4.9456 | 0 | 1.3328 | 0.30485 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 30.8926 | 4.352% | CZ 6A | 0 | 0 | 0.053912 | 0.69667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.86016 | 4.352% | CZ 6A | 50.3828 | 3.1457 | 6.2373 | 90.1767 | 30.4611 | 33.3046 | 5.4035 | 51.7755 | 0 | 13.9535 | 3.1914 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 417.4296 | 4.352%
CZ 6B | 0.51158 | 0.031917 | 0.055799 | 0.77526 | 0.43869 | 0.26998 | 0.020609 | 0.54362 | 0 | 0.1108 | 0.032175 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.0901 | 0.7088% | CZ 6B | 16.4205 | 1.0245 | 5.4489 | 65.5457 | 14.0809 | 8.6658 | 0.66151 | 17.449 | 0 | 3.5565 | 1.0328 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 183.1129 | 0.7088% | CZ 6B | 4.8126 | 0.30026 | 0.032928 | 1.8241 | 4.1269 | 2.5398 | 0.19388 | 5.114 | 0 | 1.0424 | 0.30268 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.5055 | 0.7088% | CZ 6B | 0 | 0 | 0.053366 | 0.59322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.75616 | 0.7088% | CZ 6B | 50.3828 | 3.1434 | 6.1776 | 83.9353 | 43.2042 | 26.5892 | 2.0297 | 53.5386 | 0 | 10.9124 | 3.1688 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 412.4795 | 0.7088%
CZ 7 | 0.51158 | 0.031898 | 0.058642 | 0.93322 | 0.38536 | 0.29374 | 0.037855 | 0.52455 | 0 | 0.12572 | 0.032093 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.2343 | 0.728% | CZ 7 | 16.4205 | 1.0238 | 5.739 | 83.8433 | 12.3692 | 9.4284 | 1.2151 | 16.8368 | 0 | 4.0352 | 1.0301 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 201.1682 | 0.728% | CZ 7 | 4.8126 | 0.30007 | 0.03294 | 1.531 | 3.6252 | 2.7633 | 0.35612 | 4.9346 | 0 | 1.1827 | 0.30191 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.0565 | 0.728% | CZ 7 | 0 | 0 | 0.056266 | 0.78619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.95204 | 0.728% | CZ 7 | 50.3828 | 3.1415 | 6.4947 | 101.9594 | 37.9524 | 28.929 | 3.7282 | 51.6602 | 0 | 12.3813 | 3.1607 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 429.1876 | 0.728%
CZ 8 | 0.51158 | 0.031722 | 0.062053 | 1.1553 | 0.49287 | 0.20343 | 0.013909 | 0.51811 | 0 | 0.10482 | 0.031576 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.4251 | 0.05054% | CZ 8 | 16.4205 | 1.0182 | 6.087 | 103.8399 | 15.82 | 6.5296 | 0.44646 | 16.6303 | 0 | 3.3644 | 1.0135 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 220.3966 | 0.05054% | CZ 8 | 4.8126 | 0.29842 | 0.032951 | 1.8901 | 4.6366 | 1.9137 | 0.13085 | 4.8741 | 0 | 0.98605 | 0.29705 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.0884 | 0.05054% | CZ 8 | 0 | 0 | 0.059745 | 0.97391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 1.1432 | 0.05054% | CZ 8 | 50.3828 | 3.1241 | 6.8751 | 126.2355 | 48.5403 | 20.0347 | 1.3699 | 51.0266 | 0 | 10.3229 | 3.1098 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 450.4192 | 0.05054%
US Weighted | 0.51158 | 0.031966 | 0.05144 | 0.58097 | 0.20535 | 0.49352 | 0.089247 | 0.52758 | 0 | 0.15279 | 0.033431 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9775 | 100% | US Weighted | 16.4205 | 1.026 | 5.0042 | 51.688 | 6.5912 | 15.8408 | 2.8646 | 16.9342 | 0 | 4.9041 | 1.0731 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 171.5735 | 100% | US Weighted | 4.8126 | 0.30071 | 0.032918 | 1.0214 | 1.9318 | 4.6427 | 0.83958 | 4.9631 | 0 | 1.4373 | 0.3145 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.5126 | 100% | US Weighted | 0 | 0 | 0.048919 | 0.48203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64052 | 100% | US Weighted | 50.3828 | 3.1481 | 5.6915 | 63.379 | 20.2238 | 48.6041 | 8.7895 | 51.9591 | 0 | 15.0471 | 3.2925 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 399.915 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 241501 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.51158 | 0.032019 | 0.0455 | 0.31781 | 0 | 1.1432 | 0.24847 | 0.56957 | 0 | 0.22095 | 0.036142 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.4249 | 0% | CZ 0A | 16.4205 | 1.0277 | 4.3982 | 32.4297 | 0 | 36.6954 | 7.9754 | 18.282 | 0 | 7.092 | 1.1601 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 174.7077 | 0% | CZ 0A | 4.8126 | 0.30121 | 0.032905 | 0 | 0 | 10.7548 | 2.3375 | 5.3581 | 0 | 2.0785 | 0.34 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 37.2317 | 0% | CZ 0A | 0 | 0 | 0.04286 | 0.3243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.47673 | 0% | CZ 0A | 50.3828 | 3.1534 | 5.029 | 35.4456 | 0 | 112.592 | 24.4709 | 56.0944 | 0 | 21.7601 | 3.5594 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 441.8852 | 0%
CZ 0B | 0.51158 | 0.032025 | 0.045451 | 0.32298 | 0.0034526 | 0.89875 | 0.20029 | 0.57802 | 0 | 0.20617 | 0.036005 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.1344 | 0% | CZ 0B | 16.4205 | 1.0279 | 4.3932 | 32.5914 | 0.11082 | 28.8479 | 6.4288 | 18.5531 | 0 | 6.6175 | 1.1557 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 165.3735 | 0% | CZ 0B | 4.8126 | 0.30127 | 0.032905 | 0.04914 | 0.03248 | 8.4549 | 1.8842 | 5.4376 | 0 | 1.9395 | 0.33871 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 34.4992 | 0% | CZ 0B | 0 | 0 | 0.042809 | 0.32424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.47662 | 0% | CZ 0B | 50.3828 | 3.154 | 5.0235 | 35.9535 | 0.34003 | 88.5138 | 19.7253 | 56.9264 | 0 | 20.3044 | 3.5459 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 413.2671 | 0%
CZ 1A | 0.51158 | 0.032029 | 0.046378 | 0.3503 | 0 | 0.97116 | 0.21637 | 0.54122 | 0 | 0.19511 | 0.035601 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.1994 | 2.054% | CZ 1A | 16.4205 | 1.028 | 4.4878 | 35.7445 | 0 | 31.1722 | 6.9449 | 17.3718 | 0 | 6.2627 | 1.1427 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 169.8019 | 2.054% | CZ 1A | 4.8126 | 0.3013 | 0.032917 | 0 | 0 | 9.1361 | 2.0354 | 5.0914 | 0 | 1.8355 | 0.33491 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 34.7961 | 2.054% | CZ 1A | 0 | 0 | 0.043754 | 0.35745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.51078 | 2.054% | CZ 1A | 50.3828 | 3.1543 | 5.127 | 39.0688 | 0 | 95.6454 | 21.3088 | 53.3018 | 0 | 19.2156 | 3.5062 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 420.1082 | 2.054%
CZ 1B | 0.51158 | 0.031988 | 0.046445 | 0.33928 | 0.0096717 | 0.89042 | 0.15093 | 0.57388 | 0 | 0.18482 | 0.035377 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.074 | 0% | CZ 1B | 16.4205 | 1.0268 | 4.4946 | 33.2913 | 0.31044 | 28.5805 | 4.8444 | 18.4204 | 0 | 5.9324 | 1.1355 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 163.6837 | 0% | CZ 1B | 4.8126 | 0.30092 | 0.032905 | 0.17881 | 0.090985 | 8.3765 | 1.4198 | 5.3987 | 0 | 1.7387 | 0.33281 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 33.8987 | 0% | CZ 1B | 0 | 0 | 0.043824 | 0.32681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.48021 | 0% | CZ 1B | 50.3828 | 3.1504 | 5.1344 | 37.5925 | 0.95252 | 87.6932 | 14.8641 | 56.519 | 0 | 18.2024 | 3.4841 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 407.373 | 0%
CZ 2A | 0.51158 | 0.031977 | 0.047479 | 0.41758 | 0.03991 | 0.76939 | 0.17074 | 0.5448 | 0 | 0.19222 | 0.034919 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.0602 | 16.55% | CZ 2A | 16.4205 | 1.0264 | 4.6001 | 40.2555 | 1.281 | 24.6958 | 5.4804 | 17.487 | 0 | 6.1699 | 1.1208 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 167.7641 | 16.55% | CZ 2A | 4.8126 | 0.30082 | 0.032917 | 0.31665 | 0.37544 | 7.2379 | 1.6062 | 5.1252 | 0 | 1.8083 | 0.32849 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 33.1605 | 16.55% | CZ 2A | 0 | 0 | 0.044878 | 0.39175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.5462 | 16.55% | CZ 2A | 50.3828 | 3.1493 | 5.2497 | 46.1334 | 3.9305 | 75.7739 | 16.8154 | 53.6552 | 0 | 18.9309 | 3.439 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 406.8576 | 16.55%
CZ 2B | 0.51158 | 0.032 | 0.04766 | 0.4993 | 0.33517 | 0.57002 | 0.085191 | 0.5714 | 0 | 0.14667 | 0.034321 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.133 | 2.4% | CZ 2B | 16.4205 | 1.0271 | 4.6186 | 40.0905 | 10.7583 | 18.2966 | 2.7344 | 18.3406 | 0 | 4.7079 | 1.1016 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 167.3229 | 2.4% | CZ 2B | 4.8126 | 0.30104 | 0.032917 | 1.4605 | 3.1531 | 5.3624 | 0.80142 | 5.3753 | 0 | 1.3798 | 0.32286 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 34.218 | 2.4% | CZ 2B | 0 | 0 | 0.045063 | 0.35107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.50571 | 2.4% | CZ 2B | 50.3828 | 3.1516 | 5.2699 | 53.6623 | 33.0095 | 56.1391 | 8.3901 | 56.2744 | 0 | 14.4452 | 3.3801 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 413.5024 | 2.4%
CZ 3A | 0.51158 | 0.031994 | 0.049946 | 0.50533 | 0.15298 | 0.58463 | 0.10698 | 0.54404 | 0 | 0.16464 | 0.033823 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9856 | 13.96% | CZ 3A | 16.4205 | 1.0269 | 4.8518 | 45.544 | 4.9104 | 18.7654 | 3.4339 | 17.4624 | 0 | 5.2846 | 1.0856 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 168.0125 | 13.96% | CZ 3A | 4.8126 | 0.30098 | 0.032917 | 0.80975 | 1.4392 | 5.4998 | 1.0064 | 5.1179 | 0 | 1.5488 | 0.31818 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 32.1026 | 13.96% | CZ 3A | 0 | 0 | 0.047395 | 0.42781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.58478 | 13.96% | CZ 3A | 50.3828 | 3.151 | 5.5249 | 55.2371 | 15.0665 | 57.5778 | 10.5363 | 53.5798 | 0 | 16.2147 | 3.331 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 399.9993 | 13.96%
CZ 3B | 0.51158 | 0.031993 | 0.049301 | 0.47953 | 0.32513 | 0.43088 | 0.06892 | 0.56921 | 0 | 0.13162 | 0.033735 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9315 | 6.966% | CZ 3B | 16.4205 | 1.0269 | 4.786 | 39.1303 | 10.4359 | 13.8302 | 2.2122 | 18.2703 | 0 | 4.2246 | 1.0828 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 160.6464 | 6.966% | CZ 3B | 4.8126 | 0.30097 | 0.032917 | 1.3182 | 3.0586 | 4.0534 | 0.64835 | 5.3547 | 0 | 1.2382 | 0.31735 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 32.3513 | 6.966% | CZ 3B | 0 | 0 | 0.046736 | 0.34632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.50264 | 6.966% | CZ 3B | 50.3828 | 3.1509 | 5.4529 | 51.6539 | 32.0204 | 42.4352 | 6.7876 | 56.0584 | 0 | 12.9622 | 3.3224 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 393.6241 | 6.966%
CZ 3C | 0.51158 | 0.031988 | 0.05004 | 0.47307 | 0.064507 | 0.37576 | 0.065295 | 0.5407 | 0 | 0.12769 | 0.033565 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.5738 | 2.177% | CZ 3C | 16.4205 | 1.0268 | 4.8613 | 45.2536 | 2.0705 | 12.061 | 2.0958 | 17.3552 | 0 | 4.0987 | 1.0774 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 155.5476 | 2.177% | CZ 3C | 4.8126 | 0.30092 | 0.032917 | 0.40604 | 0.60684 | 3.5349 | 0.61425 | 5.0865 | 0 | 1.2013 | 0.31575 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 28.128 | 2.177% | CZ 3C | 0 | 0 | 0.04749 | 0.43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.59575 | 2.177% | CZ 3C | 50.3828 | 3.1504 | 5.5353 | 52.1988 | 6.353 | 37.0067 | 6.4306 | 53.2507 | 0 | 12.5761 | 3.3056 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 359.5875 | 2.177%
CZ 4A | 0.51158 | 0.031945 | 0.052164 | 0.60236 | 0.21655 | 0.47252 | 0.076249 | 0.5346 | 0 | 0.15085 | 0.033099 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9816 | 20.37% | CZ 4A | 16.4205 | 1.0254 | 5.0781 | 52.8862 | 6.9507 | 15.1669 | 2.4474 | 17.1596 | 0 | 4.842 | 1.0624 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 172.2661 | 20.37% | CZ 4A | 4.8126 | 0.30052 | 0.032917 | 1.1538 | 2.0371 | 4.4452 | 0.7173 | 5.0292 | 0 | 1.4191 | 0.31137 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.4752 | 20.37% | CZ 4A | 0 | 0 | 0.049658 | 0.48949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64873 | 20.37% | CZ 4A | 50.3828 | 3.1462 | 5.7723 | 65.5812 | 21.3269 | 46.5364 | 7.5095 | 52.6507 | 0 | 14.8568 | 3.2597 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 400.4198 | 20.37%
CZ 4B | 0.51158 | 0.03197 | 0.051468 | 0.50518 | 0.41671 | 0.31611 | 0.039383 | 0.58066 | 0 | 0.11144 | 0.032989 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.8971 | 0.5664% | CZ 4B | 16.4205 | 1.0262 | 5.0071 | 40.8084 | 13.3755 | 10.1465 | 1.2641 | 18.6381 | 0 | 3.577 | 1.0589 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 160.549 | 0.5664% | CZ 4B | 4.8126 | 0.30075 | 0.032917 | 1.4445 | 3.9201 | 2.9738 | 0.37049 | 5.4625 | 0 | 1.0484 | 0.31034 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.8924 | 0.5664% | CZ 4B | 0 | 0 | 0.048948 | 0.3588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.51732 | 0.5664% | CZ 4B | 50.3828 | 3.1486 | 5.6946 | 54.3393 | 41.0399 | 31.1324 | 3.8786 | 57.1869 | 0 | 10.9753 | 3.2489 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 390.4248 | 0.5664%
CZ 4C | 0.51158 | 0.031909 | 0.052846 | 0.5812 | 0.11488 | 0.23905 | 0.023203 | 0.53295 | 0 | 0.10857 | 0.032617 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.5285 | 2.852% | CZ 4C | 16.4205 | 1.0242 | 5.1477 | 51.2337 | 3.6873 | 7.6731 | 0.74477 | 17.1066 | 0 | 3.4849 | 1.0469 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 156.7965 | 2.852% | CZ 4C | 4.8126 | 0.30018 | 0.032917 | 1.0857 | 1.0807 | 2.2489 | 0.21828 | 5.0137 | 0 | 1.0214 | 0.30684 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 27.3371 | 2.852% | CZ 4C | 0 | 0 | 0.050354 | 0.47529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.63522 | 2.852% | CZ 4C | 50.3828 | 3.1425 | 5.8483 | 63.316 | 11.3136 | 23.5434 | 2.2852 | 52.4879 | 0 | 10.6927 | 3.2123 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 355.6223 | 2.852%
CZ 5A | 0.51158 | 0.031955 | 0.05441 | 0.64672 | 0.25852 | 0.33599 | 0.050071 | 0.53571 | 0 | 0.12994 | 0.032551 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.8871 | 20.94% | CZ 5A | 16.4205 | 1.0257 | 5.3073 | 56.1831 | 8.2978 | 10.7847 | 1.6072 | 17.1951 | 0 | 4.1707 | 1.0448 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 171.2636 | 20.94% | CZ 5A | 4.8126 | 0.30061 | 0.032917 | 1.3193 | 2.4319 | 3.1608 | 0.47103 | 5.0396 | 0 | 1.2224 | 0.30622 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 30.3134 | 20.94% | CZ 5A | 0 | 0 | 0.05195 | 0.51682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.67834 | 20.94% | CZ 5A | 50.3828 | 3.1471 | 6.0227 | 70.3 | 25.46 | 33.0905 | 4.9312 | 52.7594 | 0 | 12.797 | 3.2058 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 391.4941 | 20.94%
CZ 5B | 0.51158 | 0.031956 | 0.05373 | 0.5637 | 0.41868 | 0.3042 | 0.029379 | 0.58053 | 0 | 0.10712 | 0.032535 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9331 | 5.178% | CZ 5B | 16.4205 | 1.0257 | 5.2379 | 45.2911 | 13.4387 | 9.7641 | 0.94302 | 18.6337 | 0 | 3.4382 | 1.0443 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 164.464 | 5.178% | CZ 5B | 4.8126 | 0.30062 | 0.032917 | 1.6449 | 3.9386 | 2.8617 | 0.27638 | 5.4612 | 0 | 1.0077 | 0.30607 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.8587 | 5.178% | CZ 5B | 0 | 0 | 0.051256 | 0.39679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.55762 | 5.178% | CZ 5B | 50.3828 | 3.1472 | 5.9469 | 60.5891 | 41.2337 | 29.9592 | 2.8935 | 57.1734 | 0 | 10.5495 | 3.2042 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 394.4769 | 5.178%
CZ 5C | 0.51158 | 0.031906 | 0.054071 | 0.60295 | 0.12025 | 0.20384 | 0.01407 | 0.53163 | 0 | 0.098818 | 0.032284 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.501 | 0.1506% | CZ 5C | 16.4205 | 1.0241 | 5.2727 | 52.3367 | 3.8597 | 6.5429 | 0.45161 | 17.0641 | 0 | 3.1718 | 1.0363 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 156.4073 | 0.1506% | CZ 5C | 4.8126 | 0.30015 | 0.032917 | 1.2359 | 1.1312 | 1.9176 | 0.13236 | 5.0012 | 0 | 0.92961 | 0.30371 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 27.0133 | 0.1506% | CZ 5C | 0 | 0 | 0.051604 | 0.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.64238 | 0.1506% | CZ 5C | 50.3828 | 3.1423 | 5.9849 | 65.5333 | 11.8427 | 20.0755 | 1.3857 | 52.3577 | 0 | 9.7321 | 3.1795 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 353.014 | 0.1506%
CZ 6A | 0.51158 | 0.031941 | 0.056342 | 0.75611 | 0.3092 | 0.33803 | 0.054109 | 0.53922 | 0 | 0.13665 | 0.032395 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.0652 | 4.352% | CZ 6A | 16.4205 | 1.0252 | 5.5044 | 67.1897 | 9.9246 | 10.85 | 1.7368 | 17.3079 | 0 | 4.3861 | 1.0398 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 184.6118 | 4.352% | CZ 6A | 4.8126 | 0.30048 | 0.032928 | 1.3402 | 2.9087 | 3.1799 | 0.50902 | 5.0726 | 0 | 1.2855 | 0.30476 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 30.9628 | 4.352% | CZ 6A | 0 | 0 | 0.053921 | 0.62617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.78967 | 4.352% | CZ 6A | 50.3828 | 3.1457 | 6.2382 | 82.4708 | 30.4516 | 33.2908 | 5.329 | 53.1055 | 0 | 13.4579 | 3.1905 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 410.4602 | 4.352%
CZ 6B | 0.51158 | 0.031917 | 0.055801 | 0.72776 | 0.43839 | 0.27536 | 0.021067 | 0.55834 | 0 | 0.1103 | 0.032169 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.0623 | 0.7088% | CZ 6B | 16.4205 | 1.0245 | 5.4492 | 60.7002 | 14.0712 | 8.8385 | 0.67619 | 17.9217 | 0 | 3.5403 | 1.0326 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 178.9016 | 0.7088% | CZ 6B | 4.8126 | 0.30026 | 0.032928 | 1.824 | 4.124 | 2.5904 | 0.19818 | 5.2525 | 0 | 1.0376 | 0.30263 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.6912 | 0.7088% | CZ 6B | 0 | 0 | 0.053368 | 0.54477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.70771 | 0.7088% | CZ 6B | 50.3828 | 3.1434 | 6.1779 | 78.6385 | 43.1746 | 27.1192 | 2.0748 | 54.9888 | 0 | 10.8627 | 3.1682 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 409.1283 | 0.7088%
CZ 7 | 0.51158 | 0.031898 | 0.058626 | 0.84241 | 0.38591 | 0.29799 | 0.037974 | 0.53977 | 0 | 0.12324 | 0.032084 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.1611 | 0.728% | CZ 7 | 16.4205 | 1.0238 | 5.7373 | 74.5536 | 12.3869 | 9.5649 | 1.2189 | 17.3254 | 0 | 3.9559 | 1.0298 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 192.4437 | 0.728% | CZ 7 | 4.8126 | 0.30007 | 0.03294 | 1.5342 | 3.6304 | 2.8033 | 0.35723 | 5.0778 | 0 | 1.1594 | 0.30182 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.2258 | 0.728% | CZ 7 | 0 | 0 | 0.056249 | 0.69319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.85901 | 0.728% | CZ 7 | 50.3828 | 3.1415 | 6.4929 | 91.8273 | 38.0066 | 29.3479 | 3.7399 | 53.1592 | 0 | 12.1378 | 3.1598 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 420.793 | 0.728%
CZ 8 | 0.51158 | 0.031722 | 0.062033 | 1.0069 | 0.49277 | 0.20945 | 0.014675 | 0.53043 | 0 | 0.1029 | 0.031575 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 4.2937 | 0.05054% | CZ 8 | 16.4205 | 1.0182 | 6.0849 | 88.6919 | 15.8169 | 6.7229 | 0.47104 | 17.0258 | 0 | 3.3028 | 1.0135 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 205.795 | 0.05054% | CZ 8 | 4.8126 | 0.29842 | 0.032951 | 1.8903 | 4.6357 | 1.9704 | 0.13805 | 4.99 | 0 | 0.96798 | 0.29704 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.2493 | 0.05054% | CZ 8 | 0 | 0 | 0.059724 | 0.82242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.99172 | 0.05054% | CZ 8 | 50.3828 | 3.1241 | 6.8728 | 109.6801 | 48.5308 | 20.6277 | 1.4453 | 52.2399 | 0 | 10.1338 | 3.1097 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 435.5445 | 0.05054%
US Weighted | 0.51158 | 0.031966 | 0.051436 | 0.55488 | 0.20542 | 0.49096 | 0.08713 | 0.54439 | 0 | 0.1493 | 0.033431 | 0.31068 | 0.021228 | 0.27812 | 0 | 0.68962 | 3.9602 | 100% | US Weighted | 16.4205 | 1.026 | 5.0038 | 49.0222 | 6.5935 | 15.7588 | 2.7967 | 17.4738 | 0 | 4.7924 | 1.0731 | 9.9723 | 0.68137 | 16.4378 | 0 | 22.1353 | 169.1875 | 100% | US Weighted | 4.8126 | 0.30071 | 0.032918 | 1.022 | 1.9324 | 4.6186 | 0.81966 | 5.1213 | 0 | 1.4046 | 0.3145 | 2.9227 | 0.1997 | 1.6061 | 0 | 6.4875 | 31.5953 | 100% | US Weighted | 0 | 0 | 0.048915 | 0.45535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10958 | 0 | 0 | 0.61384 | 100% | US Weighted | 50.3828 | 3.1481 | 5.6911 | 60.4693 | 20.2308 | 48.3525 | 8.581 | 53.6148 | 0 | 14.7043 | 3.2925 | 30.5979 | 2.0907 | 28.7914 | 0 | 67.9175 | 397.8647 | 100%
Building Type: | Hospital |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Hospital |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 241501 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | Prototype Floor Area: | Prototype Floor Area: | 241501 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 241501 | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.11084 | 0.013036 | 0.0040803 | 0.29646 | 0 | 0.34207 | 0.13164 | 0.22923 | -0.023612 | 0.13049 | 0.016523 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2887 | 0% | CZ 0A | 3.5579 | 0.41843 | 0.39753 | 30.2507 | 0 | 10.9798 | 4.2254 | 7.3579 | -0.75788 | 4.1884 | 0.53035 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 62.3656 | 0% | CZ 0A | 1.0427 | 0.12264 | 0.0025312 | 0 | 0 | 3.218 | 1.2384 | 2.1565 | -0.22212 | 1.2275 | 0.15544 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 9.2983 | 0% | CZ 0A | 0 | 0 | 0.003889 | 0.30251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3064 | 0% | CZ 0A | 10.9165 | 1.2839 | 0.45156 | 33.0641 | 0 | 33.6892 | 12.9648 | 22.5762 | -2.3254 | 12.8512 | 1.6273 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 130.8334 | 0%
CZ 0B | 0.11078 | 0.013039 | 0.0040056 | 0.2984 | 0.0030967 | 0.1944 | 0.12085 | 0.23734 | -0.023612 | 0.12546 | 0.016463 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.1381 | 0% | CZ 0B | 3.5559 | 0.41851 | 0.38992 | 30.0937 | 0.099397 | 6.2399 | 3.8789 | 7.6181 | -0.75788 | 4.027 | 0.52843 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 57.3089 | 0% | CZ 0B | 1.0422 | 0.12266 | 0.0025312 | 0.04777 | 0.029132 | 1.8288 | 1.1368 | 2.2327 | -0.22212 | 1.1802 | 0.15487 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 7.9123 | 0% | CZ 0B | 0 | 0 | 0.0038128 | 0.29931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30312 | 0% | CZ 0B | 10.9106 | 1.2841 | 0.44324 | 33.2144 | 0.30498 | 19.1457 | 11.9017 | 23.3744 | -2.3254 | 12.356 | 1.6214 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 115.9653 | 0%
CZ 1A | 0.11059 | 0.01304 | 0.0040803 | 0.32081 | 0 | 0.33457 | 0.12347 | 0.20684 | -0.023612 | 0.12194 | 0.016382 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.266 | 2.054% | CZ 1A | 3.5497 | 0.41855 | 0.39746 | 32.7362 | 0 | 10.739 | 3.9633 | 6.639 | -0.75788 | 3.9141 | 0.52584 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 63.3422 | 2.054% | CZ 1A | 1.0404 | 0.12267 | 0.0025427 | 0 | 0 | 3.1474 | 1.1616 | 1.9458 | -0.22212 | 1.1471 | 0.15411 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.8562 | 2.054% | CZ 1A | 0 | 0 | 0.0038878 | 0.32736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33125 | 2.054% | CZ 1A | 10.8915 | 1.2842 | 0.45156 | 35.7806 | 0 | 32.9502 | 12.1604 | 20.3705 | -2.3254 | 12.0095 | 1.6134 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 128.9207 | 2.054%
CZ 1B | 0.11065 | 0.013024 | 0.0036941 | 0.30796 | 0.0086138 | 0.2571 | 0.091475 | 0.22522 | -0.023612 | 0.1105 | 0.016293 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.1588 | 0% | CZ 1B | 3.5517 | 0.41804 | 0.35813 | 30.1241 | 0.27648 | 8.2524 | 2.9361 | 7.2289 | -0.75788 | 3.5467 | 0.52297 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 57.6746 | 0% | CZ 1B | 1.0409 | 0.12252 | 0.0025312 | 0.17486 | 0.081033 | 2.4186 | 0.86054 | 2.1187 | -0.22212 | 1.0395 | 0.15327 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.147 | 0% | CZ 1B | 0 | 0 | 0.0034949 | 0.29527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29877 | 0% | CZ 1B | 10.8976 | 1.2827 | 0.4085 | 34.1041 | 0.84833 | 25.3207 | 9.0089 | 22.1804 | -2.3254 | 10.8822 | 1.6046 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 117.9468 | 0%
CZ 2A | 0.11069 | 0.013019 | 0.0035446 | 0.3719 | 0.022215 | 0.19638 | 0.10106 | 0.211 | -0.022247 | 0.12416 | 0.016214 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.1858 | 16.55% | CZ 2A | 3.5528 | 0.41788 | 0.34278 | 35.8504 | 0.71305 | 6.3034 | 3.2439 | 6.7726 | -0.71407 | 3.9854 | 0.52042 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 62.2055 | 16.55% | CZ 2A | 1.0413 | 0.12248 | 0.0025427 | 0.28223 | 0.20898 | 1.8474 | 0.95073 | 1.9849 | -0.20928 | 1.168 | 0.15253 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 7.9086 | 16.55% | CZ 2A | 0 | 0 | 0.0033411 | 0.34887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35222 | 16.55% | CZ 2A | 10.901 | 1.2822 | 0.3918 | 41.0866 | 2.1879 | 19.3408 | 9.9532 | 20.7802 | -2.191 | 12.2282 | 1.5968 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 121.2917 | 16.55%
CZ 2B | 0.11062 | 0.013029 | 0.003453 | 0.45038 | 0.19867 | 0.2058 | 0.059925 | 0.20698 | -0.021252 | 0.094347 | 0.015888 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.3757 | 2.4% | CZ 2B | 3.5505 | 0.4182 | 0.33344 | 36.3849 | 6.3768 | 6.6056 | 1.9234 | 6.6437 | -0.68216 | 3.0283 | 0.50998 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 66.3098 | 2.4% | CZ 2B | 1.0406 | 0.12257 | 0.0025427 | 1.2875 | 1.8689 | 1.936 | 0.56373 | 1.9472 | -0.19993 | 0.88755 | 0.14947 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 9.9628 | 2.4% | CZ 2B | 0 | 0 | 0.0032477 | 0.31992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32317 | 2.4% | CZ 2B | 10.894 | 1.2832 | 0.38159 | 48.4459 | 19.5659 | 20.268 | 5.9017 | 20.3849 | -2.0931 | 9.2918 | 1.5648 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 139.6227 | 2.4%
CZ 3A | 0.11055 | 0.013026 | 0.0026926 | 0.4261 | 0.079851 | 0.19886 | 0.068597 | 0.19064 | -0.021369 | 0.1142 | 0.015931 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.237 | 13.96% | CZ 3A | 3.5485 | 0.41812 | 0.25585 | 38.2495 | 2.5631 | 6.3831 | 2.2018 | 6.1193 | -0.68589 | 3.6656 | 0.51135 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 64.4474 | 13.96% | CZ 3A | 1.04 | 0.12254 | 0.0025427 | 0.7035 | 0.75119 | 1.8708 | 0.64532 | 1.7935 | -0.20102 | 1.0743 | 0.14987 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.3092 | 13.96% | CZ 3A | 0 | 0 | 0.0024718 | 0.35849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36096 | 13.96% | CZ 3A | 10.888 | 1.2829 | 0.29678 | 46.5481 | 7.8642 | 19.5852 | 6.7558 | 18.7756 | -2.1045 | 11.2473 | 1.569 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 126.4425 | 13.96%
CZ 3B | 0.1107 | 0.013025 | 0.0029749 | 0.41834 | 0.18466 | 0.114 | 0.047431 | 0.19792 | -0.020697 | 0.087736 | 0.015789 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2098 | 6.966% | CZ 3B | 3.5532 | 0.41808 | 0.28466 | 34.0804 | 5.9271 | 3.6592 | 1.5224 | 6.3527 | -0.66434 | 2.8161 | 0.5068 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 59.6733 | 6.966% | CZ 3B | 1.0414 | 0.12253 | 0.0025427 | 1.1576 | 1.7371 | 1.0724 | 0.4462 | 1.8619 | -0.19471 | 0.82536 | 0.14853 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.5776 | 6.966% | CZ 3B | 0 | 0 | 0.0027598 | 0.3013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30406 | 6.966% | CZ 3B | 10.9022 | 1.2828 | 0.32827 | 45.052 | 18.186 | 11.2274 | 4.6713 | 19.492 | -2.0384 | 8.6407 | 1.555 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 123.0334 | 6.966%
CZ 3C | 0.11076 | 0.013024 | 0.0026107 | 0.41362 | 0.032334 | 0.087471 | 0.049298 | 0.20232 | 0 | 0.082382 | 0.015816 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.0476 | 2.177% | CZ 3C | 3.5551 | 0.41804 | 0.24749 | 39.5027 | 1.0379 | 2.8076 | 1.5823 | 6.4942 | 0 | 2.6443 | 0.50766 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 60.0144 | 2.177% | CZ 3C | 1.042 | 0.12252 | 0.0025427 | 0.36366 | 0.30418 | 0.82287 | 0.46376 | 1.9033 | 0 | 0.77499 | 0.14879 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 6.3053 | 2.177% | CZ 3C | 0 | 0 | 0.0023882 | 0.38262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38501 | 2.177% | CZ 3C | 10.9082 | 1.2827 | 0.28765 | 45.6274 | 3.1845 | 8.6146 | 4.8551 | 19.9261 | 0 | 8.1134 | 1.5577 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 108.0914 | 2.177%
CZ 4A | 0.11076 | 0.013006 | 0.0018284 | 0.47874 | 0.10736 | 0.16399 | 0.049957 | 0.18642 | -0.021369 | 0.10919 | 0.015772 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2536 | 20.37% | CZ 4A | 3.5552 | 0.41745 | 0.16766 | 41.4723 | 3.4459 | 5.2636 | 1.6035 | 5.9836 | -0.68589 | 3.5046 | 0.50625 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 66.4513 | 20.37% | CZ 4A | 1.042 | 0.12235 | 0.0025427 | 0.99242 | 1.0099 | 1.5427 | 0.46996 | 1.7537 | -0.20102 | 1.0271 | 0.14837 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.2667 | 20.37% | CZ 4A | 0 | 0 | 0.0015899 | 0.38086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38245 | 20.37% | CZ 4A | 10.9083 | 1.2809 | 0.20039 | 52.0179 | 10.5731 | 16.1502 | 4.92 | 18.3595 | -2.1045 | 10.7532 | 1.5533 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 128.3465 | 20.37%
CZ 4B | 0.11087 | 0.013015 | 0.0020622 | 0.42359 | 0.22067 | 0.07111 | 0.030845 | 0.19108 | -0.020504 | 0.07576 | 0.015634 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.172 | 0.5664% | CZ 4B | 3.5586 | 0.41777 | 0.19153 | 33.8643 | 7.0829 | 2.2825 | 0.99005 | 6.1333 | -0.65813 | 2.4317 | 0.50182 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 58.0134 | 0.5664% | CZ 4B | 1.043 | 0.12244 | 0.0025427 | 1.2588 | 2.0759 | 0.66896 | 0.29017 | 1.7976 | -0.19289 | 0.7127 | 0.14707 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.2829 | 0.5664% | CZ 4B | 0 | 0 | 0.0018285 | 0.29569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29752 | 0.5664% | CZ 4B | 10.9189 | 1.2818 | 0.22648 | 45.4974 | 21.7324 | 7.0033 | 3.0378 | 18.8188 | -2.0193 | 7.4613 | 1.5397 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 119.2328 | 0.5664%
CZ 4C | 0.11057 | 0.012991 | 0.001658 | 0.47526 | 0.077948 | 0.048483 | 0.019696 | 0.18303 | -0.019652 | 0.071341 | 0.015594 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.0348 | 2.852% | CZ 4C | 3.5491 | 0.41698 | 0.15028 | 41.118 | 2.502 | 1.5562 | 0.63219 | 5.8749 | -0.63077 | 2.2899 | 0.50052 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 59.1763 | 2.852% | CZ 4C | 1.0402 | 0.12221 | 0.0025427 | 0.99227 | 0.73329 | 0.4561 | 0.18528 | 1.7218 | -0.18487 | 0.67113 | 0.14669 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 6.2434 | 2.852% | CZ 4C | 0 | 0 | 0.001416 | 0.37732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37874 | 2.852% | CZ 4C | 10.8895 | 1.2794 | 0.18139 | 51.6296 | 7.6768 | 4.7749 | 1.9397 | 18.026 | -1.9354 | 7.0261 | 1.5357 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 106.7579 | 2.852%
CZ 5A | 0.11077 | 0.013011 | 0.0012672 | 0.48506 | 0.14294 | 0.1012 | 0.034105 | 0.17523 | -0.020947 | 0.096895 | 0.015616 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.1931 | 20.94% | CZ 5A | 3.5556 | 0.41761 | 0.1104 | 41.0362 | 4.5881 | 3.2484 | 1.0947 | 5.6247 | -0.67235 | 3.1101 | 0.50123 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 63.8317 | 20.94% | CZ 5A | 1.0421 | 0.12239 | 0.0025427 | 1.1378 | 1.3447 | 0.95206 | 0.32084 | 1.6485 | -0.19705 | 0.91153 | 0.1469 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 7.789 | 20.94% | CZ 5A | 0 | 0 | 0.0010173 | 0.37154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37256 | 20.94% | CZ 5A | 10.9095 | 1.2813 | 0.13781 | 52.5209 | 14.0777 | 9.9671 | 3.3589 | 17.2581 | -2.0629 | 9.5428 | 1.5379 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 122.2633 | 20.94%
CZ 5B | 0.11086 | 0.013011 | 0.001428 | 0.44845 | 0.25292 | 0.10186 | 0.022452 | 0.18421 | -0.020805 | 0.07409 | 0.015558 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2419 | 5.178% | CZ 5B | 3.5583 | 0.41761 | 0.12681 | 34.8929 | 8.1182 | 3.2694 | 0.72067 | 5.9129 | -0.66779 | 2.3781 | 0.49938 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 60.4434 | 5.178% | CZ 5B | 1.0429 | 0.12239 | 0.0025427 | 1.4616 | 2.3793 | 0.9582 | 0.21122 | 1.733 | -0.19572 | 0.69699 | 0.14636 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.9155 | 5.178% | CZ 5B | 0 | 0 | 0.0011813 | 0.29906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30024 | 5.178% | CZ 5B | 10.9178 | 1.2813 | 0.15574 | 47.9889 | 24.909 | 10.0314 | 2.2112 | 18.1424 | -2.049 | 7.2967 | 1.5322 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 126.152 | 5.178%
CZ 5C | 0.1106 | 0.01299 | 0.0012007 | 0.34771 | 0.085836 | 0.084796 | 0.0095066 | 0.17683 | -0.019689 | 0.064362 | 0.015536 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 0.92759 | 0.1506% | CZ 5C | 3.55 | 0.41694 | 0.10361 | 27.1551 | 2.7551 | 2.7218 | 0.30514 | 5.6758 | -0.63199 | 2.0659 | 0.49867 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 45.8331 | 0.1506% | CZ 5C | 1.0404 | 0.1222 | 0.0025427 | 1.1198 | 0.80748 | 0.7977 | 0.089432 | 1.6635 | -0.18523 | 0.60547 | 0.14615 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 6.5662 | 0.1506% | CZ 5C | 0 | 0 | 0.00094938 | 0.23334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23429 | 0.1506% | CZ 5C | 10.8924 | 1.2793 | 0.13039 | 37.2277 | 8.4535 | 8.3512 | 0.93626 | 17.415 | -1.9391 | 6.3387 | 1.5301 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 94.3496 | 0.1506%
CZ 6A | 0.11077 | 0.013004 | 0.00096537 | 0.5448 | 0.17792 | 0.1126 | 0.037684 | 0.17522 | -0.021326 | 0.10888 | 0.015557 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.314 | 4.352% | CZ 6A | 3.5555 | 0.41741 | 0.079516 | 47.0872 | 5.7109 | 3.6142 | 1.2096 | 5.624 | -0.68451 | 3.4948 | 0.49934 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 71.8249 | 4.352% | CZ 6A | 1.042 | 0.12234 | 0.0025542 | 1.1438 | 1.6738 | 1.0593 | 0.3545 | 1.6483 | -0.20062 | 1.0243 | 0.14635 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.3733 | 4.352% | CZ 6A | 0 | 0 | 0.00070801 | 0.43185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43255 | 4.352% | CZ 6A | 10.9092 | 1.2807 | 0.10413 | 59.1753 | 17.5226 | 11.0894 | 3.7113 | 17.2562 | -2.1003 | 10.7231 | 1.5321 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 134.9378 | 4.352%
CZ 6B | 0.11077 | 0.012995 | 0.0010077 | 0.43278 | 0.25601 | 0.1345 | 0.014566 | 0.17527 | -0.02084 | 0.072936 | 0.015457 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2434 | 0.7088% | CZ 6B | 3.5553 | 0.4171 | 0.083834 | 32.3082 | 8.2174 | 4.317 | 0.46754 | 5.6256 | -0.66893 | 2.3411 | 0.49612 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 58.3774 | 0.7088% | CZ 6B | 1.042 | 0.12224 | 0.0025542 | 1.5943 | 2.4084 | 1.2652 | 0.13703 | 1.6488 | -0.19605 | 0.68614 | 0.14541 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 9.2127 | 0.7088% | CZ 6B | 0 | 0 | 0.00075119 | 0.26869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26944 | 0.7088% | CZ 6B | 10.9088 | 1.2798 | 0.10884 | 46.0578 | 25.2133 | 13.2459 | 1.4346 | 17.2611 | -2.0525 | 7.1832 | 1.5222 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 125.8973 | 0.7088%
CZ 7 | 0.11076 | 0.012986 | 0.00056428 | 0.46526 | 0.2078 | 0.14121 | 0.025517 | 0.17249 | -0.021382 | 0.079729 | 0.01546 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2483 | 0.728% | CZ 7 | 3.5552 | 0.41682 | 0.038503 | 37.787 | 6.67 | 4.5324 | 0.81905 | 5.5365 | -0.68632 | 2.5591 | 0.49624 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 62.9415 | 0.728% | CZ 7 | 1.042 | 0.12216 | 0.0025657 | 1.3032 | 1.9549 | 1.3284 | 0.24005 | 1.6226 | -0.20115 | 0.75004 | 0.14544 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.6668 | 0.728% | CZ 7 | 0 | 0 | 0.00029749 | 0.33341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3337 | 0.728% | CZ 7 | 10.9084 | 1.2789 | 0.059376 | 50.084 | 20.4654 | 13.9068 | 2.5131 | 16.9874 | -2.1058 | 7.8521 | 1.5226 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 127.2066 | 0.728%
CZ 8 | 0.11006 | 0.012915 | 0.00032704 | 0.54657 | 0.2658 | 0.11866 | 0.011004 | 0.17176 | -0.021589 | 0.070493 | 0.015279 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.3392 | 0.05054% | CZ 8 | 3.5327 | 0.41455 | 0.01421 | 43.889 | 8.5315 | 3.8087 | 0.35319 | 5.5131 | -0.69295 | 2.2627 | 0.49043 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 69.3341 | 0.05054% | CZ 8 | 1.0354 | 0.1215 | 0.0025772 | 1.5983 | 2.5004 | 1.1163 | 0.10351 | 1.6158 | -0.20309 | 0.66315 | 0.14374 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 9.0542 | 0.05054% | CZ 8 | 0 | 0 | 5.4161e-05 | 0.38436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38441 | 0.05054% | CZ 8 | 10.8393 | 1.272 | 0.032901 | 58.7425 | 26.1771 | 11.6862 | 1.0837 | 16.9158 | -2.1262 | 6.9425 | 1.5048 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 136.8046 | 0.05054%
US Weighted | 0.11071 | 0.013014 | 0.0022191 | 0.44579 | 0.11286 | 0.15064 | 0.055816 | 0.18992 | -0.020866 | 0.10396 | 0.015821 | 0.0040286 | 0.012578 | 0 | 0 | 0.02131 | 1.2178 | 100% | US Weighted | 3.5536 | 0.41773 | 0.20753 | 38.8799 | 3.6226 | 4.8351 | 1.7916 | 6.096 | -0.66975 | 3.3369 | 0.50781 | 0.12931 | 0.40371 | 0 | 0 | 0.684 | 63.796 | 100% | US Weighted | 1.0415 | 0.12243 | 0.0025435 | 0.88895 | 1.0617 | 1.4171 | 0.52508 | 1.7866 | -0.19629 | 0.978 | 0.14883 | 0.037899 | 0.11832 | 0 | 0 | 0.20047 | 8.1332 | 100% | US Weighted | 0 | 0 | 0.0019885 | 0.35847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36046 | 100% | US Weighted | 10.9034 | 1.2817 | 0.24397 | 48.4869 | 11.1153 | 14.8355 | 5.4971 | 18.7043 | -2.055 | 10.2386 | 1.5581 | 0.39676 | 1.2387 | 0 | 0 | 2.0987 | 124.5441 | 100%
Building Type: | Hospital |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Hospital |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Hospital |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Hospital |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 241501 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 241501 | [17 empty] | Prototype Floor Area: | 241501 | Building Type: | Hospital | [15 empty] | Prototype Floor Area: | 241501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 21.67% | 40.71% | 8.968% | 93.28% |  | 29.92% | 52.98% | 40.25% |  | 59.06% | 45.72% | 1.297% | 59.25% | 0% |  | 3.09% | 29.12% | 0% | CZ 0A | 21.67% | 40.71% | 9.038% | 93.28% |  | 29.92% | 52.98% | 40.25% |  | 59.06% | 45.72% | 1.297% | 59.25% | 0% |  | 3.09% | 35.7% | 0% | CZ 0A | 21.67% | 40.71% | 7.692% |  |  | 29.92% | 52.98% | 40.25% |  | 59.06% | 45.72% | 1.297% | 59.25% | 0% |  | 3.09% | 24.97% | 0% | CZ 0A |  |  | 9.074% | 93.28% | [9 empty] | 0% |  |  | 64.27% | 0% | CZ 0A | 21.67% | 40.71% | 8.979% | 93.28% |  | 29.92% | 52.98% | 40.25% |  | 59.06% | 45.72% | 1.297% | 59.25% | 0% |  | 3.09% | 29.61% | 0%
CZ 0B | 21.66% | 40.71% | 8.813% | 92.39% | 89.69% | 21.63% | 60.34% | 41.06% |  | 60.85% | 45.73% | 1.297% | 59.25% | 0% |  | 3.09% | 27.53% | 0% | CZ 0B | 21.66% | 40.71% | 8.876% | 92.34% | 89.69% | 21.63% | 60.34% | 41.06% |  | 60.85% | 45.73% | 1.297% | 59.25% | 0% |  | 3.09% | 34.65% | 0% | CZ 0B | 21.66% | 40.71% | 7.692% | 97.21% | 89.69% | 21.63% | 60.34% | 41.06% |  | 60.85% | 45.73% | 1.297% | 59.25% | 0% |  | 3.09% | 22.93% | 0% | CZ 0B |  |  | 8.907% | 92.31% | [9 empty] | 0% |  |  | 63.6% | 0% | CZ 0B | 21.66% | 40.71% | 8.823% | 92.38% | 89.69% | 21.63% | 60.34% | 41.06% |  | 60.85% | 45.73% | 1.297% | 59.25% | 0% |  | 3.09% | 28.06% | 0%
CZ 1A | 21.62% | 40.71% | 8.798% | 91.58% |  | 34.45% | 57.07% | 38.22% |  | 62.5% | 46.02% | 1.297% | 59.25% | 0% |  | 3.09% | 30.15% | 2.054% | CZ 1A | 21.62% | 40.71% | 8.856% | 91.58% |  | 34.45% | 57.07% | 38.22% |  | 62.5% | 46.02% | 1.297% | 59.25% | 0% |  | 3.09% | 37.3% | 2.054% | CZ 1A | 21.62% | 40.71% | 7.725% |  |  | 34.45% | 57.07% | 38.22% |  | 62.5% | 46.02% | 1.297% | 59.25% | 0% |  | 3.09% | 25.45% | 2.054% | CZ 1A |  |  | 8.886% | 91.58% | [9 empty] | 0% |  |  | 64.85% | 2.054% | CZ 1A | 21.62% | 40.71% | 8.807% | 91.58% |  | 34.45% | 57.07% | 38.22% |  | 62.5% | 46.02% | 1.297% | 59.25% | 0% |  | 3.09% | 30.69% | 2.054%
CZ 1B | 21.63% | 40.71% | 7.954% | 90.77% | 89.06% | 28.87% | 60.61% | 39.24% |  | 59.78% | 46.06% | 1.297% | 59.25% | 0% |  | 3.09% | 28.44% | 0% | CZ 1B | 21.63% | 40.71% | 7.968% | 90.49% | 89.06% | 28.87% | 60.61% | 39.24% |  | 59.78% | 46.06% | 1.297% | 59.25% | 0% |  | 3.09% | 35.24% | 0% | CZ 1B | 21.63% | 40.71% | 7.692% | 97.79% | 89.06% | 28.87% | 60.61% | 39.24% |  | 59.78% | 46.06% | 1.297% | 59.25% | 0% |  | 3.09% | 24.03% | 0% | CZ 1B |  |  | 7.975% | 90.35% | [9 empty] | 0% |  |  | 62.22% | 0% | CZ 1B | 21.63% | 40.71% | 7.956% | 90.72% | 89.06% | 28.87% | 60.61% | 39.24% |  | 59.78% | 46.06% | 1.297% | 59.25% | 0% |  | 3.09% | 28.95% | 0%
CZ 2A | 21.64% | 40.71% | 7.465% | 89.06% | 55.66% | 25.52% | 59.19% | 38.73% |  | 64.59% | 46.43% | 1.297% | 59.25% | 0% |  | 3.09% | 29.21% | 16.55% | CZ 2A | 21.64% | 40.71% | 7.452% | 89.06% | 55.66% | 25.52% | 59.19% | 38.73% |  | 64.59% | 46.43% | 1.297% | 59.25% | 0% |  | 3.09% | 37.08% | 16.55% | CZ 2A | 21.64% | 40.71% | 7.725% | 89.13% | 55.66% | 25.52% | 59.19% | 38.73% |  | 64.59% | 46.43% | 1.297% | 59.25% | 0% |  | 3.09% | 23.85% | 16.55% | CZ 2A |  |  | 7.445% | 89.06% | [9 empty] | 0% |  |  | 64.48% | 16.55% | CZ 2A | 21.64% | 40.71% | 7.463% | 89.06% | 55.66% | 25.52% | 59.19% | 38.73% |  | 64.59% | 46.43% | 1.297% | 59.25% | 0% |  | 3.09% | 29.81% | 16.55%
CZ 2B | 21.62% | 40.71% | 7.245% | 90.2% | 59.27% | 36.1% | 70.34% | 36.22% |  | 64.32% | 46.29% | 1.297% | 59.25% | 0% |  | 3.09% | 33.29% | 2.4% | CZ 2B | 21.62% | 40.71% | 7.22% | 90.76% | 59.27% | 36.1% | 70.34% | 36.22% |  | 64.32% | 46.29% | 1.297% | 59.25% | 0% |  | 3.09% | 39.63% | 2.4% | CZ 2B | 21.62% | 40.71% | 7.725% | 88.15% | 59.27% | 36.1% | 70.34% | 36.22% |  | 64.32% | 46.29% | 1.297% | 59.25% | 0% |  | 3.09% | 29.12% | 2.4% | CZ 2B |  |  | 7.207% | 91.13% | [9 empty] | 0% |  |  | 63.9% | 2.4% | CZ 2B | 21.62% | 40.71% | 7.241% | 90.28% | 59.27% | 36.1% | 70.34% | 36.22% |  | 64.32% | 46.29% | 1.297% | 59.25% | 0% |  | 3.09% | 33.77% | 2.4%
CZ 3A | 21.61% | 40.71% | 5.391% | 84.32% | 52.2% | 34.02% | 64.12% | 35.04% |  | 69.36% | 47.1% | 1.297% | 59.25% | 0% |  | 3.09% | 31.04% | 13.96% | CZ 3A | 21.61% | 40.71% | 5.273% | 83.98% | 52.2% | 34.02% | 64.12% | 35.04% |  | 69.36% | 47.1% | 1.297% | 59.25% | 0% |  | 3.09% | 38.36% | 13.96% | CZ 3A | 21.61% | 40.71% | 7.725% | 86.88% | 52.2% | 34.02% | 64.12% | 35.04% |  | 69.36% | 47.1% | 1.297% | 59.25% | 0% |  | 3.09% | 25.88% | 13.96% | CZ 3A |  |  | 5.215% | 83.8% | [9 empty] | 0% |  |  | 61.73% | 13.96% | CZ 3A | 21.61% | 40.71% | 5.372% | 84.27% | 52.2% | 34.02% | 64.12% | 35.04% |  | 69.36% | 47.1% | 1.297% | 59.25% | 0% |  | 3.09% | 31.61% | 13.96%
CZ 3B | 21.64% | 40.71% | 6.034% | 87.24% | 56.8% | 26.46% | 68.82% | 34.77% |  | 66.66% | 46.8% | 1.297% | 59.25% | 0% |  | 3.09% | 30.77% | 6.966% | CZ 3B | 21.64% | 40.71% | 5.948% | 87.09% | 56.8% | 26.46% | 68.82% | 34.77% |  | 66.66% | 46.8% | 1.297% | 59.25% | 0% |  | 3.09% | 37.15% | 6.966% | CZ 3B | 21.64% | 40.71% | 7.725% | 87.82% | 56.8% | 26.46% | 68.82% | 34.77% |  | 66.66% | 46.8% | 1.297% | 59.25% | 0% |  | 3.09% | 26.51% | 6.966% | CZ 3B |  |  | 5.905% | 87% | [9 empty] | 0% |  |  | 60.49% | 6.966% | CZ 3B | 21.64% | 40.71% | 6.02% | 87.22% | 56.8% | 26.46% | 68.82% | 34.77% |  | 66.66% | 46.8% | 1.297% | 59.25% | 0% |  | 3.09% | 31.26% | 6.966%
CZ 3C | 21.65% | 40.71% | 5.217% | 87.43% | 50.13% | 23.28% | 75.5% | 37.42% |  | 64.51% | 47.12% | 1.297% | 59.25% | 0% |  | 3.09% | 29.31% | 2.177% | CZ 3C | 21.65% | 40.71% | 5.091% | 87.29% | 50.13% | 23.28% | 75.5% | 37.42% |  | 64.51% | 47.12% | 1.297% | 59.25% | 0% |  | 3.09% | 38.58% | 2.177% | CZ 3C | 21.65% | 40.71% | 7.725% | 89.56% | 50.13% | 23.28% | 75.5% | 37.42% |  | 64.51% | 47.12% | 1.297% | 59.25% | 0% |  | 3.09% | 22.42% | 2.177% | CZ 3C |  |  | 5.029% | 87.22% | [9 empty] | 0% |  |  | 64.63% | 2.177% | CZ 3C | 21.65% | 40.71% | 5.197% | 87.41% | 50.13% | 23.28% | 75.5% | 37.42% |  | 64.51% | 47.12% | 1.297% | 59.25% | 0% |  | 3.09% | 30.06% | 2.177%
CZ 4A | 21.65% | 40.71% | 3.505% | 79.48% | 49.58% | 34.7% | 65.52% | 34.87% |  | 72.38% | 47.65% | 1.297% | 59.25% | 0% |  | 3.09% | 31.48% | 20.37% | CZ 4A | 21.65% | 40.71% | 3.302% | 78.42% | 49.58% | 34.7% | 65.52% | 34.87% |  | 72.38% | 47.65% | 1.297% | 59.25% | 0% |  | 3.09% | 38.57% | 20.37% | CZ 4A | 21.65% | 40.71% | 7.725% | 86.01% | 49.58% | 34.7% | 65.52% | 34.87% |  | 72.38% | 47.65% | 1.297% | 59.25% | 0% |  | 3.09% | 26.26% | 20.37% | CZ 4A |  |  | 3.202% | 77.81% | [9 empty] | 0% |  |  | 58.95% | 20.37% | CZ 4A | 21.65% | 40.71% | 3.472% | 79.32% | 49.58% | 34.7% | 65.52% | 34.87% |  | 72.38% | 47.65% | 1.297% | 59.25% | 0% |  | 3.09% | 32.05% | 20.37%
CZ 4B | 21.67% | 40.71% | 4.007% | 83.85% | 52.95% | 22.5% | 78.32% | 32.91% |  | 67.98% | 47.39% | 1.297% | 59.25% | 0% |  | 3.09% | 30.07% | 0.5664% | CZ 4B | 21.67% | 40.71% | 3.825% | 82.98% | 52.95% | 22.5% | 78.32% | 32.91% |  | 67.98% | 47.39% | 1.297% | 59.25% | 0% |  | 3.09% | 36.13% | 0.5664% | CZ 4B | 21.67% | 40.71% | 7.725% | 87.14% | 52.95% | 22.5% | 78.32% | 32.91% |  | 67.98% | 47.39% | 1.297% | 59.25% | 0% |  | 3.09% | 25.97% | 0.5664% | CZ 4B |  |  | 3.736% | 82.41% | [9 empty] | 0% |  |  | 57.51% | 0.5664% | CZ 4B | 21.67% | 40.71% | 3.977% | 83.73% | 52.95% | 22.5% | 78.32% | 32.91% |  | 67.98% | 47.39% | 1.297% | 59.25% | 0% |  | 3.09% | 30.54% | 0.5664%
CZ 4C | 21.61% | 40.71% | 3.137% | 81.77% | 67.85% | 20.28% | 84.88% | 34.34% |  | 65.71% | 47.81% | 1.297% | 59.25% | 0% |  | 3.09% | 29.33% | 2.852% | CZ 4C | 21.61% | 40.71% | 2.919% | 80.26% | 67.85% | 20.28% | 84.88% | 34.34% |  | 65.71% | 47.81% | 1.297% | 59.25% | 0% |  | 3.09% | 37.74% | 2.852% | CZ 4C | 21.61% | 40.71% | 7.725% | 91.39% | 67.85% | 20.28% | 84.88% | 34.34% |  | 65.71% | 47.81% | 1.297% | 59.25% | 0% |  | 3.09% | 22.84% | 2.852% | CZ 4C |  |  | 2.812% | 79.39% | [9 empty] | 0% |  |  | 59.62% | 2.852% | CZ 4C | 21.61% | 40.71% | 3.102% | 81.54% | 67.85% | 20.28% | 84.88% | 34.34% |  | 65.71% | 47.81% | 1.297% | 59.25% | 0% |  | 3.09% | 30.02% | 2.852%
CZ 5A | 21.65% | 40.71% | 2.329% | 75% | 55.29% | 30.12% | 68.11% | 32.71% |  | 74.57% | 47.97% | 1.297% | 59.25% | 0% |  | 3.09% | 30.69% | 20.94% | CZ 5A | 21.65% | 40.71% | 2.08% | 73.04% | 55.29% | 30.12% | 68.11% | 32.71% |  | 74.57% | 47.97% | 1.297% | 59.25% | 0% |  | 3.09% | 37.27% | 20.94% | CZ 5A | 21.65% | 40.71% | 7.725% | 86.24% | 55.29% | 30.12% | 68.11% | 32.71% |  | 74.57% | 47.97% | 1.297% | 59.25% | 0% |  | 3.09% | 25.69% | 20.94% | CZ 5A |  |  | 1.958% | 71.89% | [9 empty] | 0% |  |  | 54.92% | 20.94% | CZ 5A | 21.65% | 40.71% | 2.288% | 74.71% | 55.29% | 30.12% | 68.11% | 32.71% |  | 74.57% | 47.97% | 1.297% | 59.25% | 0% |  | 3.09% | 31.23% | 20.94%
CZ 5B | 21.67% | 40.71% | 2.658% | 79.55% | 60.41% | 33.48% | 76.42% | 31.73% |  | 69.17% | 47.82% | 1.297% | 59.25% | 0% |  | 3.09% | 31.58% | 5.178% | CZ 5B | 21.67% | 40.71% | 2.421% | 77.04% | 60.41% | 33.48% | 76.42% | 31.73% |  | 69.17% | 47.82% | 1.297% | 59.25% | 0% |  | 3.09% | 36.75% | 5.178% | CZ 5B | 21.67% | 40.71% | 7.725% | 88.86% | 60.41% | 33.48% | 76.42% | 31.73% |  | 69.17% | 47.82% | 1.297% | 59.25% | 0% |  | 3.09% | 27.98% | 5.178% | CZ 5B |  |  | 2.305% | 75.37% | [9 empty] | 0% |  |  | 53.84% | 5.178% | CZ 5B | 21.67% | 40.71% | 2.619% | 79.2% | 60.41% | 33.48% | 76.42% | 31.73% |  | 69.17% | 47.82% | 1.297% | 59.25% | 0% |  | 3.09% | 31.98% | 5.178%
CZ 5C | 21.62% | 40.71% | 2.221% | 57.67% | 71.38% | 41.6% | 67.57% | 33.26% |  | 65.13% | 48.12% | 1.297% | 59.25% | 0% |  | 3.09% | 26.49% | 0.1506% | CZ 5C | 21.62% | 40.71% | 1.965% | 51.89% | 71.38% | 41.6% | 67.57% | 33.26% |  | 65.13% | 48.12% | 1.297% | 59.25% | 0% |  | 3.09% | 29.3% | 0.1506% | CZ 5C | 21.62% | 40.71% | 7.725% | 90.61% | 71.38% | 41.6% | 67.57% | 33.26% |  | 65.13% | 48.12% | 1.297% | 59.25% | 0% |  | 3.09% | 24.31% | 0.1506% | CZ 5C |  |  | 1.84% | 48.49% | [9 empty] | 0% |  |  | 36.47% | 0.1506% | CZ 5C | 21.62% | 40.71% | 2.179% | 56.81% | 71.38% | 41.6% | 67.57% | 33.26% |  | 65.13% | 48.12% | 1.297% | 59.25% | 0% |  | 3.09% | 26.73% | 0.1506%
CZ 6A | 21.65% | 40.71% | 1.713% | 72.05% | 57.54% | 33.31% | 69.64% | 32.49% |  | 79.68% | 48.02% | 1.297% | 59.25% | 0% |  | 3.09% | 32.32% | 4.352% | CZ 6A | 21.65% | 40.71% | 1.445% | 70.08% | 57.54% | 33.31% | 69.64% | 32.49% |  | 79.68% | 48.02% | 1.297% | 59.25% | 0% |  | 3.09% | 38.91% | 4.352% | CZ 6A | 21.65% | 40.71% | 7.757% | 85.35% | 57.54% | 33.31% | 69.64% | 32.49% |  | 79.68% | 48.02% | 1.297% | 59.25% | 0% |  | 3.09% | 27.04% | 4.352% | CZ 6A |  |  | 1.313% | 68.97% | [9 empty] | 0% |  |  | 54.78% | 4.352% | CZ 6A | 21.65% | 40.71% | 1.669% | 71.75% | 57.54% | 33.31% | 69.64% | 32.49% |  | 79.68% | 48.02% | 1.297% | 59.25% | 0% |  | 3.09% | 32.87% | 4.352%
CZ 6B | 21.65% | 40.71% | 1.806% | 59.47% | 58.4% | 48.84% | 69.14% | 31.39% |  | 66.13% | 48.05% | 1.297% | 59.25% | 0% |  | 3.09% | 30.61% | 0.7088% | CZ 6B | 21.65% | 40.71% | 1.538% | 53.23% | 58.4% | 48.84% | 69.14% | 31.39% |  | 66.13% | 48.05% | 1.297% | 59.25% | 0% |  | 3.09% | 32.63% | 0.7088% | CZ 6B | 21.65% | 40.71% | 7.757% | 87.41% | 58.4% | 48.84% | 69.14% | 31.39% |  | 66.13% | 48.05% | 1.297% | 59.25% | 0% |  | 3.09% | 29.07% | 0.7088% | CZ 6B |  |  | 1.408% | 49.32% | [9 empty] | 0% |  |  | 38.07% | 0.7088% | CZ 6B | 21.65% | 40.71% | 1.762% | 58.57% | 58.4% | 48.84% | 69.14% | 31.39% |  | 66.13% | 48.05% | 1.297% | 59.25% | 0% |  | 3.09% | 30.77% | 0.7088%
CZ 7 | 21.65% | 40.71% | 0.9625% | 55.23% | 53.85% | 47.39% | 67.2% | 31.96% |  | 64.69% | 48.19% | 1.297% | 59.25% | 0% |  | 3.09% | 30% | 0.728% | CZ 7 | 21.65% | 40.71% | 0.6711% | 50.68% | 53.85% | 47.39% | 67.2% | 31.96% |  | 64.69% | 48.19% | 1.297% | 59.25% | 0% |  | 3.09% | 32.71% | 0.728% | CZ 7 | 21.65% | 40.71% | 7.789% | 84.94% | 53.85% | 47.39% | 67.2% | 31.96% |  | 64.69% | 48.19% | 1.297% | 59.25% | 0% |  | 3.09% | 27.76% | 0.728% | CZ 7 |  |  | 0.5289% | 48.1% | [9 empty] | 0% |  |  | 38.85% | 0.728% | CZ 7 | 21.65% | 40.71% | 0.9145% | 54.54% | 53.85% | 47.39% | 67.2% | 31.96% |  | 64.69% | 48.19% | 1.297% | 59.25% | 0% |  | 3.09% | 30.23% | 0.728%
CZ 8 | 21.51% | 40.71% | 0.5272% | 54.28% | 53.94% | 56.65% | 74.98% | 32.38% |  | 68.51% | 48.39% | 1.297% | 59.25% | 0% |  | 3.09% | 31.19% | 0.05054% | CZ 8 | 21.51% | 40.71% | 0.2335% | 49.48% | 53.94% | 56.65% | 74.98% | 32.38% |  | 68.51% | 48.39% | 1.297% | 59.25% | 0% |  | 3.09% | 33.69% | 0.05054% | CZ 8 | 21.51% | 40.71% | 7.821% | 84.55% | 53.94% | 56.65% | 74.98% | 32.38% |  | 68.51% | 48.39% | 1.297% | 59.25% | 0% |  | 3.09% | 28.97% | 0.05054% | CZ 8 |  |  | 0.09068% | 46.73% | [9 empty] | 0% |  |  | 38.76% | 0.05054% | CZ 8 | 21.51% | 40.71% | 0.4787% | 53.56% | 53.94% | 56.65% | 74.98% | 32.38% |  | 68.51% | 48.39% | 1.297% | 59.25% | 0% |  | 3.09% | 31.41% | 0.05054%
US Weighted | 21.64% | 40.71% | 4.426% | 81.43% | 53.45% | 30.94% | 66.62% | 34.89% | 0% | 69.99% | 47.34% | 1.297% | 59.25% | 0% | 0% | 3.09% | 30.75% | 100% | US Weighted | 21.64% | 40.71% | 4.27% | 80.4% | 53.45% | 30.94% | 66.62% | 34.89% | 0% | 69.99% | 47.34% | 1.297% | 59.25% | 0% | 0% | 3.09% | 37.71% | 100% | US Weighted | 21.64% | 40.71% | 7.727% | 85.47% | 53.45% | 30.94% | 66.62% | 34.89% | 0% | 69.99% | 47.34% | 1.297% | 59.25% | 0% | 0% | 3.09% | 25.73% | 100% | US Weighted | 0% | 0% | 4.193% | 79.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 59.11% | 100% | US Weighted | 21.64% | 40.71% | 4.4% | 81.28% | 53.45% | 30.94% | 66.62% | 34.89% | 0% | 69.99% | 47.34% | 1.297% | 59.25% | 0% | 0% | 3.09% | 31.3% | 100%

## HotSml
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Small Hotel |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 43202 |  | Building Type: | Small Hotel |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 |  | Building Type: | Small Hotel |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Small Hotel |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Small Hotel | [14 empty] | Prototype Floor Area: | 43202 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.12596 | 0.030289 | 0.12352 | 0.068337 | 0 | 0.20535 | 0 | 0.11032 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1358 |  | STD2019 | 4.043 | 0.9722 | 12.6038 | 2.9114 | 0 | 6.5912 | 0 | 3.5412 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.1535 |  | STD2019 | 1.1849 | 0.28493 | 0 | 0.5463 | 0 | 1.9318 | 0 | 1.0379 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.5742 |  | STD2019 | 0 | 0 | 0.12604 | 0.010475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22898 |  | STD2019 | 12.405 | 2.983 | 13.776 | 6.8641 | 0 | 20.2238 | 0 | 10.8653 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 114.7909
STD2016 | 0.19632 | 0.030289 | 0.12351 | 0.061636 | 0 | 0.21858 | 0 | 0.11605 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2184 |  | STD2016 | 6.3015 | 0.9722 | 12.6026 | 2.704 | 0 | 7.0159 | 0 | 3.7248 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 54.8118 |  | STD2016 | 1.8469 | 0.28493 | 0 | 0.48223 | 0 | 2.0563 | 0 | 1.0917 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.3503 |  | STD2016 | 0 | 0 | 0.12603 | 0.010586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22908 |  | STD2016 | 19.3348 | 2.983 | 13.7747 | 6.2055 | 0 | 21.5269 | 0 | 11.4289 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 122.9276
STD2013 | 0.21944 | 0.044985 | 0.12527 | 0.097726 | 0 | 0.23853 | 0 | 0.18084 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3788 |  | STD2013 | 7.0435 | 1.4439 | 12.7823 | 3.8845 | 0 | 7.6562 | 0 | 5.8045 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 60.1055 |  | STD2013 | 2.0643 | 0.42319 | 0 | 0.81877 | 0 | 2.2439 | 0 | 1.7012 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.8397 |  | STD2013 | 0 | 0 | 0.12782 | 0.010908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2312 |  | STD2013 | 21.6114 | 4.4304 | 13.9711 | 9.764 | 0 | 23.4913 | 0 | 17.8099 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 138.7518
STD2010 | 0.28297 | 0.044985 | 0.1253 | 0.099568 | 0 | 0.26635 | 0 | 0.20837 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.5224 |  | STD2010 | 9.0828 | 1.4439 | 12.7856 | 3.8403 | 0 | 8.5493 | 0 | 6.6881 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 64.6126 |  | STD2010 | 2.662 | 0.42319 | 0 | 0.85001 | 0 | 2.5057 | 0 | 1.9602 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 12.2039 |  | STD2010 | 0 | 0 | 0.12786 | 0.0094004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22973 |  | STD2010 | 27.8686 | 4.4304 | 13.9747 | 9.9262 | 0 | 26.2318 | 0 | 20.5211 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 152.872
STD2007 | 0.3405 | 0.065124 | 0.12563 | 0.10951 | 0 | 0.31798 | 0 | 0.21696 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.678 |  | STD2007 | 10.9295 | 2.0903 | 12.8193 | 4.1075 | 0 | 10.2065 | 0 | 6.964 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 69.5794 |  | STD2007 | 3.2032 | 0.61265 | 0 | 0.95051 | 0 | 2.9913 | 0 | 2.041 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.6719 |  | STD2007 | 0 | 0 | 0.12819 | 0.0086435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22931 |  | STD2007 | 33.5348 | 6.4138 | 14.0115 | 10.8957 | 0 | 31.3164 | 0 | 21.3674 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 168.1948
STD2004 | 0.3405 | 0.065124 | 0.12573 | 0.19438 | 0 | 0.33409 | 0 | 0.218 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.7802 |  | STD2004 | 10.9295 | 2.0903 | 12.8298 | 8.185 | 0 | 10.7235 | 0 | 6.9972 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 74.2176 |  | STD2004 | 3.2032 | 0.61265 | 0 | 1.5669 | 0 | 3.1429 | 0 | 2.0508 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.4495 |  | STD2004 | 0 | 0 | 0.1283 | 0.028389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24916 |  | STD2004 | 33.5348 | 6.4138 | 14.023 | 19.5063 | 0 | 32.9027 | 0 | 21.4694 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 178.5051
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 0.00010284 | 0.084867 | 0 | 0.016107 | 0 | 0.0010353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10211 |  | 2004-2007 | 0 | 0 | 0.010494 | 4.0775 | 0 | 0.51699 | 0 | 0.033231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6382 |  | 2004-2007 | 0 | 0 | 0 | 0.61634 | 0 | 0.15152 | 0 | 0.0097395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7776 |  | 2004-2007 | 0 | 0 | 0.00010494 | 0.019746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01985 |  | 2004-2007 | 0 | 0 | 0.01147 | 8.6106 | 0 | 1.5863 | 0 | 0.10196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3103
2007-2010 | 0.057533 | 0.020139 | 0.00033003 | 0.009942 | 0 | 0.051628 | 0 | 0.0085934 | 0 | 0 | 0 | 0.0058591 | 0 | 0 | 0 | 0.0016135 | 0.15564 |  | 2007-2010 | 1.8467 | 0.64643 | 0.033676 | 0.26723 | 0 | 1.6571 | 0 | 0.27583 | 0 | 0 | 0 | 0.18806 | 0 | 0 | 0 | 0.051789 | 4.9668 |  | 2007-2010 | 0.54123 | 0.18946 | 0 | 0.10051 | 0 | 0.48568 | 0 | 0.080841 | 0 | 0 | 0 | 0.055119 | 0 | 0 | 0 | 0.015179 | 1.468 |  | 2007-2010 | 0 | 0 | 0.00033676 | -0.00075697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0004202 |  | 2007-2010 | 5.6662 | 1.9834 | 0.036808 | 0.96946 | 0 | 5.0846 | 0 | 0.84633 | 0 | 0 | 0 | 0.57704 | 0 | 0 | 0 | 0.1589 | 15.3227
2010-2013 | 0.063535 | 0 | 3.2112e-05 | 0.0018422 | 0 | 0.027827 | 0 | 0.027529 | 0 | 0 | 0 | 0.00045806 | 0 | 0 | 0 | 0.022343 | 0.14357 |  | 2010-2013 | 2.0393 | 0 | 0.0032768 | -0.044234 | 0 | 0.89318 | 0 | 0.88362 | 0 | 0 | 0 | 0.014703 | 0 | 0 | 0 | 0.71715 | 4.507 |  | 2010-2013 | 0.59769 | 0 | 0 | 0.031233 | 0 | 0.26177 | 0 | 0.25898 | 0 | 0 | 0 | 0.0043092 | 0 | 0 | 0 | 0.21018 | 1.3642 |  | 2010-2013 | 0 | 0 | 3.2768e-05 | -0.001508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0014752 |  | 2010-2013 | 6.2572 | 0 | 0.0035815 | 0.16215 | 0 | 2.7405 | 0 | 2.7112 | 0 | 0 | 0 | 0.045113 | 0 | 0 | 0 | 2.2004 | 14.1202
2013-2016 | 0.023115 | 0.014696 | 0.001761 | 0.03609 | 0 | 0.019946 | 0 | 0.064791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1604 |  | 2013-2016 | 0.74195 | 0.47173 | 0.17969 | 1.1805 | 0 | 0.64022 | 0 | 2.0797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2938 |  | 2013-2016 | 0.21745 | 0.13825 | 0 | 0.33654 | 0 | 0.18764 | 0 | 0.60951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4894 |  | 2013-2016 | 0 | 0 | 0.0017969 | 0.00032226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021192 |  | 2013-2016 | 2.2765 | 1.4474 | 0.1964 | 3.5585 | 0 | 1.9644 | 0 | 6.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8242
2016-2019 | 0.070364 | 0 | -1.1402e-05 | -0.0067011 | 0 | 0.013232 | 0 | 0.0057224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082606 |  | 2016-2019 | 2.2585 | 0 | -0.0011635 | -0.20744 | 0 | 0.42471 | 0 | 0.18368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6583 |  | 2016-2019 | 0.66194 | 0 | 0 | -0.064068 | 0 | 0.12448 | 0 | 0.053833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77618 |  | 2016-2019 | 0 | 0 | -1.1635e-05 | 0.00011155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9913e-05 |  | 2016-2019 | 6.9298 | 0 | -0.0012717 | -0.65853 | 0 | 1.3031 | 0 | 0.56358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1367
2004-2019 | 0.21455 | 0.034836 | 0.0022145 | 0.12604 | 0 | 0.12874 | 0 | 0.10767 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.64432 |  | 2004-2019 | 6.8865 | 1.1182 | 0.22597 | 5.2736 | 0 | 4.1322 | 0 | 3.456 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 22.0642 |  | 2004-2019 | 2.0183 | 0.32771 | 0 | 1.0206 | 0 | 1.2111 | 0 | 1.0129 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.8754 |  | 2004-2019 | 0 | 0 | 0.0022597 | 0.017914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020174 |  | 2004-2019 | 21.1297 | 3.4308 | 0.24699 | 12.6422 | 0 | 12.6789 | 0 | 10.6041 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 63.7142
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.08179% | 43.66% |  | 4.821% |  | 0.4749% |  | 0% |  | 0% |  | 0% |  | 0% | 5.736% |  | 2004-2007 | 0% | 0% | 0.08179% | 49.82% |  | 4.821% |  | 0.4749% |  | 0% |  | 0% |  | 0% |  | 0% | 6.249% |  | 2004-2007 | 0% | 0% |  | 39.34% |  | 4.821% |  | 0.4749% |  | 0% |  | 0% |  | 0% |  | 0% | 5.381% |  | 2004-2007 |  |  | 0.08179% | 69.55% | [9 empty] | 0% |  |  | 7.967% |  | 2004-2007 | 0% | 0% | 0.08179% | 44.14% |  | 4.821% |  | 0.4749% |  | 0% |  | 0% |  | 0% |  | 0% | 5.776%
2007-2010 | 16.9% | 30.92% | 0.2627% | 9.079% |  | 16.24% |  | 3.961% |  | 0% |  | 3.307% |  | 0% |  | 0.7508% | 9.275% |  | 2007-2010 | 16.9% | 30.92% | 0.2627% | 6.506% |  | 16.24% |  | 3.961% |  | 0% |  | 3.307% |  | 0% |  | 0.7508% | 7.138% |  | 2007-2010 | 16.9% | 30.92% |  | 10.57% |  | 16.24% |  | 3.961% |  | 0% |  | 3.307% |  | 0% |  | 0.7508% | 10.74% |  | 2007-2010 |  |  | 0.2627% | -8.758% | [9 empty] | 0% |  |  | -0.1832% |  | 2007-2010 | 16.9% | 30.92% | 0.2627% | 8.898% |  | 16.24% |  | 3.961% |  | 0% |  | 3.307% |  | 0% |  | 0.7508% | 9.11%
2010-2013 | 22.45% | 0% | 0.02563% | 1.85% |  | 10.45% |  | 13.21% |  | 0% |  | 0.2674% |  | 0% |  | 10.48% | 9.43% |  | 2010-2013 | 22.45% | 0% | 0.02563% | -1.152% |  | 10.45% |  | 13.21% |  | 0% |  | 0.2674% |  | 0% |  | 10.48% | 6.975% |  | 2010-2013 | 22.45% | 0% |  | 3.674% |  | 10.45% |  | 13.21% |  | 0% |  | 0.2674% |  | 0% |  | 10.48% | 11.18% |  | 2010-2013 |  |  | 0.02563% | -16.04% | [9 empty] | 0% |  |  | -0.6422% |  | 2010-2013 | 22.45% | 0% | 0.02563% | 1.634% |  | 10.45% |  | 13.21% |  | 0% |  | 0.2674% |  | 0% |  | 10.48% | 9.237%
2013-2016 | 10.53% | 32.67% | 1.406% | 36.93% |  | 8.362% |  | 35.83% |  | 0% |  | 0% |  | 0% |  | 0% | 11.63% |  | 2013-2016 | 10.53% | 32.67% | 1.406% | 30.39% |  | 8.362% |  | 35.83% |  | 0% |  | 0% |  | 0% |  | 0% | 8.807% |  | 2013-2016 | 10.53% | 32.67% |  | 41.1% |  | 8.362% |  | 35.83% |  | 0% |  | 0% |  | 0% |  | 0% | 13.74% |  | 2013-2016 |  |  | 1.406% | 2.954% | [9 empty] | 0% |  |  | 0.9166% |  | 2013-2016 | 10.53% | 32.67% | 1.406% | 36.44% |  | 8.362% |  | 35.83% |  | 0% |  | 0% |  | 0% |  | 0% | 11.4%
2016-2019 | 35.84% | 0% | -0.009232% | -10.87% |  | 6.054% |  | 4.931% |  | 0% |  | 0% |  | 0% |  | 0% | 6.78% |  | 2016-2019 | 35.84% | 0% | -0.009232% | -7.672% |  | 6.054% |  | 4.931% |  | 0% |  | 0% |  | 0% |  | 0% | 4.85% |  | 2016-2019 | 35.84% | 0% |  | -13.29% |  | 6.054% |  | 4.931% |  | 0% |  | 0% |  | 0% |  | 0% | 8.301% |  | 2016-2019 |  |  | -0.009232% | 1.054% | [9 empty] | 0% |  |  | 0.04361% |  | 2016-2019 | 35.84% | 0% | -0.009232% | -10.61% |  | 6.054% |  | 4.931% |  | 0% |  | 0% |  | 0% |  | 0% | 6.619%
2004-2019 | 63.01% | 53.49% | 1.761% | 64.84% |  | 38.53% |  | 49.39% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 36.19% |  | 2004-2019 | 63.01% | 53.49% | 1.761% | 64.43% |  | 38.53% |  | 49.39% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 29.73% |  | 2004-2019 | 63.01% | 53.49% |  | 65.13% |  | 38.53% |  | 49.39% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 40.66% |  | 2004-2019 |  |  | 1.761% | 63.1% | [9 empty] | 0% |  |  | 8.097% |  | 2004-2019 | 63.01% | 53.49% | 1.761% | 64.81% |  | 38.53% |  | 49.39% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.69%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.1256 | 0.030335 | 0.091082 | 6.8368e-06 | 0 | 0.52493 | 0 | 0.11856 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3626 | 0% | CZ 0A | 4.0314 | 0.97368 | 9.2941 | 0.00021945 | 0 | 16.849 | 0 | 3.8054 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 56.4445 | 0% | CZ 0A | 1.1815 | 0.28537 | 0 | 6.4316e-05 | 0 | 4.9382 | 0 | 1.1153 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 11.1088 | 0% | CZ 0A | 0 | 0 | 0.092941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.18541 | 0% | CZ 0A | 12.3696 | 2.9875 | 10.1585 | 0.00067332 | 0 | 51.6976 | 0 | 11.6761 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 136.5636 | 0%
CZ 0B | 0.12563 | 0.030342 | 0.09122 | 8.2041e-05 | 0 | 0.48957 | 0 | 0.12051 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3294 | 0% | CZ 0B | 4.0325 | 0.9739 | 9.3081 | 0.0026333 | 0 | 15.714 | 0 | 3.8682 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 55.39 | 0% | CZ 0B | 1.1819 | 0.28543 | 0 | 0.00077179 | 0 | 4.6055 | 0 | 1.1337 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.7956 | 0% | CZ 0B | 0 | 0 | 0.093081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.18555 | 0% | CZ 0B | 12.3729 | 2.9882 | 10.1738 | 0.0080799 | 0 | 48.2152 | 0 | 11.8686 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 133.3006 | 0%
CZ 1A | 0.12675 | 0.030348 | 0.095225 | 5.4694e-05 | 0 | 0.38137 | 0 | 0.11262 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2184 | 2.061% | CZ 1A | 4.0685 | 0.97412 | 9.7169 | 0.0017556 | 0 | 12.2413 | 0 | 3.6147 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.1079 | 2.061% | CZ 1A | 1.1924 | 0.2855 | 0 | 0.00051453 | 0 | 3.5877 | 0 | 1.0594 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.7139 | 2.061% | CZ 1A | 0 | 0 | 0.097169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.18964 | 2.061% | CZ 1A | 12.4834 | 2.9889 | 10.6205 | 0.0053866 | 0 | 37.5599 | 0 | 11.0909 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 122.4227 | 2.061%
CZ 1B | 0.12623 | 0.030307 | 0.097423 | 0.0023448 | 0 | 0.41338 | 0 | 0.11701 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2588 | 0% | CZ 1B | 4.0518 | 0.9728 | 9.9411 | 0.091503 | 0 | 13.2685 | 0 | 3.7558 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 53.5722 | 0% | CZ 1B | 1.1875 | 0.28511 | 0 | 0.019874 | 0 | 3.8888 | 0 | 1.1008 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.0704 | 0% | CZ 1B | 0 | 0 | 0.099411 | 0.00023694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19212 | 0% | CZ 1B | 12.4322 | 2.9848 | 10.8656 | 0.23395 | 0 | 40.7117 | 0 | 11.5239 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 126.4259 | 0%
CZ 2A | 0.12615 | 0.030301 | 0.10293 | 0.0044756 | 0 | 0.33369 | 0 | 0.11117 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1808 | 19.12% | CZ 2A | 4.0492 | 0.97258 | 10.5034 | 0.19178 | 0 | 10.7107 | 0 | 3.5682 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 51.4865 | 19.12% | CZ 2A | 1.1868 | 0.28505 | 0 | 0.035631 | 0 | 3.1391 | 0 | 1.0458 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.2807 | 19.12% | CZ 2A | 0 | 0 | 0.10503 | 0.00070205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19821 | 19.12% | CZ 2A | 12.4241 | 2.9842 | 11.4802 | 0.44975 | 0 | 32.8635 | 0 | 10.9482 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 118.8236 | 19.12%
CZ 2B | 0.12692 | 0.030321 | 0.10407 | 0.0044108 | 0 | 0.27407 | 0 | 0.11442 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1263 | 1.527% | CZ 2B | 4.074 | 0.97324 | 10.6197 | 0.17752 | 0 | 8.7971 | 0 | 3.6726 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 49.8048 | 1.527% | CZ 2B | 1.194 | 0.28524 | 0 | 0.03666 | 0 | 2.5783 | 0 | 1.0764 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.759 | 1.527% | CZ 2B | 0 | 0 | 0.1062 | 0.00052435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19919 | 1.527% | CZ 2B | 12.5002 | 2.9862 | 11.6073 | 0.4411 | 0 | 26.9921 | 0 | 11.2687 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 113.4693 | 1.527%
CZ 3A | 0.12665 | 0.030314 | 0.117 | 0.034749 | 0 | 0.22215 | 0 | 0.10827 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1112 | 16.87% | CZ 3A | 4.0652 | 0.97302 | 11.9389 | 1.4954 | 0 | 7.1304 | 0 | 3.4751 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 50.5687 | 16.87% | CZ 3A | 1.1914 | 0.28518 | 0 | 0.27579 | 0 | 2.0898 | 0 | 1.0185 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.4491 | 16.87% | CZ 3A | 0 | 0 | 0.11939 | 0.005544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2174 | 16.87% | CZ 3A | 12.4733 | 2.9855 | 13.0492 | 3.4932 | 0 | 21.8782 | 0 | 10.6627 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 112.2158 | 16.87%
CZ 3B | 0.12668 | 0.030314 | 0.11324 | 0.013622 | 0 | 0.22277 | 0 | 0.11267 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.0914 | 6.686% | CZ 3B | 4.0661 | 0.97302 | 11.5549 | 0.59574 | 0 | 7.1504 | 0 | 3.6165 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 49.4473 | 6.686% | CZ 3B | 1.1917 | 0.28518 | 0 | 0.10683 | 0 | 2.0957 | 0 | 1.0599 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.3277 | 6.686% | CZ 3B | 0 | 0 | 0.11555 | 0.0023124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21033 | 6.686% | CZ 3B | 12.476 | 2.9855 | 12.6295 | 1.3711 | 0 | 21.9395 | 0 | 11.0963 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 110.1717 | 6.686%
CZ 3C | 0.12645 | 0.030307 | 0.11862 | 0.0030717 | 0 | 0.17934 | 0 | 0.13196 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.0618 | 0.9608% | CZ 3C | 4.0589 | 0.9728 | 12.1041 | 0.12025 | 0 | 5.7563 | 0 | 4.2357 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 48.7386 | 0.9608% | CZ 3C | 1.1896 | 0.28511 | 0 | 0.025984 | 0 | 1.6871 | 0 | 1.2414 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.0175 | 0.9608% | CZ 3C | 0 | 0 | 0.12104 | 0.00031592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21383 | 0.9608% | CZ 3C | 12.4537 | 2.9848 | 13.2298 | 0.30655 | 0 | 17.6619 | 0 | 12.9964 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 107.3069 | 0.9608%
CZ 4A | 0.12554 | 0.030266 | 0.12906 | 0.081463 | 0 | 0.16828 | 0 | 0.10603 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1127 | 19.16% | CZ 4A | 4.0295 | 0.97148 | 13.169 | 3.5345 | 0 | 5.4014 | 0 | 3.4034 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 51.9999 | 19.16% | CZ 4A | 1.181 | 0.28473 | 0 | 0.64264 | 0 | 1.5831 | 0 | 0.99747 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.2772 | 19.16% | CZ 4A | 0 | 0 | 0.13169 | 0.013418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23758 | 19.16% | CZ 4A | 12.3635 | 2.9808 | 14.3937 | 8.1944 | 0 | 16.5731 | 0 | 10.4425 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 112.6218 | 19.16%
CZ 4B | 0.12552 | 0.030294 | 0.12556 | 0.029666 | 0 | 0.17568 | 0 | 0.12677 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.0856 | 0.8608% | CZ 4B | 4.0288 | 0.97236 | 12.8127 | 1.2196 | 0 | 5.6389 | 0 | 4.0692 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 50.2321 | 0.8608% | CZ 4B | 1.1808 | 0.28498 | 0 | 0.24311 | 0 | 1.6527 | 0 | 1.1926 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.1425 | 0.8608% | CZ 4B | 0 | 0 | 0.12813 | 0.0039008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2245 | 0.8608% | CZ 4B | 12.3615 | 2.9835 | 14.0043 | 2.9715 | 0 | 17.3017 | 0 | 12.4854 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 109.7816 | 0.8608%
CZ 4C | 0.12634 | 0.030232 | 0.1327 | 0.038485 | 0 | 0.11949 | 0 | 0.1305 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.0498 | 1.635% | CZ 4C | 4.0551 | 0.97039 | 13.5407 | 1.6595 | 0 | 3.8352 | 0 | 4.1888 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 49.7403 | 1.635% | CZ 4C | 1.1885 | 0.2844 | 0 | 0.30499 | 0 | 1.124 | 0 | 1.2277 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 7.7179 | 1.635% | CZ 4C | 0 | 0 | 0.13541 | 0.006189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23407 | 1.635% | CZ 4C | 12.4423 | 2.9774 | 14.7999 | 3.8694 | 0 | 11.7676 | 0 | 12.8524 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 106.3827 | 1.635%
CZ 5A | 0.12543 | 0.03028 | 0.13936 | 0.13666 | 0 | 0.12627 | 0 | 0.10514 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1352 | 17.17% | CZ 5A | 4.0262 | 0.97192 | 14.2208 | 5.8275 | 0 | 4.0532 | 0 | 3.3748 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 53.965 | 17.17% | CZ 5A | 1.18 | 0.28485 | 0 | 1.0918 | 0 | 1.1879 | 0 | 0.98911 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.3221 | 17.17% | CZ 5A | 0 | 0 | 0.14221 | 0.021022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2557 | 17.17% | CZ 5A | 12.3534 | 2.9821 | 15.5433 | 13.728 | 0 | 12.4362 | 0 | 10.355 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 115.0719 | 17.17%
CZ 5B | 0.12535 | 0.03028 | 0.13638 | 0.070909 | 0 | 0.14317 | 0 | 0.12499 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1031 | 5.989% | CZ 5B | 4.0233 | 0.97192 | 13.9163 | 2.9373 | 0 | 4.5954 | 0 | 4.0119 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 51.9467 | 5.989% | CZ 5B | 1.1792 | 0.28485 | 0 | 0.57813 | 0 | 1.3468 | 0 | 1.1758 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.1532 | 5.989% | CZ 5B | 0 | 0 | 0.13916 | 0.0096467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24128 | 5.989% | CZ 5B | 12.3447 | 2.9821 | 15.2105 | 7.1069 | 0 | 14.1 | 0 | 12.3097 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 111.7275 | 5.989%
CZ 5C | 0.12598 | 0.030232 | 0.13849 | 0.040382 | 0 | 0.10784 | 0 | 0.12892 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.0439 | 0.1299% | CZ 5C | 4.0437 | 0.97039 | 14.1315 | 1.8493 | 0 | 3.4615 | 0 | 4.1381 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 50.0851 | 0.1299% | CZ 5C | 1.1851 | 0.2844 | 0 | 0.3055 | 0 | 1.0145 | 0 | 1.2128 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 7.5907 | 0.1299% | CZ 5C | 0 | 0 | 0.14131 | 0.0080692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24186 | 0.1299% | CZ 5C | 12.4073 | 2.9774 | 15.4457 | 4.0802 | 0 | 10.621 | 0 | 12.6968 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 105.9022 | 0.1299%
CZ 6A | 0.12549 | 0.030259 | 0.14699 | 0.22175 | 0 | 0.12411 | 0 | 0.10664 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2273 | 5.175% | CZ 6A | 4.0279 | 0.97126 | 14.9987 | 9.2809 | 0 | 3.9836 | 0 | 3.4229 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 58.1759 | 5.175% | CZ 6A | 1.1805 | 0.28466 | 0 | 1.7951 | 0 | 1.1675 | 0 | 1.0032 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.0194 | 5.175% | CZ 6A | 0 | 0 | 0.14999 | 0.03156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.27402 | 5.175% | CZ 6A | 12.3588 | 2.9801 | 16.3936 | 22.2425 | 0 | 12.2228 | 0 | 10.5025 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 124.3741 | 5.175%
CZ 6B | 0.12556 | 0.030239 | 0.14501 | 0.13478 | 0 | 0.11099 | 0 | 0.12091 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1396 | 1.6% | CZ 6B | 4.0303 | 0.97061 | 14.7969 | 5.5748 | 0 | 3.5627 | 0 | 3.8809 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 54.3068 | 1.6% | CZ 6B | 1.1812 | 0.28447 | 0 | 1.0999 | 0 | 1.0442 | 0 | 1.1374 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.3356 | 1.6% | CZ 6B | 0 | 0 | 0.14797 | 0.018218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25866 | 1.6% | CZ 6B | 12.3662 | 2.9781 | 16.173 | 13.5064 | 0 | 10.9314 | 0 | 11.9077 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 115.5365 | 1.6%
CZ 7 | 0.12557 | 0.030225 | 0.15604 | 0.25254 | 0 | 0.10639 | 0 | 0.11621 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.259 | 0.993% | CZ 7 | 4.0305 | 0.97017 | 15.9224 | 10.7174 | 0 | 3.415 | 0 | 3.7301 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 60.2763 | 0.993% | CZ 7 | 1.1813 | 0.28434 | 0 | 2.0245 | 0 | 1.0009 | 0 | 1.0932 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.1726 | 0.993% | CZ 7 | 0 | 0 | 0.15922 | 0.038097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.28979 | 0.993% | CZ 7 | 12.3669 | 2.9768 | 17.4032 | 25.3588 | 0 | 10.4782 | 0 | 11.4451 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 127.7027 | 0.993%
CZ 8 | 0.12787 | 0.030054 | 0.1682 | 0.33553 | 0 | 0.079402 | 0 | 0.13028 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3434 | 0.06422% | CZ 8 | 4.1045 | 0.96468 | 17.1635 | 14.3344 | 0 | 2.5486 | 0 | 4.1817 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 64.7881 | 0.06422% | CZ 8 | 1.203 | 0.28273 | 0 | 2.6769 | 0 | 0.74696 | 0 | 1.2256 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.7236 | 0.06422% | CZ 8 | 0 | 0 | 0.17163 | 0.052007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.31611 | 0.06422% | CZ 8 | 12.5938 | 2.9599 | 18.7597 | 33.7093 | 0 | 7.82 | 0 | 12.8308 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 136.3472 | 0.06422%
US Weighted | 0.12596 | 0.030289 | 0.12352 | 0.068337 | 0 | 0.20535 | 0 | 0.11032 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1358 | 100% | US Weighted | 4.043 | 0.9722 | 12.6038 | 2.9114 | 0 | 6.5912 | 0 | 3.5412 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.1535 | 100% | US Weighted | 1.1849 | 0.28493 | 0 | 0.5463 | 0 | 1.9318 | 0 | 1.0379 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.5742 | 100% | US Weighted | 0 | 0 | 0.12604 | 0.010475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22898 | 100% | US Weighted | 12.405 | 2.983 | 13.776 | 6.8641 | 0 | 20.2238 | 0 | 10.8653 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 114.7909 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.19576 | 0.030335 | 0.091078 | 6.8368e-06 | 0 | 0.54521 | 0 | 0.12273 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.4572 | 0% | CZ 0A | 6.2836 | 0.97368 | 9.2937 | 0.00021945 | 0 | 17.5001 | 0 | 3.9395 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 59.4814 | 0% | CZ 0A | 1.8416 | 0.28537 | 0 | 6.4316e-05 | 0 | 5.129 | 0 | 1.1546 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 11.999 | 0% | CZ 0A | 0 | 0 | 0.092937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.18541 | 0% | CZ 0A | 19.2799 | 2.9875 | 10.158 | 0.00067332 | 0 | 53.6953 | 0 | 12.0875 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 145.8826 | 0%
CZ 0B | 0.19617 | 0.030342 | 0.091215 | 8.8878e-05 | 0 | 0.50894 | 0 | 0.12528 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.4241 | 0% | CZ 0B | 6.2968 | 0.9739 | 9.3077 | 0.0028528 | 0 | 16.3357 | 0 | 4.0213 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 58.4289 | 0% | CZ 0B | 1.8455 | 0.28543 | 0 | 0.0008361 | 0 | 4.7877 | 0 | 1.1786 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 11.6864 | 0% | CZ 0B | 0 | 0 | 0.093077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.18555 | 0% | CZ 0B | 19.3203 | 2.9882 | 10.1733 | 0.0087532 | 0 | 50.1227 | 0 | 12.3386 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 142.6256 | 0%
CZ 1A | 0.1969 | 0.030348 | 0.095221 | 4.7857e-05 | 0 | 0.4015 | 0 | 0.11787 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3139 | 2.061% | CZ 1A | 6.32 | 0.97412 | 9.7164 | 0.0015361 | 0 | 12.8874 | 0 | 3.7832 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 55.1733 | 2.061% | CZ 1A | 1.8523 | 0.2855 | 0 | 0.00045021 | 0 | 3.7771 | 0 | 1.1088 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.6125 | 2.061% | CZ 1A | 0 | 0 | 0.097164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.18964 | 2.061% | CZ 1A | 19.3916 | 2.9889 | 10.6201 | 0.0047132 | 0 | 39.5421 | 0 | 11.6081 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 131.8292 | 2.061%
CZ 1B | 0.19609 | 0.030307 | 0.097421 | 0.0018111 | 0 | 0.43374 | 0 | 0.12225 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3537 | 0% | CZ 1B | 6.2941 | 0.9728 | 9.9409 | 0.06956 | 0 | 13.9223 | 0 | 3.9241 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 56.6144 | 0% | CZ 1B | 1.8447 | 0.28511 | 0 | 0.0155 | 0 | 4.0804 | 0 | 1.1501 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.9642 | 0% | CZ 1B | 0 | 0 | 0.099409 | 0.00016674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19205 | 0% | CZ 1B | 19.3122 | 2.9848 | 10.8654 | 0.18049 | 0 | 42.7175 | 0 | 12.0403 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 135.7745 | 0%
CZ 2A | 0.19673 | 0.030301 | 0.10293 | 0.003724 | 0 | 0.35117 | 0 | 0.11648 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2734 | 19.12% | CZ 2A | 6.3148 | 0.97258 | 10.5032 | 0.15908 | 0 | 11.2718 | 0 | 3.7389 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 54.451 | 19.12% | CZ 2A | 1.8507 | 0.28505 | 0 | 0.029714 | 0 | 3.3036 | 0 | 1.0958 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.1533 | 19.12% | CZ 2A | 0 | 0 | 0.10503 | 0.000577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19808 | 19.12% | CZ 2A | 19.3755 | 2.9842 | 11.48 | 0.37414 | 0 | 34.5851 | 0 | 11.472 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 127.9447 | 19.12%
CZ 2B | 0.19808 | 0.030321 | 0.10407 | 0.0035452 | 0 | 0.28991 | 0 | 0.12024 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2182 | 1.527% | CZ 2B | 6.358 | 0.97324 | 10.6194 | 0.14131 | 0 | 9.3054 | 0 | 3.8594 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.7474 | 1.527% | CZ 2B | 1.8634 | 0.28524 | 0 | 0.02965 | 0 | 2.7272 | 0 | 1.1311 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.625 | 1.527% | CZ 2B | 0 | 0 | 0.10619 | 0.00040149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19907 | 1.527% | CZ 2B | 19.5081 | 2.9862 | 11.6071 | 0.35428 | 0 | 28.5515 | 0 | 11.8417 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 122.5226 | 1.527%
CZ 3A | 0.19764 | 0.030314 | 0.11699 | 0.030705 | 0 | 0.2363 | 0 | 0.11407 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1981 | 16.87% | CZ 3A | 6.3437 | 0.97302 | 11.9376 | 1.3486 | 0 | 7.5847 | 0 | 3.6614 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 53.3397 | 16.87% | CZ 3A | 1.8592 | 0.28518 | 0 | 0.24003 | 0 | 2.2229 | 0 | 1.0731 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.2689 | 16.87% | CZ 3A | 0 | 0 | 0.11938 | 0.0052961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21714 | 16.87% | CZ 3A | 19.4644 | 2.9855 | 13.0477 | 3.0917 | 0 | 23.272 | 0 | 11.2344 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 120.7694 | 16.87%
CZ 3B | 0.19761 | 0.030314 | 0.11323 | 0.0109 | 0 | 0.2371 | 0 | 0.11886 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1801 | 6.686% | CZ 3B | 6.3428 | 0.97302 | 11.5538 | 0.47813 | 0 | 7.6104 | 0 | 3.8153 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.2641 | 6.686% | CZ 3B | 1.859 | 0.28518 | 0 | 0.085283 | 0 | 2.2305 | 0 | 1.1182 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.1665 | 6.686% | CZ 3B | 0 | 0 | 0.11554 | 0.0018714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20988 | 6.686% | CZ 3B | 19.4617 | 2.9855 | 12.6283 | 1.0974 | 0 | 23.3508 | 0 | 11.7064 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 118.9038 | 6.686%
CZ 3C | 0.19717 | 0.030307 | 0.1186 | 0.0022389 | 0 | 0.19308 | 0 | 0.13881 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1523 | 0.9608% | CZ 3C | 6.3288 | 0.9728 | 12.1025 | 0.084043 | 0 | 6.1976 | 0 | 4.4556 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 51.632 | 0.9608% | CZ 3C | 1.8549 | 0.28511 | 0 | 0.019423 | 0 | 1.8164 | 0 | 1.3059 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.87 | 0.9608% | CZ 3C | 0 | 0 | 0.12103 | 0.00017771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21367 | 0.9608% | CZ 3C | 19.4186 | 2.9848 | 13.2281 | 0.22277 | 0 | 19.0159 | 0 | 13.6711 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 116.215 | 0.9608%
CZ 4A | 0.19559 | 0.030266 | 0.12904 | 0.071795 | 0 | 0.17996 | 0 | 0.11186 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1906 | 19.16% | CZ 4A | 6.2779 | 0.97148 | 13.167 | 3.2271 | 0 | 5.7765 | 0 | 3.5903 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 54.5009 | 19.16% | CZ 4A | 1.8399 | 0.28473 | 0 | 0.55131 | 0 | 1.693 | 0 | 1.0523 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.0096 | 19.16% | CZ 4A | 0 | 0 | 0.13167 | 0.01346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2376 | 19.16% | CZ 4A | 19.2624 | 2.9808 | 14.3916 | 7.2429 | 0 | 17.7238 | 0 | 11.0162 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 120.2913 | 19.16%
CZ 4B | 0.19567 | 0.030294 | 0.12555 | 0.02542 | 0 | 0.18905 | 0 | 0.1194 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1575 | 0.8608% | CZ 4B | 6.2807 | 0.97236 | 12.8112 | 1.1627 | 0 | 6.0681 | 0 | 3.8326 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.6184 | 0.8608% | CZ 4B | 1.8408 | 0.28498 | 0 | 0.1925 | 0 | 1.7785 | 0 | 1.1233 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.8084 | 0.8608% | CZ 4B | 0 | 0 | 0.12811 | 0.0050592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22564 | 0.8608% | CZ 4B | 19.2711 | 2.9835 | 14.0026 | 2.5682 | 0 | 18.6187 | 0 | 11.7596 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 116.8774 | 0.8608%
CZ 4C | 0.19693 | 0.030232 | 0.13269 | 0.030445 | 0 | 0.13059 | 0 | 0.13735 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1303 | 1.635% | CZ 4C | 6.3209 | 0.97039 | 13.5396 | 1.3569 | 0 | 4.1916 | 0 | 4.4087 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.2787 | 1.635% | CZ 4C | 1.8525 | 0.2844 | 0 | 0.23533 | 0 | 1.2285 | 0 | 1.2921 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.4812 | 1.635% | CZ 4C | 0 | 0 | 0.1354 | 0.0055396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23341 | 1.635% | CZ 4C | 19.3943 | 2.9774 | 14.7987 | 3.0692 | 0 | 12.8611 | 0 | 13.527 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 114.3015 | 1.635%
CZ 5A | 0.19543 | 0.03028 | 0.13935 | 0.12482 | 0 | 0.13628 | 0 | 0.11114 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2094 | 17.17% | CZ 5A | 6.2728 | 0.97192 | 14.2197 | 5.488 | 0 | 4.3744 | 0 | 3.5673 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 56.3848 | 17.17% | CZ 5A | 1.8385 | 0.28485 | 0 | 0.9749 | 0 | 1.2821 | 0 | 1.0455 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.0142 | 17.17% | CZ 5A | 0 | 0 | 0.1422 | 0.021617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25628 | 17.17% | CZ 5A | 19.2469 | 2.9821 | 15.5421 | 12.5689 | 0 | 13.422 | 0 | 10.9455 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 122.3812 | 17.17%
CZ 5B | 0.19537 | 0.03028 | 0.13636 | 0.061562 | 0 | 0.15444 | 0 | 0.13236 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1824 | 5.989% | CZ 5B | 6.2709 | 0.97192 | 13.9147 | 2.6123 | 0 | 4.957 | 0 | 4.2485 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 54.4659 | 5.989% | CZ 5B | 1.8379 | 0.28485 | 0 | 0.49356 | 0 | 1.4528 | 0 | 1.2452 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.9026 | 5.989% | CZ 5B | 0 | 0 | 0.13915 | 0.0092825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2409 | 5.989% | CZ 5B | 19.2408 | 2.9821 | 15.2088 | 6.1816 | 0 | 15.2096 | 0 | 13.0355 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 119.5323 | 5.989%
CZ 5C | 0.19619 | 0.030232 | 0.13848 | 0.031494 | 0 | 0.11852 | 0 | 0.13566 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.1226 | 0.1299% | CZ 5C | 6.2974 | 0.97039 | 14.1304 | 1.5032 | 0 | 3.8041 | 0 | 4.3545 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 52.5506 | 0.1299% | CZ 5C | 1.8457 | 0.2844 | 0 | 0.23006 | 0 | 1.1149 | 0 | 1.2762 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 8.3396 | 0.1299% | CZ 5C | 0 | 0 | 0.1413 | 0.0071829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24096 | 0.1299% | CZ 5C | 19.3223 | 2.9774 | 15.4445 | 3.1936 | 0 | 11.672 | 0 | 13.3607 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 113.6442 | 0.1299%
CZ 6A | 0.1952 | 0.030259 | 0.14697 | 0.2076 | 0 | 0.13447 | 0 | 0.11286 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2994 | 5.175% | CZ 6A | 6.2654 | 0.97126 | 14.9974 | 8.9199 | 0 | 4.3163 | 0 | 3.6226 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 60.5834 | 5.175% | CZ 6A | 1.8363 | 0.28466 | 0 | 1.6494 | 0 | 1.265 | 0 | 1.0617 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.6855 | 5.175% | CZ 6A | 0 | 0 | 0.14997 | 0.03292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.27537 | 5.175% | CZ 6A | 19.224 | 2.9801 | 16.3922 | 20.8661 | 0 | 13.2436 | 0 | 11.1152 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 131.4949 | 5.175%
CZ 6B | 0.19534 | 0.030239 | 0.14499 | 0.122 | 0 | 0.12146 | 0 | 0.12827 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2144 | 1.6% | CZ 6B | 6.27 | 0.97061 | 14.7951 | 5.1791 | 0 | 3.8984 | 0 | 4.1172 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 56.7212 | 1.6% | CZ 6B | 1.8376 | 0.28447 | 0 | 0.97786 | 0 | 1.1426 | 0 | 1.2067 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.0376 | 1.6% | CZ 6B | 0 | 0 | 0.14795 | 0.018427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25885 | 1.6% | CZ 6B | 19.2381 | 2.9781 | 16.1711 | 12.2512 | 0 | 11.9615 | 0 | 12.6328 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 122.9067 | 1.6%
CZ 7 | 0.19494 | 0.030225 | 0.15603 | 0.24239 | 0 | 0.11685 | 0 | 0.11225 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3248 | 0.993% | CZ 7 | 6.2573 | 0.97017 | 15.9213 | 10.7204 | 0 | 3.7508 | 0 | 3.6031 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 62.7136 | 0.993% | CZ 7 | 1.8339 | 0.28434 | 0 | 1.8848 | 0 | 1.0993 | 0 | 1.056 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.7467 | 0.993% | CZ 7 | 0 | 0 | 0.15921 | 0.042893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.29458 | 0.993% | CZ 7 | 19.1991 | 2.9768 | 17.402 | 24.4206 | 0 | 11.5084 | 0 | 11.0553 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 134.2358 | 0.993%
CZ 8 | 0.19824 | 0.030054 | 0.16819 | 0.32183 | 0 | 0.087422 | 0 | 0.13749 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.4153 | 0.06422% | CZ 8 | 6.363 | 0.96468 | 17.1624 | 14.1257 | 0 | 2.806 | 0 | 4.413 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 67.3255 | 0.06422% | CZ 8 | 1.8649 | 0.28273 | 0 | 2.5171 | 0 | 0.8224 | 0 | 1.2934 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.3688 | 0.06422% | CZ 8 | 0 | 0 | 0.17162 | 0.055375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.31947 | 0.06422% | CZ 8 | 19.5236 | 2.9599 | 18.7585 | 32.4035 | 0 | 8.6098 | 0 | 13.5405 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 143.4695 | 0.06422%
US Weighted | 0.19632 | 0.030289 | 0.12351 | 0.061636 | 0 | 0.21858 | 0 | 0.11605 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2184 | 100% | US Weighted | 6.3015 | 0.9722 | 12.6026 | 2.704 | 0 | 7.0159 | 0 | 3.7248 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 54.8118 | 100% | US Weighted | 1.8469 | 0.28493 | 0 | 0.48223 | 0 | 2.0563 | 0 | 1.0917 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.3503 | 100% | US Weighted | 0 | 0 | 0.12603 | 0.010586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22908 | 100% | US Weighted | 19.3348 | 2.983 | 13.7747 | 6.2055 | 0 | 21.5269 | 0 | 11.4289 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 122.9276 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.21827 | 0.045061 | 0.098351 | 0 | 0 | 0.64326 | 0 | 0.18285 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.6599 | 0% | CZ 0A | 7.006 | 1.4464 | 10.0359 | 0 | 0 | 20.6474 | 0 | 5.8691 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 66.4953 | 0% | CZ 0A | 2.0533 | 0.4239 | 0 | 0 | 0 | 6.0514 | 0 | 1.7201 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 13.8371 | 0% | CZ 0A | 0 | 0 | 0.10036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19283 | 0% | CZ 0A | 21.4964 | 4.4379 | 10.9692 | 0 | 0 | 63.3521 | 0 | 18.008 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 165.9373 | 0%
CZ 0B | 0.2185 | 0.045068 | 0.098126 | 8.2041e-05 | 0 | 0.58881 | 0 | 0.18603 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.6087 | 0% | CZ 0B | 7.0132 | 1.4466 | 10.0128 | 0.0026333 | 0 | 18.8995 | 0 | 5.9711 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 64.8365 | 0% | CZ 0B | 2.0555 | 0.42397 | 0 | 0.00077179 | 0 | 5.5391 | 0 | 1.75 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 13.3577 | 0% | CZ 0B | 0 | 0 | 0.10013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.1926 | 0% | CZ 0B | 21.5187 | 4.4385 | 10.944 | 0.0080799 | 0 | 57.9891 | 0 | 18.3211 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 160.8932 | 0%
CZ 1A | 0.22043 | 0.045075 | 0.10248 | 3.4184e-05 | 0 | 0.46124 | 0 | 0.18024 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.4816 | 2.061% | CZ 1A | 7.0754 | 1.4468 | 10.4575 | 0.0010972 | 0 | 14.8046 | 0 | 5.7855 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 61.0615 | 2.061% | CZ 1A | 2.0737 | 0.42403 | 0 | 0.00032158 | 0 | 4.339 | 0 | 1.6956 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 12.121 | 2.061% | CZ 1A | 0 | 0 | 0.10458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19705 | 2.061% | CZ 1A | 21.7092 | 4.4392 | 11.4301 | 0.0033666 | 0 | 45.4249 | 0 | 17.7514 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 148.432 | 2.061%
CZ 1B | 0.21947 | 0.045013 | 0.10265 | 0.0027217 | 0 | 0.49494 | 0 | 0.18393 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.5208 | 0% | CZ 1B | 7.0444 | 1.4448 | 10.4742 | 0.099843 | 0 | 15.8865 | 0 | 5.9037 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 62.3442 | 0% | CZ 1B | 2.0646 | 0.42345 | 0 | 0.023925 | 0 | 4.6561 | 0 | 1.7303 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 12.4867 | 0% | CZ 1B | 0 | 0 | 0.10474 | 0.0001821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.1974 | 0% | CZ 1B | 21.6143 | 4.4331 | 11.4483 | 0.27038 | 0 | 48.7444 | 0 | 18.1144 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 152.2986 | 0%
CZ 2A | 0.2202 | 0.045 | 0.10735 | 0.006122 | 0 | 0.39954 | 0 | 0.17972 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.43 | 19.12% | CZ 2A | 7.0679 | 1.4444 | 10.9542 | 0.24072 | 0 | 12.8244 | 0 | 5.7686 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 59.7908 | 19.12% | CZ 2A | 2.0715 | 0.42333 | 0 | 0.051646 | 0 | 3.7586 | 0 | 1.6907 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 11.5841 | 19.12% | CZ 2A | 0 | 0 | 0.10954 | 0.00064501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20266 | 19.12% | CZ 2A | 21.6863 | 4.4318 | 11.973 | 0.61118 | 0 | 39.3489 | 0 | 17.6996 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 143.4245 | 19.12%
CZ 2B | 0.2217 | 0.045034 | 0.10824 | 0.0055093 | 0 | 0.3214 | 0 | 0.18382 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3578 | 1.527% | CZ 2B | 7.1162 | 1.4455 | 11.0451 | 0.20736 | 0 | 10.3163 | 0 | 5.9002 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 57.5213 | 1.527% | CZ 2B | 2.0856 | 0.42365 | 0 | 0.047722 | 0 | 3.0235 | 0 | 1.7293 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.8982 | 1.527% | CZ 2B | 0 | 0 | 0.11045 | 0.00044537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20337 | 1.527% | CZ 2B | 21.8345 | 4.4352 | 12.0723 | 0.54828 | 0 | 31.6535 | 0 | 18.1036 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 136.321 | 1.527%
CZ 3A | 0.22118 | 0.045027 | 0.11916 | 0.050265 | 0 | 0.25927 | 0 | 0.17884 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3458 | 16.87% | CZ 3A | 7.0995 | 1.4453 | 12.1596 | 1.9918 | 0 | 8.322 | 0 | 5.7405 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 58.2492 | 16.87% | CZ 3A | 2.0807 | 0.42358 | 0 | 0.42198 | 0 | 2.439 | 0 | 1.6824 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.6361 | 16.87% | CZ 3A | 0 | 0 | 0.1216 | 0.0055199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21959 | 16.87% | CZ 3A | 21.7833 | 4.4345 | 13.2904 | 5.021 | 0 | 25.5344 | 0 | 17.6134 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 135.3507 | 16.87%
CZ 3B | 0.22117 | 0.04502 | 0.116 | 0.019764 | 0 | 0.25719 | 0 | 0.18335 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3146 | 6.686% | CZ 3B | 7.0991 | 1.445 | 11.8364 | 0.77635 | 0 | 8.2553 | 0 | 5.8851 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 56.7879 | 6.686% | CZ 3B | 2.0806 | 0.42352 | 0 | 0.16683 | 0 | 2.4195 | 0 | 1.7248 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.4036 | 6.686% | CZ 3B | 0 | 0 | 0.11836 | 0.0020711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21291 | 6.686% | CZ 3B | 21.7819 | 4.4338 | 12.9372 | 1.973 | 0 | 25.3297 | 0 | 18.0571 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 132.1864 | 6.686%
CZ 3C | 0.22068 | 0.045013 | 0.11894 | 0.0037924 | 0 | 0.20017 | 0 | 0.20402 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2647 | 0.9608% | CZ 3C | 7.0833 | 1.4448 | 12.1363 | 0.13737 | 0 | 6.4251 | 0 | 6.5485 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 55.266 | 0.9608% | CZ 3C | 2.076 | 0.42345 | 0 | 0.033573 | 0 | 1.8831 | 0 | 1.9192 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.9237 | 0.9608% | CZ 3C | 0 | 0 | 0.12136 | 0.00022817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21406 | 0.9608% | CZ 3C | 21.7335 | 4.4331 | 13.265 | 0.37641 | 0 | 19.7142 | 0 | 20.0926 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 127.2885 | 0.9608%
CZ 4A | 0.21811 | 0.044952 | 0.12941 | 0.11653 | 0 | 0.19284 | 0 | 0.17712 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.351 | 19.16% | CZ 4A | 7.0007 | 1.4429 | 13.2052 | 4.6899 | 0 | 6.1897 | 0 | 5.6852 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 59.7041 | 19.16% | CZ 4A | 2.0518 | 0.42288 | 0 | 0.96853 | 0 | 1.8141 | 0 | 1.6662 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.5119 | 19.16% | CZ 4A | 0 | 0 | 0.13205 | 0.013852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23838 | 19.16% | CZ 4A | 21.4803 | 4.4271 | 14.4333 | 11.6536 | 0 | 18.9917 | 0 | 17.4437 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 136.1034 | 19.16%
CZ 4B | 0.21811 | 0.044993 | 0.12619 | 0.04632 | 0 | 0.20013 | 0 | 0.1841 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2919 | 0.8608% | CZ 4B | 7.001 | 1.4442 | 12.877 | 1.8575 | 0 | 6.4238 | 0 | 5.9092 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 57.0033 | 0.8608% | CZ 4B | 2.0519 | 0.42326 | 0 | 0.38589 | 0 | 1.8827 | 0 | 1.7319 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.064 | 0.8608% | CZ 4B | 0 | 0 | 0.12877 | 0.005408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22665 | 0.8608% | CZ 4B | 21.481 | 4.4311 | 14.0746 | 4.631 | 0 | 19.7101 | 0 | 18.1312 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 130.1327 | 0.8608%
CZ 4C | 0.21955 | 0.044904 | 0.13289 | 0.056791 | 0 | 0.12921 | 0 | 0.20377 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2592 | 1.635% | CZ 4C | 7.047 | 1.4413 | 13.5602 | 2.2349 | 0 | 4.1473 | 0 | 6.5406 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 56.462 | 1.635% | CZ 4C | 2.0654 | 0.42243 | 0 | 0.47883 | 0 | 1.2155 | 0 | 1.9169 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.6874 | 1.635% | CZ 4C | 0 | 0 | 0.1356 | 0.0060113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23408 | 1.635% | CZ 4C | 21.6224 | 4.4224 | 14.8213 | 5.6699 | 0 | 12.7251 | 0 | 20.0683 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 127.0031 | 1.635%
CZ 5A | 0.21827 | 0.044972 | 0.13955 | 0.19468 | 0 | 0.14022 | 0 | 0.17699 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3868 | 17.17% | CZ 5A | 7.006 | 1.4435 | 14.2403 | 7.763 | 0 | 4.5008 | 0 | 5.681 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 62.1253 | 17.17% | CZ 5A | 2.0533 | 0.42307 | 0 | 1.6278 | 0 | 1.3191 | 0 | 1.665 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.6767 | 17.17% | CZ 5A | 0 | 0 | 0.1424 | 0.022088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25696 | 17.17% | CZ 5A | 21.4964 | 4.4291 | 15.5646 | 19.456 | 0 | 13.8098 | 0 | 17.4309 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 139.8607 | 17.17%
CZ 5B | 0.21817 | 0.044972 | 0.13657 | 0.10479 | 0 | 0.15948 | 0 | 0.19762 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3337 | 5.989% | CZ 5B | 7.0029 | 1.4435 | 13.9356 | 4.0286 | 0 | 5.119 | 0 | 6.3431 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 59.3633 | 5.989% | CZ 5B | 2.0524 | 0.42307 | 0 | 0.8963 | 0 | 1.5003 | 0 | 1.859 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.3195 | 5.989% | CZ 5B | 0 | 0 | 0.13936 | 0.0097037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24153 | 5.989% | CZ 5B | 21.487 | 4.4291 | 15.2316 | 10.444 | 0 | 15.7066 | 0 | 19.4623 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 134.4343 | 5.989%
CZ 5C | 0.21915 | 0.044897 | 0.13867 | 0.062821 | 0 | 0.11123 | 0 | 0.202 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.2508 | 0.1299% | CZ 5C | 7.0341 | 1.4411 | 14.1501 | 2.5634 | 0 | 3.5702 | 0 | 6.4837 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 56.7332 | 0.1299% | CZ 5C | 2.0616 | 0.42236 | 0 | 0.51742 | 0 | 1.0464 | 0 | 1.9003 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 9.5363 | 0.1299% | CZ 5C | 0 | 0 | 0.1415 | 0.0079793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24195 | 0.1299% | CZ 5C | 21.5826 | 4.4217 | 15.4661 | 6.289 | 0 | 10.9543 | 0 | 19.8939 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 126.2814 | 0.1299%
CZ 6A | 0.21837 | 0.044945 | 0.14722 | 0.31051 | 0 | 0.13848 | 0 | 0.17831 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.5099 | 5.175% | CZ 6A | 7.0093 | 1.4426 | 15.0226 | 12.276 | 0 | 4.4449 | 0 | 5.7233 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 67.4095 | 5.175% | CZ 6A | 2.0543 | 0.42281 | 0 | 2.6104 | 0 | 1.3027 | 0 | 1.6774 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 11.6561 | 5.175% | CZ 6A | 0 | 0 | 0.15023 | 0.033692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.27639 | 5.175% | CZ 6A | 21.5065 | 4.4264 | 16.4198 | 31.0113 | 0 | 13.6381 | 0 | 17.5609 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 152.2367 | 5.175%
CZ 6B | 0.21851 | 0.044918 | 0.14522 | 0.19561 | 0 | 0.12077 | 0 | 0.19399 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3911 | 1.6% | CZ 6B | 7.0137 | 1.4418 | 14.8186 | 7.5934 | 0 | 3.8765 | 0 | 6.2265 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 62.4612 | 1.6% | CZ 6B | 2.0556 | 0.42255 | 0 | 1.6633 | 0 | 1.1361 | 0 | 1.8249 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.6908 | 1.6% | CZ 6B | 0 | 0 | 0.14819 | 0.019184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25984 | 1.6% | CZ 6B | 21.52 | 4.4237 | 16.1967 | 19.5095 | 0 | 11.8942 | 0 | 19.1048 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 140.3228 | 1.6%
CZ 7 | 0.21807 | 0.04489 | 0.15629 | 0.36953 | 0 | 0.1167 | 0 | 0.17788 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.5554 | 0.993% | CZ 7 | 6.9996 | 1.4409 | 15.9478 | 14.8725 | 0 | 3.7457 | 0 | 5.7095 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 70.2067 | 0.993% | CZ 7 | 2.0515 | 0.4223 | 0 | 3.0713 | 0 | 1.0978 | 0 | 1.6734 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 11.9046 | 0.993% | CZ 7 | 0 | 0 | 0.15948 | 0.043933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.29588 | 0.993% | CZ 7 | 21.4769 | 4.421 | 17.431 | 36.955 | 0 | 11.4929 | 0 | 17.5185 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 156.969 | 0.993%
CZ 8 | 0.22174 | 0.044644 | 0.16852 | 0.51217 | 0 | 0.080701 | 0 | 0.20346 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.7033 | 0.06422% | CZ 8 | 7.1173 | 1.433 | 17.1959 | 20.3842 | 0 | 2.5903 | 0 | 6.5307 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 76.742 | 0.06422% | CZ 8 | 2.086 | 0.41998 | 0 | 4.2875 | 0 | 0.75918 | 0 | 1.914 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 13.0551 | 0.06422% | CZ 8 | 0 | 0 | 0.17196 | 0.057551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.32198 | 0.06422% | CZ 8 | 21.8378 | 4.3968 | 18.7952 | 51.1766 | 0 | 7.9479 | 0 | 20.038 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 171.866 | 0.06422%
US Weighted | 0.21944 | 0.044985 | 0.12527 | 0.097726 | 0 | 0.23853 | 0 | 0.18084 | 0 | 0.00017776 | 0 | 0.17086 | 0 | 0.11009 | 0 | 0.19094 | 1.3788 | 100% | US Weighted | 7.0435 | 1.4439 | 12.7823 | 3.8845 | 0 | 7.6562 | 0 | 5.8045 | 0 | 0.0057056 | 0 | 5.4842 | 0 | 9.8721 | 0 | 6.1287 | 60.1055 | 100% | US Weighted | 2.0643 | 0.42319 | 0 | 0.81877 | 0 | 2.2439 | 0 | 1.7012 | 0 | 0.0016722 | 0 | 1.6073 | 0 | 0.18317 | 0 | 1.7962 | 10.8397 | 100% | US Weighted | 0 | 0 | 0.12782 | 0.010908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2312 | 100% | US Weighted | 21.6114 | 4.4304 | 13.9711 | 9.764 | 0 | 23.4913 | 0 | 17.8099 | 0 | 0.017506 | 0 | 16.827 | 0 | 12.0248 | 0 | 18.8045 | 138.7518 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.28597 | 0.045061 | 0.098377 | 0 | 0 | 0.70256 | 0 | 0.21191 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.8387 | 0% | CZ 0A | 9.179 | 1.4464 | 10.0385 | 0 | 0 | 22.5506 | 0 | 6.8017 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 72.2386 | 0% | CZ 0A | 2.6902 | 0.4239 | 0 | 0 | 0 | 6.6092 | 0 | 1.9935 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 15.5196 | 0% | CZ 0A | 0 | 0 | 0.10038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19286 | 0% | CZ 0A | 28.1637 | 4.4379 | 10.9721 | 0 | 0 | 69.1918 | 0 | 20.8696 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 183.5543 | 0%
CZ 0B | 0.28597 | 0.045068 | 0.098152 | 8.2041e-05 | 0 | 0.64526 | 0 | 0.21902 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.7884 | 0% | CZ 0B | 9.179 | 1.4466 | 10.0155 | 0.0026333 | 0 | 20.7115 | 0 | 7.0299 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 70.6075 | 0% | CZ 0B | 2.6902 | 0.42397 | 0 | 0.00077179 | 0 | 6.0702 | 0 | 2.0604 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 15.0483 | 0% | CZ 0B | 0 | 0 | 0.10015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19263 | 0% | CZ 0B | 28.1637 | 4.4385 | 10.9469 | 0.0080799 | 0 | 63.5487 | 0 | 21.5698 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 178.595 | 0%
CZ 1A | 0.28597 | 0.045075 | 0.10252 | 1.3674e-05 | 0 | 0.52138 | 0 | 0.20871 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.6585 | 2.061% | CZ 1A | 9.179 | 1.4468 | 10.461 | 0.00043889 | 0 | 16.7353 | 0 | 6.699 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 66.7441 | 2.061% | CZ 1A | 2.6902 | 0.42403 | 0 | 0.00012863 | 0 | 4.9048 | 0 | 1.9634 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 13.7854 | 2.061% | CZ 1A | 0 | 0 | 0.10461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19708 | 2.061% | CZ 1A | 28.1637 | 4.4392 | 11.4339 | 0.0013466 | 0 | 51.3488 | 0 | 20.5545 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 165.8607 | 2.061%
CZ 1B | 0.28597 | 0.045013 | 0.10267 | 0.003284 | 0 | 0.54281 | 0 | 0.21669 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.6913 | 0% | CZ 1B | 9.179 | 1.4448 | 10.4764 | 0.10797 | 0 | 17.4231 | 0 | 6.9553 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 67.809 | 0% | CZ 1B | 2.6902 | 0.42345 | 0 | 0.03055 | 0 | 5.1064 | 0 | 2.0385 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 14.092 | 0% | CZ 1B | 0 | 0 | 0.10476 | 3.7297e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19727 | 0% | CZ 1B | 28.1637 | 4.4331 | 11.4507 | 0.3239 | 0 | 53.459 | 0 | 21.3409 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 169.0906 | 0%
CZ 2A | 0.28597 | 0.045 | 0.10739 | 0.006039 | 0 | 0.44405 | 0 | 0.20961 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.5929 | 19.12% | CZ 2A | 9.179 | 1.4444 | 10.9586 | 0.2179 | 0 | 14.2532 | 0 | 6.728 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 65.0035 | 19.12% | CZ 2A | 2.6902 | 0.42333 | 0 | 0.053575 | 0 | 4.1774 | 0 | 1.9719 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 13.1192 | 19.12% | CZ 2A | 0 | 0 | 0.10959 | 0.00035103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20241 | 19.12% | CZ 2A | 28.1637 | 4.4318 | 11.9778 | 0.59924 | 0 | 43.7329 | 0 | 20.6433 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 159.468 | 19.12%
CZ 2B | 0.28597 | 0.045034 | 0.10828 | 0.0056133 | 0 | 0.35496 | 0 | 0.21887 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.5136 | 1.527% | CZ 2B | 9.179 | 1.4455 | 11.049 | 0.19311 | 0 | 11.3936 | 0 | 7.0251 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 62.5078 | 1.527% | CZ 2B | 2.6902 | 0.42365 | 0 | 0.051067 | 0 | 3.3393 | 0 | 2.0589 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 12.366 | 1.527% | CZ 2B | 0 | 0 | 0.11049 | 0.00018868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20315 | 1.527% | CZ 2B | 28.1637 | 4.4352 | 12.0766 | 0.55524 | 0 | 34.9588 | 0 | 21.555 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 151.6638 | 1.527%
CZ 3A | 0.28217 | 0.045027 | 0.11917 | 0.048133 | 0 | 0.28986 | 0 | 0.2083 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.4875 | 16.87% | CZ 3A | 9.0572 | 1.4453 | 12.1607 | 1.832 | 0 | 9.304 | 0 | 6.6861 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 62.7077 | 16.87% | CZ 3A | 2.6545 | 0.42358 | 0 | 0.41419 | 0 | 2.7269 | 0 | 1.9596 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 11.9816 | 16.87% | CZ 3A | 0 | 0 | 0.12161 | 0.0041882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21827 | 16.87% | CZ 3A | 27.79 | 4.4345 | 13.2916 | 4.794 | 0 | 28.5475 | 0 | 20.5147 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 149.2915 | 16.87%
CZ 3B | 0.2821 | 0.04502 | 0.116 | 0.018752 | 0 | 0.2852 | 0 | 0.21711 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.4591 | 6.686% | CZ 3B | 9.0547 | 1.445 | 11.8369 | 0.67257 | 0 | 9.1544 | 0 | 6.9689 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 61.355 | 6.686% | CZ 3B | 2.6538 | 0.42352 | 0 | 0.1669 | 0 | 2.683 | 0 | 2.0425 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 11.7725 | 6.686% | CZ 3B | 0 | 0 | 0.11837 | 0.0010311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21187 | 6.686% | CZ 3B | 27.7826 | 4.4338 | 12.9377 | 1.86 | 0 | 28.0883 | 0 | 21.3827 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 146.4042 | 6.686%
CZ 3C | 0.28597 | 0.045013 | 0.11896 | 0.0036527 | 0 | 0.23155 | 0 | 0.20562 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.3856 | 0.9608% | CZ 3C | 9.179 | 1.4448 | 12.1385 | 0.12837 | 0 | 7.4322 | 0 | 6.5998 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 59.1452 | 0.9608% | CZ 3C | 2.6902 | 0.42345 | 0 | 0.032865 | 0 | 2.1782 | 0 | 1.9343 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 11.0619 | 0.9608% | CZ 3C | 0 | 0 | 0.12139 | 0.00016235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21402 | 0.9608% | CZ 3C | 28.1637 | 4.4331 | 13.2674 | 0.36181 | 0 | 22.804 | 0 | 20.2501 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 139.1995 | 0.9608%
CZ 4A | 0.28198 | 0.044952 | 0.12944 | 0.11479 | 0 | 0.21644 | 0 | 0.20456 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.487 | 19.16% | CZ 4A | 9.051 | 1.4429 | 13.2083 | 4.4606 | 0 | 6.9474 | 0 | 6.566 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 63.8987 | 19.16% | CZ 4A | 2.6527 | 0.42288 | 0 | 0.97548 | 0 | 2.0362 | 0 | 1.9244 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 11.8145 | 19.16% | CZ 4A | 0 | 0 | 0.13208 | 0.011323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23588 | 19.16% | CZ 4A | 27.7711 | 4.4271 | 14.4366 | 11.4498 | 0 | 21.3167 | 0 | 20.1464 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 149.4671 | 19.16%
CZ 4B | 0.28193 | 0.044993 | 0.12623 | 0.04694 | 0 | 0.22287 | 0 | 0.21815 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.436 | 0.8608% | CZ 4B | 9.0495 | 1.4442 | 12.8803 | 1.739 | 0 | 7.1537 | 0 | 7.0023 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 61.4914 | 0.8608% | CZ 4B | 2.6523 | 0.42326 | 0 | 0.41033 | 0 | 2.0966 | 0 | 2.0522 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 11.4376 | 0.8608% | CZ 4B | 0 | 0 | 0.1288 | 0.0033896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22466 | 0.8608% | CZ 4B | 27.7664 | 4.4311 | 14.0781 | 4.6663 | 0 | 21.9496 | 0 | 21.485 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 144.2958 | 0.8608%
CZ 4C | 0.28211 | 0.044904 | 0.13294 | 0.05693 | 0 | 0.14637 | 0 | 0.20469 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.3628 | 1.635% | CZ 4C | 9.055 | 1.4413 | 13.5652 | 2.229 | 0 | 4.6981 | 0 | 6.57 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 59.7811 | 1.635% | CZ 4C | 2.6539 | 0.42243 | 0 | 0.48153 | 0 | 1.3769 | 0 | 1.9255 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 10.6632 | 1.635% | CZ 4C | 0 | 0 | 0.13565 | 0.00586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23398 | 1.635% | CZ 4C | 27.7832 | 4.4224 | 14.8268 | 5.6816 | 0 | 14.4151 | 0 | 20.1586 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 137.207 | 1.635%
CZ 5A | 0.28198 | 0.044972 | 0.13961 | 0.19967 | 0 | 0.15692 | 0 | 0.20421 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.5222 | 17.17% | CZ 5A | 9.051 | 1.4435 | 14.2456 | 7.7431 | 0 | 5.0369 | 0 | 6.5546 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 66.2972 | 17.17% | CZ 5A | 2.6527 | 0.42307 | 0 | 1.699 | 0 | 1.4762 | 0 | 1.921 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 11.9749 | 17.17% | CZ 5A | 0 | 0 | 0.14246 | 0.019462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25439 | 17.17% | CZ 5A | 27.7711 | 4.4291 | 15.5704 | 19.9137 | 0 | 15.4547 | 0 | 20.1114 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 153.1697 | 17.17%
CZ 5B | 0.282 | 0.044972 | 0.13662 | 0.11342 | 0 | 0.17704 | 0 | 0.21666 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.4656 | 5.989% | CZ 5B | 9.0515 | 1.4435 | 13.9406 | 4.3099 | 0 | 5.6828 | 0 | 6.9542 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 63.6049 | 5.989% | CZ 5B | 2.6528 | 0.42307 | 0 | 0.97702 | 0 | 1.6655 | 0 | 2.0382 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 11.5595 | 5.989% | CZ 5B | 0 | 0 | 0.13941 | 0.0097629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24164 | 5.989% | CZ 5B | 27.7725 | 4.4291 | 15.2371 | 11.2955 | 0 | 17.4363 | 0 | 21.3375 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 147.4273 | 5.989%
CZ 5C | 0.28214 | 0.044897 | 0.13872 | 0.067175 | 0 | 0.12334 | 0 | 0.20287 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.354 | 0.1299% | CZ 5C | 9.0561 | 1.4411 | 14.1554 | 2.7069 | 0 | 3.9588 | 0 | 6.5118 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 60.0525 | 0.1299% | CZ 5C | 2.6542 | 0.42236 | 0 | 0.55787 | 0 | 1.1603 | 0 | 1.9085 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 10.506 | 0.1299% | CZ 5C | 0 | 0 | 0.14155 | 0.0080341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24206 | 0.1299% | CZ 5C | 27.7866 | 4.4217 | 15.4718 | 6.7185 | 0 | 12.1467 | 0 | 19.9801 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 136.4448 | 0.1299%
CZ 6A | 0.28201 | 0.044945 | 0.14724 | 0.32715 | 0 | 0.1558 | 0 | 0.20694 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.659 | 5.175% | CZ 6A | 9.0519 | 1.4426 | 15.0246 | 12.6005 | 0 | 5.0009 | 0 | 6.6424 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 71.9854 | 5.175% | CZ 6A | 2.653 | 0.42281 | 0 | 2.7952 | 0 | 1.4657 | 0 | 1.9468 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 13.0863 | 5.175% | CZ 6A | 0 | 0 | 0.15025 | 0.030634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.27335 | 5.175% | CZ 6A | 27.7738 | 4.4264 | 16.4219 | 32.6108 | 0 | 15.3443 | 0 | 20.3808 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 166.8773 | 5.175%
CZ 6B | 0.28207 | 0.044918 | 0.14524 | 0.21189 | 0 | 0.13524 | 0 | 0.21296 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.5272 | 1.6% | CZ 6B | 9.0539 | 1.4418 | 14.8208 | 8.0927 | 0 | 4.3408 | 0 | 6.8355 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 66.808 | 1.6% | CZ 6B | 2.6535 | 0.42255 | 0 | 1.8197 | 0 | 1.2722 | 0 | 2.0034 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 11.9742 | 1.6% | CZ 6B | 0 | 0 | 0.14821 | 0.018839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25952 | 1.6% | CZ 6B | 27.7799 | 4.4237 | 16.1991 | 21.1094 | 0 | 13.319 | 0 | 20.9733 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 153.7236 | 1.6%
CZ 7 | 0.28202 | 0.04489 | 0.1563 | 0.37832 | 0 | 0.13264 | 0 | 0.20633 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.6954 | 0.993% | CZ 7 | 9.0521 | 1.4409 | 15.9491 | 14.8805 | 0 | 4.2575 | 0 | 6.6226 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 74.4252 | 0.993% | CZ 7 | 2.653 | 0.4223 | 0 | 3.1908 | 0 | 1.2478 | 0 | 1.941 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 13.2577 | 0.993% | CZ 7 | 0 | 0 | 0.15949 | 0.039936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2919 | 0.993% | CZ 7 | 27.7745 | 4.421 | 17.4324 | 37.7691 | 0 | 13.0631 | 0 | 20.3202 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 170.6996 | 0.993%
CZ 8 | 0.28278 | 0.044644 | 0.16863 | 0.54844 | 0 | 0.091619 | 0 | 0.20538 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.8364 | 0.06422% | CZ 8 | 9.0765 | 1.433 | 17.2069 | 21.7826 | 0 | 2.9408 | 0 | 6.5921 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 81.2544 | 0.06422% | CZ 8 | 2.6602 | 0.41998 | 0 | 4.5974 | 0 | 0.86189 | 0 | 1.932 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 14.2743 | 0.06422% | CZ 8 | 0 | 0 | 0.17207 | 0.060965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.32551 | 0.06422% | CZ 8 | 27.8492 | 4.3968 | 18.8072 | 54.7931 | 0 | 9.0232 | 0 | 20.2266 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 185.0153 | 0.06422%
US Weighted | 0.28297 | 0.044985 | 0.1253 | 0.099568 | 0 | 0.26635 | 0 | 0.20837 | 0 | 0.00017776 | 0 | 0.17132 | 0 | 0.11009 | 0 | 0.21328 | 1.5224 | 100% | US Weighted | 9.0828 | 1.4439 | 12.7856 | 3.8403 | 0 | 8.5493 | 0 | 6.6881 | 0 | 0.0057056 | 0 | 5.4989 | 0 | 9.8721 | 0 | 6.8458 | 64.6126 | 100% | US Weighted | 2.662 | 0.42319 | 0 | 0.85001 | 0 | 2.5057 | 0 | 1.9602 | 0 | 0.0016722 | 0 | 1.6116 | 0 | 0.18317 | 0 | 2.0064 | 12.2039 | 100% | US Weighted | 0 | 0 | 0.12786 | 0.0094004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22973 | 100% | US Weighted | 27.8686 | 4.4304 | 13.9747 | 9.9262 | 0 | 26.2318 | 0 | 20.5211 | 0 | 0.017506 | 0 | 16.8721 | 0 | 12.0248 | 0 | 21.0049 | 152.872 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.3405 | 0.06523 | 0.099285 | 0 | 0 | 0.80249 | 0 | 0.22019 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 2.03 | 0% | CZ 0A | 10.9295 | 2.0937 | 10.1311 | 0 | 0 | 25.758 | 0 | 7.0677 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 78.4423 | 0% | CZ 0A | 3.2032 | 0.61364 | 0 | 0 | 0 | 7.5492 | 0 | 2.0714 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 17.3107 | 0% | CZ 0A | 0 | 0 | 0.10131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19378 | 0% | CZ 0A | 33.5348 | 6.4242 | 11.0733 | 0 | 0 | 79.0331 | 0 | 21.6857 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 202.4061 | 0%
CZ 0B | 0.3405 | 0.065243 | 0.099076 | 5.4694e-05 | 0 | 0.73657 | 0 | 0.22648 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.9703 | 0% | CZ 0B | 10.9295 | 2.0942 | 10.1098 | 0.0017556 | 0 | 23.6424 | 0 | 7.2696 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 76.5095 | 0% | CZ 0B | 3.2032 | 0.61376 | 0 | 0.00051453 | 0 | 6.9292 | 0 | 2.1306 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 16.7504 | 0% | CZ 0B | 0 | 0 | 0.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19357 | 0% | CZ 0B | 33.5348 | 6.4255 | 11.05 | 0.0053866 | 0 | 72.5416 | 0 | 22.3051 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 196.5175 | 0%
CZ 1A | 0.3405 | 0.06525 | 0.10345 | 0 | 0 | 0.60587 | 0 | 0.21852 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.8359 | 2.061% | CZ 1A | 10.9295 | 2.0944 | 10.5558 | 0 | 0 | 19.4472 | 0 | 7.0141 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 72.5034 | 2.061% | CZ 1A | 3.2032 | 0.61383 | 0 | 0 | 0 | 5.6997 | 0 | 2.0557 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 15.4456 | 2.061% | CZ 1A | 0 | 0 | 0.10556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19803 | 2.061% | CZ 1A | 33.5348 | 6.4262 | 11.5375 | 0 | 0 | 59.6697 | 0 | 21.5214 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 183.3447 | 2.061%
CZ 1B | 0.3405 | 0.065168 | 0.10352 | 0.0029758 | 0 | 0.61934 | 0 | 0.22337 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.8572 | 0% | CZ 1B | 10.9295 | 2.0918 | 10.5633 | 0.096117 | 0 | 19.8793 | 0 | 7.1697 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 73.192 | 0% | CZ 1B | 3.2032 | 0.61306 | 0 | 0.027913 | 0 | 5.8263 | 0 | 2.1013 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 15.645 | 0% | CZ 1B | 0 | 0 | 0.10563 | 8.7757e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19811 | 0% | CZ 1B | 33.5348 | 6.4181 | 11.5457 | 0.29318 | 0 | 60.9955 | 0 | 21.9987 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 185.4411 | 0%
CZ 2A | 0.3405 | 0.065147 | 0.10818 | 0.0061169 | 0 | 0.51904 | 0 | 0.21768 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.759 | 19.12% | CZ 2A | 10.9295 | 2.0911 | 11.0387 | 0.21198 | 0 | 16.6601 | 0 | 6.9871 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 70.3808 | 19.12% | CZ 2A | 3.2032 | 0.61286 | 0 | 0.05544 | 0 | 4.8828 | 0 | 2.0478 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.6753 | 19.12% | CZ 2A | 0 | 0 | 0.11039 | 0.00022817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20309 | 19.12% | CZ 2A | 33.5348 | 6.4161 | 12.0653 | 0.60534 | 0 | 51.1179 | 0 | 21.4385 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 175.8331 | 19.12%
CZ 2B | 0.3405 | 0.065195 | 0.10894 | 0.005673 | 0 | 0.42847 | 0 | 0.22859 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6797 | 1.527% | CZ 2B | 10.9295 | 2.0926 | 11.1159 | 0.18916 | 0 | 13.7528 | 0 | 7.3371 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.8795 | 1.527% | CZ 2B | 3.2032 | 0.61331 | 0 | 0.052417 | 0 | 4.0307 | 0 | 2.1504 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.9233 | 1.527% | CZ 2B | 0 | 0 | 0.11116 | 0.00010311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20373 | 1.527% | CZ 2B | 33.5348 | 6.4208 | 12.1497 | 0.56003 | 0 | 42.1977 | 0 | 22.5125 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 168.0307 | 1.527%
CZ 3A | 0.3405 | 0.065182 | 0.11959 | 0.051121 | 0 | 0.34822 | 0 | 0.21619 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6431 | 16.87% | CZ 3A | 10.9295 | 2.0922 | 12.203 | 1.8849 | 0 | 11.177 | 0 | 6.9391 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.6881 | 16.87% | CZ 3A | 3.2032 | 0.61319 | 0 | 0.44809 | 0 | 3.2758 | 0 | 2.0337 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.4472 | 16.87% | CZ 3A | 0 | 0 | 0.12203 | 0.0035607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21806 | 16.87% | CZ 3A | 33.5348 | 6.4194 | 13.3379 | 5.0802 | 0 | 34.2943 | 0 | 21.2911 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 164.6129 | 16.87%
CZ 3B | 0.3405 | 0.065182 | 0.11647 | 0.018025 | 0 | 0.33476 | 0 | 0.22596 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6032 | 6.686% | CZ 3B | 10.9295 | 2.0922 | 11.8842 | 0.61992 | 0 | 10.7451 | 0 | 7.2529 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 65.9862 | 6.686% | CZ 3B | 3.2032 | 0.61319 | 0 | 0.16401 | 0 | 3.1492 | 0 | 2.1257 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.1285 | 6.686% | CZ 3B | 0 | 0 | 0.11884 | 0.00060333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21192 | 6.686% | CZ 3B | 33.5348 | 6.4194 | 12.9895 | 1.7829 | 0 | 32.9692 | 0 | 22.2539 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 160.6049 | 6.686%
CZ 3C | 0.3405 | 0.065168 | 0.11909 | 0.0035145 | 0 | 0.28435 | 0 | 0.21324 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.5282 | 0.9608% | CZ 3C | 10.9295 | 2.0918 | 12.1521 | 0.11762 | 0 | 9.1272 | 0 | 6.8445 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 63.725 | 0.9608% | CZ 3C | 3.2032 | 0.61306 | 0 | 0.032415 | 0 | 2.675 | 0 | 2.006 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 12.4029 | 0.9608% | CZ 3C | 0 | 0 | 0.12152 | 7.0205e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21406 | 0.9608% | CZ 3C | 33.5348 | 6.4181 | 13.2823 | 0.34703 | 0 | 28.0048 | 0 | 21.0009 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 153.243 | 0.9608%
CZ 4A | 0.3405 | 0.065079 | 0.12963 | 0.12773 | 0 | 0.25944 | 0 | 0.21285 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6376 | 19.16% | CZ 4A | 10.9295 | 2.0889 | 13.228 | 4.7924 | 0 | 8.3275 | 0 | 6.832 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.6607 | 19.16% | CZ 4A | 3.2032 | 0.61222 | 0 | 1.1084 | 0 | 2.4407 | 0 | 2.0023 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.24 | 19.16% | CZ 4A | 0 | 0 | 0.13228 | 0.010105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23486 | 19.16% | CZ 4A | 33.5348 | 6.4093 | 14.4582 | 12.7085 | 0 | 25.5512 | 0 | 20.9625 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 164.2797 | 19.16%
CZ 4B | 0.3405 | 0.065134 | 0.12646 | 0.046436 | 0 | 0.2598 | 0 | 0.22903 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.5697 | 0.8608% | CZ 4B | 10.9295 | 2.0907 | 12.9042 | 1.6364 | 0 | 8.3391 | 0 | 7.3514 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 65.7136 | 0.8608% | CZ 4B | 3.2032 | 0.61274 | 0 | 0.41722 | 0 | 2.4441 | 0 | 2.1546 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 12.705 | 0.8608% | CZ 4B | 0 | 0 | 0.12904 | 0.0021281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22364 | 0.8608% | CZ 4B | 33.5348 | 6.4147 | 14.1043 | 4.6004 | 0 | 25.5869 | 0 | 22.5563 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 157.4525 | 0.8608%
CZ 4C | 0.3405 | 0.065004 | 0.13294 | 0.060896 | 0 | 0.18024 | 0 | 0.21252 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.4944 | 1.635% | CZ 4C | 10.9295 | 2.0865 | 13.565 | 2.2674 | 0 | 5.7852 | 0 | 6.8215 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 63.9174 | 1.635% | CZ 4C | 3.2032 | 0.61151 | 0 | 0.5308 | 0 | 1.6956 | 0 | 1.9993 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 11.9135 | 1.635% | CZ 4C | 0 | 0 | 0.13565 | 0.0045634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23268 | 1.635% | CZ 4C | 33.5348 | 6.4019 | 14.8265 | 6.0557 | 0 | 17.7508 | 0 | 20.9302 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 150.1551 | 1.635%
CZ 5A | 0.3405 | 0.0651 | 0.13965 | 0.22279 | 0 | 0.1939 | 0 | 0.21281 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6771 | 17.17% | CZ 5A | 10.9295 | 2.0896 | 14.2495 | 8.4245 | 0 | 6.2239 | 0 | 6.8309 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 71.2102 | 17.17% | CZ 5A | 3.2032 | 0.61241 | 0 | 1.9246 | 0 | 1.8241 | 0 | 2.002 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.4395 | 17.17% | CZ 5A | 0 | 0 | 0.1425 | 0.018578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25354 | 17.17% | CZ 5A | 33.5348 | 6.4114 | 15.5747 | 22.179 | 0 | 19.0967 | 0 | 20.9591 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 168.4109 | 17.17%
CZ 5B | 0.3405 | 0.065106 | 0.13662 | 0.11656 | 0 | 0.21881 | 0 | 0.22759 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6075 | 5.989% | CZ 5B | 10.9295 | 2.0898 | 13.941 | 4.2757 | 0 | 7.0233 | 0 | 7.3051 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.0268 | 5.989% | CZ 5B | 3.2032 | 0.61248 | 0 | 1.0247 | 0 | 2.0584 | 0 | 2.141 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 12.913 | 5.989% | CZ 5B | 0 | 0 | 0.13941 | 0.007795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23968 | 5.989% | CZ 5B | 33.5348 | 6.412 | 15.2376 | 11.5793 | 0 | 21.5496 | 0 | 22.4142 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 161.3827 | 5.989%
CZ 5C | 0.3405 | 0.065004 | 0.1387 | 0.064588 | 0 | 0.15951 | 0 | 0.211 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.4816 | 0.1299% | CZ 5C | 10.9295 | 2.0865 | 14.1532 | 2.4791 | 0 | 5.1199 | 0 | 6.7727 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 64.0033 | 0.1299% | CZ 5C | 3.2032 | 0.61151 | 0 | 0.55299 | 0 | 1.5005 | 0 | 1.985 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 11.7264 | 0.1299% | CZ 5C | 0 | 0 | 0.14153 | 0.0059236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23993 | 0.1299% | CZ 5C | 33.5348 | 6.4019 | 15.4694 | 6.4367 | 0 | 15.7093 | 0 | 20.7807 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 148.988 | 0.1299%
CZ 6A | 0.3405 | 0.065072 | 0.14728 | 0.36962 | 0 | 0.19202 | 0 | 0.21644 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.8333 | 5.175% | CZ 6A | 10.9295 | 2.0887 | 15.029 | 13.9369 | 0 | 6.1633 | 0 | 6.9472 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 77.5569 | 5.175% | CZ 6A | 3.2032 | 0.61216 | 0 | 3.1983 | 0 | 1.8064 | 0 | 2.0361 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.7293 | 5.175% | CZ 6A | 0 | 0 | 0.15029 | 0.030243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.273 | 5.175% | CZ 6A | 33.5348 | 6.4087 | 16.4267 | 36.7885 | 0 | 18.9109 | 0 | 21.316 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 184.0407 | 5.175%
CZ 6B | 0.3405 | 0.065024 | 0.14525 | 0.23016 | 0 | 0.16868 | 0 | 0.22315 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6751 | 1.6% | CZ 6B | 10.9295 | 2.0871 | 14.8217 | 8.57 | 0 | 5.4144 | 0 | 7.1627 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 71.4477 | 1.6% | CZ 6B | 3.2032 | 0.61171 | 0 | 2.0062 | 0 | 1.5869 | 0 | 2.0993 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.3804 | 1.6% | CZ 6B | 0 | 0 | 0.14822 | 0.017249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25794 | 1.6% | CZ 6B | 33.5348 | 6.404 | 16.2001 | 22.8882 | 0 | 16.6128 | 0 | 21.9772 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 168.2722 | 1.6%
CZ 7 | 0.3405 | 0.064983 | 0.15632 | 0.40696 | 0 | 0.16615 | 0 | 0.21564 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.8529 | 0.993% | CZ 7 | 10.9295 | 2.0858 | 15.9509 | 15.7166 | 0 | 5.333 | 0 | 6.9215 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 79.3996 | 0.993% | CZ 7 | 3.2032 | 0.61132 | 0 | 3.4714 | 0 | 1.563 | 0 | 2.0286 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.7507 | 0.993% | CZ 7 | 0 | 0 | 0.15951 | 0.03872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.2907 | 0.993% | CZ 7 | 33.5348 | 6.3999 | 17.4343 | 40.5747 | 0 | 16.363 | 0 | 21.2372 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 186.1991 | 0.993%
CZ 8 | 0.3405 | 0.064628 | 0.16867 | 0.55603 | 0 | 0.11233 | 0 | 0.21305 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.9576 | 0.06422% | CZ 8 | 10.9295 | 2.0744 | 17.2109 | 21.8808 | 0 | 3.6057 | 0 | 6.8383 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 85.0019 | 0.06422% | CZ 8 | 3.2032 | 0.60798 | 0 | 4.6883 | 0 | 1.0568 | 0 | 2.0042 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 15.4336 | 0.06422% | CZ 8 | 0 | 0 | 0.17211 | 0.058843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.32342 | 0.06422% | CZ 8 | 33.5348 | 6.3649 | 18.8115 | 55.5133 | 0 | 11.0633 | 0 | 20.982 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 196.925 | 0.06422%
US Weighted | 0.3405 | 0.065124 | 0.12563 | 0.10951 | 0 | 0.31798 | 0 | 0.21696 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.678 | 100% | US Weighted | 10.9295 | 2.0903 | 12.8193 | 4.1075 | 0 | 10.2065 | 0 | 6.964 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 69.5794 | 100% | US Weighted | 3.2032 | 0.61265 | 0 | 0.95051 | 0 | 2.9913 | 0 | 2.041 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.6719 | 100% | US Weighted | 0 | 0 | 0.12819 | 0.0086435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22931 | 100% | US Weighted | 33.5348 | 6.4138 | 14.0115 | 10.8957 | 0 | 31.3164 | 0 | 21.3674 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 168.1948 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 43202 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.3405 | 0.06523 | 0.099289 | 0 | 0 | 0.92693 | 0 | 0.22122 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 2.1555 | 0% | CZ 0A | 10.9295 | 2.0937 | 10.1315 | 0 | 0 | 29.7526 | 0 | 7.1006 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 82.4703 | 0% | CZ 0A | 3.2032 | 0.61364 | 0 | 0 | 0 | 8.72 | 0 | 2.0811 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 18.4911 | 0% | CZ 0A | 0 | 0 | 0.10132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19379 | 0% | CZ 0A | 33.5348 | 6.4242 | 11.0738 | 0 | 0 | 91.2895 | 0 | 21.7866 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 214.764 | 0%
CZ 0B | 0.3405 | 0.065243 | 0.09908 | 2.7347e-05 | 0 | 0.83617 | 0 | 0.22765 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 2.071 | 0% | CZ 0B | 10.9295 | 2.0942 | 10.1102 | 0.00087778 | 0 | 26.8392 | 0 | 7.3071 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 79.7434 | 0% | CZ 0B | 3.2032 | 0.61376 | 0 | 0.00025726 | 0 | 7.8661 | 0 | 2.1416 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 17.6981 | 0% | CZ 0B | 0 | 0 | 0.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19357 | 0% | CZ 0B | 33.5348 | 6.4255 | 11.0505 | 0.0026933 | 0 | 82.3505 | 0 | 22.4202 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 206.4394 | 0%
CZ 1A | 0.3405 | 0.06525 | 0.10345 | 0 | 0 | 0.67128 | 0 | 0.21872 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.9015 | 2.061% | CZ 1A | 10.9295 | 2.0944 | 10.5563 | 0 | 0 | 21.5467 | 0 | 7.0205 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 74.6096 | 2.061% | CZ 1A | 3.2032 | 0.61383 | 0 | 0 | 0 | 6.315 | 0 | 2.0576 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 16.0628 | 2.061% | CZ 1A | 0 | 0 | 0.10556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.19803 | 2.061% | CZ 1A | 33.5348 | 6.4262 | 11.538 | 0 | 0 | 66.1114 | 0 | 21.5409 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 189.8064 | 2.061%
CZ 1B | 0.3405 | 0.065168 | 0.10353 | 0.0076727 | 0 | 0.69303 | 0 | 0.22405 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.9363 | 0% | CZ 1B | 10.9295 | 2.0918 | 10.5644 | 0.29996 | 0 | 22.2447 | 0 | 7.1917 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 75.7843 | 0% | CZ 1B | 3.2032 | 0.61306 | 0 | 0.064959 | 0 | 6.5196 | 0 | 2.1078 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 16.3817 | 0% | CZ 1B | 0 | 0 | 0.10564 | 0.00078323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.1989 | 0% | CZ 1B | 33.5348 | 6.4181 | 11.5469 | 0.76566 | 0 | 68.2532 | 0 | 22.0661 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 193.2399 | 0%
CZ 2A | 0.3405 | 0.065147 | 0.10823 | 0.019334 | 0 | 0.57952 | 0 | 0.219 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.8341 | 19.12% | CZ 2A | 10.9295 | 2.0911 | 11.0438 | 0.80705 | 0 | 18.6013 | 0 | 7.0293 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 72.9643 | 19.12% | CZ 2A | 3.2032 | 0.61286 | 0 | 0.1568 | 0 | 5.4517 | 0 | 2.0602 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 15.3579 | 19.12% | CZ 2A | 0 | 0 | 0.11044 | 0.0027205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20563 | 19.12% | CZ 2A | 33.5348 | 6.4161 | 12.0708 | 1.9389 | 0 | 57.0741 | 0 | 21.5678 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 183.2576 | 19.12%
CZ 2B | 0.3405 | 0.065195 | 0.10899 | 0.02041 | 0 | 0.4633 | 0 | 0.22996 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.7307 | 1.527% | CZ 2B | 10.9295 | 2.0926 | 11.1214 | 0.79017 | 0 | 14.8709 | 0 | 7.3813 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 69.6482 | 1.527% | CZ 2B | 3.2032 | 0.61331 | 0 | 0.17385 | 0 | 4.3584 | 0 | 2.1633 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.3853 | 1.527% | CZ 2B | 0 | 0 | 0.11121 | 0.0019701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.20566 | 1.527% | CZ 2B | 33.5348 | 6.4208 | 12.1557 | 2.0353 | 0 | 45.6283 | 0 | 22.6478 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 173.0779 | 1.527%
CZ 3A | 0.3405 | 0.065182 | 0.11967 | 0.099916 | 0 | 0.37199 | 0 | 0.21772 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.7173 | 16.87% | CZ 3A | 10.9295 | 2.0922 | 12.2114 | 4.2555 | 0 | 11.9402 | 0 | 6.9885 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 70.8796 | 16.87% | CZ 3A | 3.2032 | 0.61319 | 0 | 0.79893 | 0 | 3.4995 | 0 | 2.0482 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.0362 | 16.87% | CZ 3A | 0 | 0 | 0.12211 | 0.015296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.22988 | 16.87% | CZ 3A | 33.5348 | 6.4194 | 13.347 | 10.0358 | 0 | 36.6361 | 0 | 21.4426 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 172.0709 | 16.87%
CZ 3B | 0.3405 | 0.065182 | 0.11655 | 0.046143 | 0 | 0.36095 | 0 | 0.22771 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6594 | 6.686% | CZ 3B | 10.9295 | 2.0922 | 11.8926 | 1.9742 | 0 | 11.5858 | 0 | 7.3088 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.2454 | 6.686% | CZ 3B | 3.2032 | 0.61319 | 0 | 0.36776 | 0 | 3.3956 | 0 | 2.1421 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.5951 | 6.686% | CZ 3B | 0 | 0 | 0.11893 | 0.0071939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21859 | 6.686% | CZ 3B | 33.5348 | 6.4194 | 12.9986 | 4.6363 | 0 | 35.5487 | 0 | 22.4256 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 166.2186 | 6.686%
CZ 3C | 0.3405 | 0.065168 | 0.1192 | 0.013623 | 0 | 0.31247 | 0 | 0.21889 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.5722 | 0.9608% | CZ 3C | 10.9295 | 2.0918 | 12.1637 | 0.59727 | 0 | 10.0297 | 0 | 7.026 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 65.3003 | 0.9608% | CZ 3C | 3.2032 | 0.61306 | 0 | 0.10664 | 0 | 2.9395 | 0 | 2.0592 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 12.7948 | 0.9608% | CZ 3C | 0 | 0 | 0.12164 | 0.0023343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.21644 | 0.9608% | CZ 3C | 33.5348 | 6.4181 | 13.295 | 1.3715 | 0 | 30.7741 | 0 | 21.5577 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 157.6064 | 0.9608%
CZ 4A | 0.3405 | 0.065079 | 0.1298 | 0.23731 | 0 | 0.25891 | 0 | 0.21439 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.7483 | 19.16% | CZ 4A | 10.9295 | 2.0889 | 13.2447 | 10.1188 | 0 | 8.3104 | 0 | 6.8816 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 74.0362 | 19.16% | CZ 4A | 3.2032 | 0.61222 | 0 | 1.896 | 0 | 2.4356 | 0 | 2.0169 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.0372 | 19.16% | CZ 4A | 0 | 0 | 0.13245 | 0.036496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26141 | 19.16% | CZ 4A | 33.5348 | 6.4093 | 14.4764 | 23.8385 | 0 | 25.4987 | 0 | 21.1147 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 175.5276 | 19.16%
CZ 4B | 0.3405 | 0.065134 | 0.12661 | 0.10794 | 0 | 0.26051 | 0 | 0.23106 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.6341 | 0.8608% | CZ 4B | 10.9295 | 2.0907 | 12.9198 | 4.62 | 0 | 8.362 | 0 | 7.4164 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 68.8006 | 0.8608% | CZ 4B | 3.2032 | 0.61274 | 0 | 0.86003 | 0 | 2.4507 | 0 | 2.1736 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.1735 | 0.8608% | CZ 4B | 0 | 0 | 0.1292 | 0.016856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.23853 | 0.8608% | CZ 4B | 33.5348 | 6.4147 | 14.1213 | 10.846 | 0 | 25.6569 | 0 | 22.7556 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 163.9844 | 0.8608%
CZ 4C | 0.3405 | 0.065004 | 0.13311 | 0.14143 | 0 | 0.16263 | 0 | 0.21353 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.5585 | 1.635% | CZ 4C | 10.9295 | 2.0865 | 13.583 | 6.2854 | 0 | 5.2199 | 0 | 6.8537 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.4203 | 1.635% | CZ 4C | 3.2032 | 0.61151 | 0 | 1.0956 | 0 | 1.5299 | 0 | 2.0087 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 12.3221 | 1.635% | CZ 4C | 0 | 0 | 0.13583 | 0.025471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.25377 | 1.635% | CZ 4C | 33.5348 | 6.4019 | 14.8462 | 14.254 | 0 | 16.0163 | 0 | 21.0292 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 156.7376 | 1.635%
CZ 5A | 0.3405 | 0.0651 | 0.13975 | 0.3752 | 0 | 0.18526 | 0 | 0.21307 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.8212 | 17.17% | CZ 5A | 10.9295 | 2.0896 | 14.26 | 15.7169 | 0 | 5.9465 | 0 | 6.839 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 78.2439 | 17.17% | CZ 5A | 3.2032 | 0.61241 | 0 | 3.0356 | 0 | 1.7428 | 0 | 2.0044 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.4716 | 17.17% | CZ 5A | 0 | 0 | 0.1426 | 0.053595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.28867 | 17.17% | CZ 5A | 33.5348 | 6.4114 | 15.5862 | 37.6374 | 0 | 18.2457 | 0 | 20.984 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 183.0546 | 17.17%
CZ 5B | 0.3405 | 0.065106 | 0.13674 | 0.22346 | 0 | 0.20769 | 0 | 0.22795 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.7038 | 5.989% | CZ 5B | 10.9295 | 2.0898 | 13.9527 | 9.3891 | 0 | 6.6665 | 0 | 7.3167 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 72.8066 | 5.989% | CZ 5B | 3.2032 | 0.61248 | 0 | 1.804 | 0 | 1.9538 | 0 | 2.1444 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 13.5911 | 5.989% | CZ 5B | 0 | 0 | 0.13953 | 0.032338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26434 | 5.989% | CZ 5B | 33.5348 | 6.412 | 15.2503 | 22.4206 | 0 | 20.4548 | 0 | 22.4499 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 171.1775 | 5.989%
CZ 5C | 0.3405 | 0.065004 | 0.13884 | 0.15888 | 0 | 0.13635 | 0 | 0.21096 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.5529 | 0.1299% | CZ 5C | 10.9295 | 2.0865 | 14.167 | 7.1828 | 0 | 4.3764 | 0 | 6.7714 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 67.9759 | 0.1299% | CZ 5C | 3.2032 | 0.61151 | 0 | 1.2145 | 0 | 1.2826 | 0 | 1.9846 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 12.1696 | 0.1299% | CZ 5C | 0 | 0 | 0.14167 | 0.03039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.26453 | 0.1299% | CZ 5C | 33.5348 | 6.4019 | 15.4845 | 16.036 | 0 | 13.428 | 0 | 20.7767 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 156.3171 | 0.1299%
CZ 6A | 0.3405 | 0.065072 | 0.14743 | 0.57728 | 0 | 0.18396 | 0 | 0.21558 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 2.0322 | 5.175% | CZ 6A | 10.9295 | 2.0887 | 15.0441 | 23.9268 | 0 | 5.9046 | 0 | 6.9198 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 87.2759 | 5.175% | CZ 6A | 3.2032 | 0.61216 | 0 | 4.7048 | 0 | 1.7305 | 0 | 2.0281 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 16.1519 | 5.175% | CZ 6A | 0 | 0 | 0.15044 | 0.078742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.32165 | 5.175% | CZ 6A | 33.5348 | 6.4087 | 16.4433 | 57.8606 | 0 | 18.117 | 0 | 21.2318 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 204.2514 | 5.175%
CZ 6B | 0.3405 | 0.065024 | 0.14542 | 0.39528 | 0 | 0.15203 | 0 | 0.22224 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.8228 | 1.6% | CZ 6B | 10.9295 | 2.0871 | 14.839 | 16.5242 | 0 | 4.8798 | 0 | 7.1335 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 78.8555 | 1.6% | CZ 6B | 3.2032 | 0.61171 | 0 | 3.2025 | 0 | 1.4302 | 0 | 2.0907 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.4115 | 1.6% | CZ 6B | 0 | 0 | 0.14839 | 0.055973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.29684 | 1.6% | CZ 6B | 33.5348 | 6.404 | 16.219 | 39.6446 | 0 | 14.9726 | 0 | 21.8876 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 183.3178 | 1.6%
CZ 7 | 0.3405 | 0.064983 | 0.15647 | 0.6876 | 0 | 0.15444 | 0 | 0.21492 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 2.1213 | 0.993% | CZ 7 | 10.9295 | 2.0858 | 15.966 | 28.7452 | 0 | 4.9573 | 0 | 6.8985 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 92.0446 | 0.993% | CZ 7 | 3.2032 | 0.61132 | 0 | 5.5707 | 0 | 1.4529 | 0 | 2.0218 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 16.7331 | 0.993% | CZ 7 | 0 | 0 | 0.15966 | 0.097379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.34951 | 0.993% | CZ 7 | 33.5348 | 6.3999 | 17.4509 | 68.9633 | 0 | 15.2103 | 0 | 21.1665 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 213.3808 | 0.993%
CZ 8 | 0.3405 | 0.064628 | 0.16874 | 0.86311 | 0 | 0.10246 | 0 | 0.21273 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 2.2545 | 0.06422% | CZ 8 | 10.9295 | 2.0744 | 17.2179 | 36.8473 | 0 | 3.2886 | 0 | 6.8283 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 99.6483 | 0.06422% | CZ 8 | 3.2032 | 0.60798 | 0 | 6.8898 | 0 | 0.96384 | 0 | 2.0012 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 17.5393 | 0.06422% | CZ 8 | 0 | 0 | 0.17218 | 0.13339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.39804 | 0.06422% | CZ 8 | 33.5348 | 6.3649 | 18.8191 | 86.7093 | 0 | 10.0904 | 0 | 20.9511 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 227.1248 | 0.06422%
US Weighted | 0.3405 | 0.065124 | 0.12573 | 0.19438 | 0 | 0.33409 | 0 | 0.218 | 0 | 0.00017776 | 0 | 0.17717 | 0 | 0.11009 | 0 | 0.21489 | 1.7802 | 100% | US Weighted | 10.9295 | 2.0903 | 12.8298 | 8.185 | 0 | 10.7235 | 0 | 6.9972 | 0 | 0.0057056 | 0 | 5.6869 | 0 | 9.8721 | 0 | 6.8976 | 74.2176 | 100% | US Weighted | 3.2032 | 0.61265 | 0 | 1.5669 | 0 | 3.1429 | 0 | 2.0508 | 0 | 0.0016722 | 0 | 1.6667 | 0 | 0.18317 | 0 | 2.0216 | 14.4495 | 100% | US Weighted | 0 | 0 | 0.1283 | 0.028389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092472 | 0 | 0 | 0.24916 | 100% | US Weighted | 33.5348 | 6.4138 | 14.023 | 19.5063 | 0 | 32.9027 | 0 | 21.4694 | 0 | 0.017506 | 0 | 17.4491 | 0 | 12.0248 | 0 | 21.1638 | 178.5051 | 100%
Building Type: | Small Hotel |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Small Hotel |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 43202 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 43202 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 43202 | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.21491 | 0.034895 | 0.0082067 | -6.8368e-06 | 0 | 0.40201 | 0 | 0.10266 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.79294 | 0% | CZ 0A | 6.898 | 1.12 | 0.83742 | -0.00021945 | 0 | 12.9036 | 0 | 3.2952 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 26.0258 | 0% | CZ 0A | 2.0217 | 0.32827 | 0 | -6.4316e-05 | 0 | 3.7818 | 0 | 0.96576 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 7.3823 | 0% | CZ 0A | 0 | 0 | 0.0083742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083742 | 0% | CZ 0A | 21.1652 | 3.4366 | 0.9153 | -0.00067332 | 0 | 39.5919 | 0 | 10.1106 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 78.2004 | 0%
CZ 0B | 0.21487 | 0.034902 | 0.0078606 | -5.4694e-05 | 0 | 0.3466 | 0 | 0.10714 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.7416 | 0% | CZ 0B | 6.8969 | 1.1203 | 0.8021 | -0.0017556 | 0 | 11.1252 | 0 | 3.4389 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 24.3534 | 0% | CZ 0B | 2.0214 | 0.32833 | 0 | -0.00051453 | 0 | 3.2606 | 0 | 1.0079 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 6.9025 | 0% | CZ 0B | 0 | 0 | 0.008021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008021 | 0% | CZ 0B | 21.1618 | 3.4373 | 0.87669 | -0.0053866 | 0 | 34.1354 | 0 | 10.5516 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 73.1389 | 0%
CZ 1A | 0.21375 | 0.034902 | 0.0082261 | -5.4694e-05 | 0 | 0.28991 | 0 | 0.10611 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.68311 | 2.061% | CZ 1A | 6.861 | 1.1203 | 0.83939 | -0.0017556 | 0 | 9.3054 | 0 | 3.4058 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 22.5017 | 2.061% | CZ 1A | 2.0108 | 0.32833 | 0 | -0.00051453 | 0 | 2.7272 | 0 | 0.99818 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 6.3489 | 2.061% | CZ 1A | 0 | 0 | 0.0083939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083939 | 2.061% | CZ 1A | 21.0514 | 3.4373 | 0.91746 | -0.0053866 | 0 | 28.5515 | 0 | 10.4499 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 67.3837 | 2.061%
CZ 1B | 0.21427 | 0.034861 | 0.0061083 | 0.0053279 | 0 | 0.27965 | 0 | 0.10704 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.67753 | 0% | CZ 1B | 6.8776 | 1.119 | 0.62329 | 0.20846 | 0 | 8.9762 | 0 | 3.4359 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 22.2121 | 0% | CZ 1B | 2.0157 | 0.32795 | 0 | 0.045085 | 0 | 2.6308 | 0 | 1.007 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 6.3113 | 0% | CZ 1B | 0 | 0 | 0.0062329 | 0.00054629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067792 | 0% | CZ 1B | 21.1026 | 3.4333 | 0.68126 | 0.53171 | 0 | 27.5415 | 0 | 10.5422 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 66.814 | 0%
CZ 2A | 0.21435 | 0.034847 | 0.0052956 | 0.014858 | 0 | 0.24583 | 0 | 0.10783 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.65329 | 19.12% | CZ 2A | 6.8803 | 1.1185 | 0.54036 | 0.61528 | 0 | 7.8906 | 0 | 3.4611 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 21.4778 | 19.12% | CZ 2A | 2.0165 | 0.32782 | 0 | 0.12117 | 0 | 2.3126 | 0 | 1.0144 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 6.0773 | 19.12% | CZ 2A | 0 | 0 | 0.0054036 | 0.0020184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007422 | 19.12% | CZ 2A | 21.1106 | 3.4319 | 0.59062 | 1.4891 | 0 | 24.2106 | 0 | 10.6196 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 64.434 | 19.12%
CZ 2B | 0.21358 | 0.034874 | 0.0049171 | 0.016 | 0 | 0.18923 | 0 | 0.11554 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.60441 | 1.527% | CZ 2B | 6.8555 | 1.1194 | 0.50175 | 0.61266 | 0 | 6.0738 | 0 | 3.7086 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 19.8434 | 1.527% | CZ 2B | 2.0092 | 0.32807 | 0 | 0.13719 | 0 | 1.7801 | 0 | 1.0869 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.6263 | 1.527% | CZ 2B | 0 | 0 | 0.0050175 | 0.0014458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064633 | 1.527% | CZ 2B | 21.0345 | 3.4346 | 0.54841 | 1.5942 | 0 | 18.6362 | 0 | 11.3791 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 59.6086 | 1.527%
CZ 3A | 0.21385 | 0.034867 | 0.0026704 | 0.065167 | 0 | 0.14985 | 0 | 0.10946 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.60614 | 16.87% | CZ 3A | 6.8642 | 1.1192 | 0.27248 | 2.7602 | 0 | 4.8098 | 0 | 3.5133 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 20.3109 | 16.87% | CZ 3A | 2.0118 | 0.32801 | 0 | 0.52314 | 0 | 1.4097 | 0 | 1.0297 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.5871 | 16.87% | CZ 3A | 0 | 0 | 0.0027248 | 0.009752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012477 | 16.87% | CZ 3A | 21.0615 | 3.4339 | 0.29783 | 6.5427 | 0 | 14.7579 | 0 | 10.7799 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 59.8551 | 16.87%
CZ 3B | 0.21383 | 0.034867 | 0.0033089 | 0.032521 | 0 | 0.13818 | 0 | 0.11504 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.56802 | 6.686% | CZ 3B | 6.8634 | 1.1192 | 0.33764 | 1.3784 | 0 | 4.4354 | 0 | 3.6924 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 18.7981 | 6.686% | CZ 3B | 2.0115 | 0.32801 | 0 | 0.26093 | 0 | 1.2999 | 0 | 1.0822 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.2674 | 6.686% | CZ 3B | 0 | 0 | 0.0033764 | 0.0048815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082579 | 6.686% | CZ 3B | 21.0588 | 3.4339 | 0.36905 | 3.2652 | 0 | 13.6092 | 0 | 11.3293 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 56.0469 | 6.686%
CZ 3C | 0.21405 | 0.034861 | 0.00058481 | 0.010551 | 0 | 0.13314 | 0 | 0.086929 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.51039 | 0.9608% | CZ 3C | 6.8706 | 1.119 | 0.059675 | 0.47702 | 0 | 4.2735 | 0 | 2.7902 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 16.5617 | 0.9608% | CZ 3C | 2.0137 | 0.32795 | 0 | 0.080652 | 0 | 1.2525 | 0 | 0.81777 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 4.7773 | 0.9608% | CZ 3C | 0 | 0 | 0.00059675 | 0.0020184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026152 | 0.9608% | CZ 3C | 21.081 | 3.4333 | 0.065224 | 1.065 | 0 | 13.1123 | 0 | 8.5613 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 50.2994 | 0.9608%
CZ 4A | 0.21497 | 0.034813 | 0.00074176 | 0.15585 | 0 | 0.090628 | 0 | 0.10836 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.63564 | 19.16% | CZ 4A | 6.9 | 1.1174 | 0.07569 | 6.5843 | 0 | 2.909 | 0 | 3.4782 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 22.0363 | 19.16% | CZ 4A | 2.0223 | 0.3275 | 0 | 1.2534 | 0 | 0.85257 | 0 | 1.0194 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.7599 | 19.16% | CZ 4A | 0 | 0 | 0.0007569 | 0.023078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023835 | 19.16% | CZ 4A | 21.1712 | 3.4286 | 0.082729 | 15.6441 | 0 | 8.9255 | 0 | 10.6721 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 62.9057 | 19.16%
CZ 4B | 0.21499 | 0.03484 | 0.0010492 | 0.078274 | 0 | 0.084837 | 0 | 0.10428 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.54854 | 0.8608% | CZ 4B | 6.9007 | 1.1183 | 0.10706 | 3.4004 | 0 | 2.7231 | 0 | 3.3472 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 18.5685 | 0.8608% | CZ 4B | 2.0225 | 0.32775 | 0 | 0.61692 | 0 | 0.79809 | 0 | 0.98101 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.031 | 0.8608% | CZ 4B | 0 | 0 | 0.0010706 | 0.012955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014026 | 0.8608% | CZ 4B | 21.1733 | 3.4312 | 0.11702 | 7.8745 | 0 | 8.3552 | 0 | 10.2702 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 54.2029 | 0.8608%
CZ 4C | 0.21417 | 0.034772 | 0.00041496 | 0.10294 | 0 | 0.04314 | 0 | 0.083026 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.50873 | 1.635% | CZ 4C | 6.8743 | 1.1161 | 0.042343 | 4.6259 | 0 | 1.3847 | 0 | 2.6649 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 17.68 | 1.635% | CZ 4C | 2.0148 | 0.32711 | 0 | 0.79063 | 0 | 0.40583 | 0 | 0.78105 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 4.6042 | 1.635% | CZ 4C | 0 | 0 | 0.00042343 | 0.019282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019706 | 1.635% | CZ 4C | 21.0925 | 3.4245 | 0.046281 | 10.3847 | 0 | 4.2487 | 0 | 8.1768 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 50.3549 | 1.635%
CZ 5A | 0.21507 | 0.03482 | 0.00038486 | 0.23854 | 0 | 0.058988 | 0 | 0.10793 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.686 | 17.17% | CZ 5A | 6.9033 | 1.1176 | 0.039271 | 9.8894 | 0 | 1.8934 | 0 | 3.4642 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 24.2788 | 17.17% | CZ 5A | 2.0232 | 0.32756 | 0 | 1.9437 | 0 | 0.55492 | 0 | 1.0153 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 6.1495 | 17.17% | CZ 5A | 0 | 0 | 0.00039271 | 0.032573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032966 | 17.17% | CZ 5A | 21.1813 | 3.4292 | 0.042923 | 23.9094 | 0 | 5.8094 | 0 | 10.629 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 67.9828 | 17.17%
CZ 5B | 0.21516 | 0.034826 | 0.00035691 | 0.15255 | 0 | 0.064525 | 0 | 0.10296 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.60065 | 5.989% | CZ 5B | 6.9062 | 1.1179 | 0.036419 | 6.4518 | 0 | 2.0711 | 0 | 3.3048 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 20.8599 | 5.989% | CZ 5B | 2.0241 | 0.32762 | 0 | 1.2259 | 0 | 0.60701 | 0 | 0.96859 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.438 | 5.989% | CZ 5B | 0 | 0 | 0.00036419 | 0.022692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023056 | 5.989% | CZ 5B | 21.1901 | 3.4299 | 0.039806 | 15.3137 | 0 | 6.3548 | 0 | 10.1402 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 59.45 | 5.989%
CZ 5C | 0.21452 | 0.034772 | 0.00034831 | 0.1185 | 0 | 0.028502 | 0 | 0.082041 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.50896 | 0.1299% | CZ 5C | 6.8858 | 1.1161 | 0.035541 | 5.3335 | 0 | 0.91487 | 0 | 2.6333 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 17.8908 | 0.1299% | CZ 5C | 2.0181 | 0.32711 | 0 | 0.90897 | 0 | 0.26813 | 0 | 0.77179 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 4.5789 | 0.1299% | CZ 5C | 0 | 0 | 0.00035541 | 0.022321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022676 | 0.1299% | CZ 5C | 21.1275 | 3.4245 | 0.038847 | 11.9557 | 0 | 2.8071 | 0 | 8.0799 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 50.4149 | 0.1299%
CZ 6A | 0.21502 | 0.034813 | 0.00044506 | 0.35553 | 0 | 0.059849 | 0 | 0.10894 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.80487 | 5.175% | CZ 6A | 6.9016 | 1.1174 | 0.045414 | 14.6459 | 0 | 1.921 | 0 | 3.4969 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 29.0999 | 5.175% | CZ 6A | 2.0227 | 0.3275 | 0 | 2.9096 | 0 | 0.56302 | 0 | 1.0249 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 7.1325 | 5.175% | CZ 6A | 0 | 0 | 0.00045414 | 0.047182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047637 | 5.175% | CZ 6A | 21.1759 | 3.4286 | 0.049638 | 35.6181 | 0 | 5.8943 | 0 | 10.7294 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 79.8773 | 5.175%
CZ 6B | 0.21494 | 0.034785 | 0.00041281 | 0.2605 | 0 | 0.041034 | 0 | 0.10133 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.68328 | 1.6% | CZ 6B | 6.8991 | 1.1165 | 0.042123 | 10.9494 | 0 | 1.3171 | 0 | 3.2526 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 24.5486 | 1.6% | CZ 6B | 2.022 | 0.32724 | 0 | 2.1025 | 0 | 0.38602 | 0 | 0.95329 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 6.0759 | 1.6% | CZ 6B | 0 | 0 | 0.00042123 | 0.037755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038176 | 1.6% | CZ 6B | 21.1685 | 3.4259 | 0.046041 | 26.1382 | 0 | 4.0413 | 0 | 9.98 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 67.7813 | 1.6%
CZ 7 | 0.21493 | 0.034758 | 0.00042786 | 0.43505 | 0 | 0.048049 | 0 | 0.098709 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.86221 | 0.993% | CZ 7 | 6.8989 | 1.1157 | 0.043659 | 18.0277 | 0 | 1.5423 | 0 | 3.1683 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 31.7683 | 0.993% | CZ 7 | 2.022 | 0.32698 | 0 | 3.5462 | 0 | 0.45201 | 0 | 0.92859 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 7.5605 | 0.993% | CZ 7 | 0 | 0 | 0.00043659 | 0.059282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059718 | 0.993% | CZ 7 | 21.1679 | 3.4232 | 0.047719 | 43.6044 | 0 | 4.7321 | 0 | 9.7214 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 85.6781 | 0.993%
CZ 8 | 0.21263 | 0.034573 | 0.00053321 | 0.52759 | 0 | 0.023054 | 0 | 0.082451 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.9111 | 0.06422% | CZ 8 | 6.825 | 1.1097 | 0.054409 | 22.5129 | 0 | 0.73997 | 0 | 2.6465 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 34.8602 | 0.06422% | CZ 8 | 2.0003 | 0.32524 | 0 | 4.2129 | 0 | 0.21687 | 0 | 0.77565 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 7.8157 | 0.06422% | CZ 8 | 0 | 0 | 0.00054409 | 0.081386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08193 | 0.06422% | CZ 8 | 20.941 | 3.405 | 0.059469 | 53 | 0 | 2.2704 | 0 | 8.1203 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 90.7776 | 0.06422%
US Weighted | 0.21455 | 0.034836 | 0.0022145 | 0.12604 | 0 | 0.12874 | 0 | 0.10767 | 0 | 0 | 0 | 0.0063172 | 0 | 0 | 0 | 0.023956 | 0.64432 | 100% | US Weighted | 6.8865 | 1.1182 | 0.22597 | 5.2736 | 0 | 4.1322 | 0 | 3.456 | 0 | 0 | 0 | 0.20277 | 0 | 0 | 0 | 0.76894 | 22.0642 | 100% | US Weighted | 2.0183 | 0.32771 | 0 | 1.0206 | 0 | 1.2111 | 0 | 1.0129 | 0 | 0 | 0 | 0.059428 | 0 | 0 | 0 | 0.22536 | 5.8754 | 100% | US Weighted | 0 | 0 | 0.0022597 | 0.017914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020174 | 100% | US Weighted | 21.1297 | 3.4308 | 0.24699 | 12.6422 | 0 | 12.6789 | 0 | 10.6041 | 0 | 0 | 0 | 0.62215 | 0 | 0 | 0 | 2.3593 | 63.7142 | 100%
Building Type: | Small Hotel |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Small Hotel |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Small Hotel |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Small Hotel |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 43202 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 43202 | [17 empty] | Prototype Floor Area: | 43202 | Building Type: | Small Hotel | [15 empty] | Prototype Floor Area: | 43202 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 63.11% | 53.5% | 8.265% |  |  | 43.37% |  | 46.41% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 36.79% | 0% | CZ 0A | 63.11% | 53.5% | 8.265% |  |  | 43.37% |  | 46.41% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 31.56% | 0% | CZ 0A | 63.11% | 53.5% |  |  |  | 43.37% |  | 46.41% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39.92% | 0% | CZ 0A |  |  | 8.265% | [10 empty] | 0% |  |  | 4.321% | 0% | CZ 0A | 63.11% | 53.5% | 8.265% |  |  | 43.37% |  | 46.41% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 36.41% | 0%
CZ 0B | 63.1% | 53.49% | 7.934% | -200% |  | 41.45% |  | 47.06% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.81% | 0% | CZ 0B | 63.1% | 53.49% | 7.934% | -200% |  | 41.45% |  | 47.06% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 30.54% | 0% | CZ 0B | 63.1% | 53.49% |  | -200% |  | 41.45% |  | 47.06% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39% | 0% | CZ 0B |  |  | 7.934% | [10 empty] | 0% |  |  | 4.144% | 0% | CZ 0B | 63.1% | 53.49% | 7.934% | -200% |  | 41.45% |  | 47.06% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.43% | 0%
CZ 1A | 62.77% | 53.49% | 7.952% |  |  | 43.19% |  | 48.51% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.92% | 2.061% | CZ 1A | 62.77% | 53.49% | 7.952% |  |  | 43.19% |  | 48.51% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 30.16% | 2.061% | CZ 1A | 62.77% | 53.49% |  |  |  | 43.19% |  | 48.51% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39.53% | 2.061% | CZ 1A |  |  | 7.952% | [10 empty] | 0% |  |  | 4.239% | 2.061% | CZ 1A | 62.77% | 53.49% | 7.952% |  |  | 43.19% |  | 48.51% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.5% | 2.061%
CZ 1B | 62.93% | 53.49% | 5.9% | 69.44% |  | 40.35% |  | 47.78% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.99% | 0% | CZ 1B | 62.93% | 53.49% | 5.9% | 69.5% |  | 40.35% |  | 47.78% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 29.31% | 0% | CZ 1B | 62.93% | 53.49% |  | 69.41% |  | 40.35% |  | 47.78% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 38.53% | 0% | CZ 1B |  |  | 5.9% | 69.75% | [9 empty] | 0% |  |  | 3.408% | 0% | CZ 1B | 62.93% | 53.49% | 5.9% | 69.44% |  | 40.35% |  | 47.78% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.58% | 0%
CZ 2A | 62.95% | 53.49% | 4.893% | 76.85% |  | 42.42% |  | 49.24% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.62% | 19.12% | CZ 2A | 62.95% | 53.49% | 4.893% | 76.24% |  | 42.42% |  | 49.24% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 29.44% | 19.12% | CZ 2A | 62.95% | 53.49% |  | 77.28% |  | 42.42% |  | 49.24% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39.57% | 19.12% | CZ 2A |  |  | 4.893% | 74.19% | [9 empty] | 0% |  |  | 3.609% | 19.12% | CZ 2A | 62.95% | 53.49% | 4.893% | 76.8% |  | 42.42% |  | 49.24% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.16% | 19.12%
CZ 2B | 62.72% | 53.49% | 4.512% | 78.39% |  | 40.84% |  | 50.24% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.92% | 1.527% | CZ 2B | 62.72% | 53.49% | 4.512% | 77.53% |  | 40.84% |  | 50.24% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 28.49% | 1.527% | CZ 2B | 62.72% | 53.49% |  | 78.91% |  | 40.84% |  | 50.24% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39.11% | 1.527% | CZ 2B |  |  | 4.512% | 73.39% | [9 empty] | 0% |  |  | 3.143% | 1.527% | CZ 2B | 62.72% | 53.49% | 4.512% | 78.33% |  | 40.84% |  | 50.24% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.44% | 1.527%
CZ 3A | 62.8% | 53.49% | 2.231% | 65.22% |  | 40.28% |  | 50.27% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.3% | 16.87% | CZ 3A | 62.8% | 53.49% | 2.231% | 64.86% |  | 40.28% |  | 50.27% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 28.66% | 16.87% | CZ 3A | 62.8% | 53.49% |  | 65.48% |  | 40.28% |  | 50.27% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39.8% | 16.87% | CZ 3A |  |  | 2.231% | 63.76% | [9 empty] | 0% |  |  | 5.428% | 16.87% | CZ 3A | 62.8% | 53.49% | 2.231% | 65.19% |  | 40.28% |  | 50.27% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.79% | 16.87%
CZ 3B | 62.8% | 53.49% | 2.839% | 70.48% |  | 38.28% |  | 50.52% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.23% | 6.686% | CZ 3B | 62.8% | 53.49% | 2.839% | 69.82% |  | 38.28% |  | 50.52% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 27.54% | 6.686% | CZ 3B | 62.8% | 53.49% |  | 70.95% |  | 38.28% |  | 50.52% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 38.74% | 6.686% | CZ 3B |  |  | 2.839% | 67.86% | [9 empty] | 0% |  |  | 3.778% | 6.686% | CZ 3B | 62.8% | 53.49% | 2.839% | 70.43% |  | 38.28% |  | 50.52% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 33.72% | 6.686%
CZ 3C | 62.86% | 53.49% | 0.4906% | 77.45% |  | 42.61% |  | 39.71% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 32.46% | 0.9608% | CZ 3C | 62.86% | 53.49% | 0.4906% | 79.87% |  | 42.61% |  | 39.71% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 25.36% | 0.9608% | CZ 3C | 62.86% | 53.49% |  | 75.63% |  | 42.61% |  | 39.71% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 37.34% | 0.9608% | CZ 3C |  |  | 0.4906% | 86.47% | [9 empty] | 0% |  |  | 1.208% | 0.9608% | CZ 3C | 62.86% | 53.49% | 0.4906% | 77.65% |  | 42.61% |  | 39.71% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 31.91% | 0.9608%
CZ 4A | 63.13% | 53.49% | 0.5715% | 65.67% |  | 35% |  | 50.54% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 36.36% | 19.16% | CZ 4A | 63.13% | 53.49% | 0.5715% | 65.07% |  | 35% |  | 50.54% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 29.76% | 19.16% | CZ 4A | 63.13% | 53.49% |  | 66.11% |  | 35% |  | 50.54% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 41.03% | 19.16% | CZ 4A |  |  | 0.5715% | 63.23% | [9 empty] | 0% |  |  | 9.118% | 19.16% | CZ 4A | 63.13% | 53.49% | 0.5715% | 65.63% |  | 35% |  | 50.54% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.84% | 19.16%
CZ 4B | 63.14% | 53.49% | 0.8287% | 72.52% |  | 32.57% |  | 45.13% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 33.57% | 0.8608% | CZ 4B | 63.14% | 53.49% | 0.8287% | 73.6% |  | 32.57% |  | 45.13% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 26.99% | 0.8608% | CZ 4B | 63.14% | 53.49% |  | 71.73% |  | 32.57% |  | 45.13% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 38.19% | 0.8608% | CZ 4B |  |  | 0.8287% | 76.86% | [9 empty] | 0% |  |  | 5.88% | 0.8608% | CZ 4B | 63.14% | 53.49% | 0.8287% | 72.6% |  | 32.57% |  | 45.13% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 33.05% | 0.8608%
CZ 4C | 62.9% | 53.49% | 0.3117% | 72.79% |  | 26.53% |  | 38.88% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 32.64% | 1.635% | CZ 4C | 62.9% | 53.49% | 0.3117% | 73.6% |  | 26.53% |  | 38.88% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 26.22% | 1.635% | CZ 4C | 62.9% | 53.49% |  | 72.16% |  | 26.53% |  | 38.88% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 37.37% | 1.635% | CZ 4C |  |  | 0.3117% | 75.7% | [9 empty] | 0% |  |  | 7.765% | 1.635% | CZ 4C | 62.9% | 53.49% | 0.3117% | 72.85% |  | 26.53% |  | 38.88% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 32.13% | 1.635%
CZ 5A | 63.16% | 53.49% | 0.2754% | 63.58% |  | 31.84% |  | 50.65% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 37.67% | 17.17% | CZ 5A | 63.16% | 53.49% | 0.2754% | 62.92% |  | 31.84% |  | 50.65% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 31.03% | 17.17% | CZ 5A | 63.16% | 53.49% |  | 64.03% |  | 31.84% |  | 50.65% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 42.49% | 17.17% | CZ 5A |  |  | 0.2754% | 60.78% | [9 empty] | 0% |  |  | 11.42% | 17.17% | CZ 5A | 63.16% | 53.49% | 0.2754% | 63.53% |  | 31.84% |  | 50.65% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 37.14% | 17.17%
CZ 5B | 63.19% | 53.49% | 0.261% | 68.27% |  | 31.07% |  | 45.17% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 35.25% | 5.989% | CZ 5B | 63.19% | 53.49% | 0.261% | 68.72% |  | 31.07% |  | 45.17% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 28.65% | 5.989% | CZ 5B | 63.19% | 53.49% |  | 67.95% |  | 31.07% |  | 45.17% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 40.01% | 5.989% | CZ 5B |  |  | 0.261% | 70.17% | [9 empty] | 0% |  |  | 8.722% | 5.989% | CZ 5B | 63.19% | 53.49% | 0.261% | 68.3% |  | 31.07% |  | 45.17% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.73% | 5.989%
CZ 5C | 63% | 53.49% | 0.2509% | 74.58% |  | 20.9% |  | 38.89% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 32.78% | 0.1299% | CZ 5C | 63% | 53.49% | 0.2509% | 74.25% |  | 20.9% |  | 38.89% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 26.32% | 0.1299% | CZ 5C | 63% | 53.49% |  | 74.85% |  | 20.9% |  | 38.89% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 37.63% | 0.1299% | CZ 5C |  |  | 0.2509% | 73.45% | [9 empty] | 0% |  |  | 8.572% | 0.1299% | CZ 5C | 63% | 53.49% | 0.2509% | 74.56% |  | 20.9% |  | 38.89% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 32.25% | 0.1299%
CZ 6A | 63.15% | 53.5% | 0.3019% | 61.59% |  | 32.53% |  | 50.53% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39.61% | 5.175% | CZ 6A | 63.15% | 53.5% | 0.3019% | 61.21% |  | 32.53% |  | 50.53% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 33.34% | 5.175% | CZ 6A | 63.15% | 53.5% |  | 61.84% |  | 32.53% |  | 50.53% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 44.16% | 5.175% | CZ 6A |  |  | 0.3019% | 59.92% | [9 empty] | 0% |  |  | 14.81% | 5.175% | CZ 6A | 63.15% | 53.5% | 0.3019% | 61.56% |  | 32.53% |  | 50.53% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39.11% | 5.175%
CZ 6B | 63.12% | 53.5% | 0.2839% | 65.9% |  | 26.99% |  | 45.6% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 37.48% | 1.6% | CZ 6B | 63.12% | 53.5% | 0.2839% | 66.26% |  | 26.99% |  | 45.6% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 31.13% | 1.6% | CZ 6B | 63.12% | 53.5% |  | 65.65% |  | 26.99% |  | 45.6% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 42.16% | 1.6% | CZ 6B |  |  | 0.2839% | 67.45% | [9 empty] | 0% |  |  | 12.86% | 1.6% | CZ 6B | 63.12% | 53.5% | 0.2839% | 65.93% |  | 26.99% |  | 45.6% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 36.97% | 1.6%
CZ 7 | 63.12% | 53.49% | 0.2734% | 63.27% |  | 31.11% |  | 45.93% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 40.65% | 0.993% | CZ 7 | 63.12% | 53.49% | 0.2734% | 62.72% |  | 31.11% |  | 45.93% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.51% | 0.993% | CZ 7 | 63.12% | 53.49% |  | 63.66% |  | 31.11% |  | 45.93% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 45.18% | 0.993% | CZ 7 |  |  | 0.2734% | 60.88% | [9 empty] | 0% |  |  | 17.09% | 0.993% | CZ 7 | 63.12% | 53.49% | 0.2734% | 63.23% |  | 31.11% |  | 45.93% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 40.15% | 0.993%
CZ 8 | 62.45% | 53.5% | 0.316% | 61.13% |  | 22.5% |  | 38.76% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 40.41% | 0.06422% | CZ 8 | 62.45% | 53.5% | 0.316% | 61.1% |  | 22.5% |  | 38.76% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 34.98% | 0.06422% | CZ 8 | 62.45% | 53.5% |  | 61.15% |  | 22.5% |  | 38.76% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 44.56% | 0.06422% | CZ 8 |  |  | 0.316% | 61.01% | [9 empty] | 0% |  |  | 20.58% | 0.06422% | CZ 8 | 62.45% | 53.5% | 0.316% | 61.12% |  | 22.5% |  | 38.76% |  | 0% |  | 3.566% |  | 0% |  | 11.15% | 39.97% | 0.06422%
US Weighted | 63.01% | 53.49% | 1.947% | 66.76% | 0% | 36.6% | 0% | 49.41% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.15% | 36.13% | 100% | US Weighted | 63.01% | 53.49% | 1.947% | 66.35% | 0% | 36.6% | 0% | 49.41% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.15% | 29.63% | 100% | US Weighted | 63.01% | 53.49% | 0% | 67.04% | 0% | 36.6% | 0% | 49.41% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.15% | 40.62% | 100% | US Weighted | 0% | 0% | 1.947% | 65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.579% | 100% | US Weighted | 63.01% | 53.49% | 1.947% | 66.73% | 0% | 36.6% | 0% | 49.41% | 0% | 0% | 0% | 3.566% | 0% | 0% | 0% | 11.15% | 35.62% | 100%

## HotLrg
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Large Hotel |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 122120 |  | Building Type: | Large Hotel |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 |  | Building Type: | Large Hotel |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Large Hotel |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Large Hotel | [14 empty] | Prototype Floor Area: | 122120 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.12731 | 0.044207 | 0.17838 | 0.023014 | 0 | 0.31212 | 0 | 0.16888 | 0.024576 | 0.012979 | 0.015034 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.673 |  | STD2019 | 4.0865 | 1.4189 | 16.6703 | 2.3484 | 0 | 10.0184 | 0 | 5.4208 | 0.78884 | 0.4166 | 0.48256 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 75.7719 |  | STD2019 | 1.1977 | 0.41587 | 0.20607 | 0 | 0 | 2.9362 | 0 | 1.5888 | 0.2312 | 0.1221 | 0.14143 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 12.7704 |  | STD2019 | 0 | 0 | 0.15967 | 0.023484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32199 |  | STD2019 | 12.5384 | 4.3537 | 19.6094 | 2.5668 | 0 | 30.7394 | 0 | 16.6327 | 2.4204 | 1.2783 | 1.4806 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 168.8868
STD2016 | 0.20008 | 0.044207 | 0.17866 | 0.05726 | 0 | 0.38126 | 0 | 0.12269 | 0.048333 | 0.014006 | 0.020573 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.8337 |  | STD2016 | 6.4223 | 1.4189 | 16.6949 | 5.8429 | 0 | 12.2375 | 0 | 3.9379 | 1.5514 | 0.44956 | 0.66034 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 83.3386 |  | STD2016 | 1.8823 | 0.41587 | 0.20649 | 0 | 0 | 3.5866 | 0 | 1.1541 | 0.45468 | 0.13176 | 0.19353 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 13.9571 |  | STD2016 | 0 | 0 | 0.1599 | 0.058429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35717 |  | STD2016 | 19.7054 | 4.3537 | 19.6392 | 6.3863 | 0 | 37.5483 | 0 | 12.0827 | 4.7601 | 1.3794 | 2.0261 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 185.1553
STD2013 | 0.22056 | 0.059534 | 0.17874 | 0.057686 | 0 | 0.39392 | 0 | 0.13464 | 0.054454 | 0.017764 | 0.020569 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.9067 |  | STD2013 | 7.0794 | 1.9109 | 16.7035 | 5.8863 | 0 | 12.644 | 0 | 4.3216 | 1.7479 | 0.57018 | 0.66022 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 85.7192 |  | STD2013 | 2.0749 | 0.56005 | 0.20649 | 0 | 0 | 3.7057 | 0 | 1.2666 | 0.51227 | 0.16711 | 0.1935 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 14.6395 |  | STD2013 | 0 | 0 | 0.15999 | 0.058863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35769 |  | STD2013 | 21.7218 | 5.8632 | 19.6486 | 6.4337 | 0 | 38.7953 | 0 | 13.2598 | 5.3629 | 1.7495 | 2.0257 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 192.3568
STD2010 | 0.3065 | 0.059534 | 0.17873 | 0.092812 | 0 | 0.45697 | 0 | 0.16215 | 0.044232 | 0.019733 | 0.025465 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.1355 |  | STD2010 | 9.838 | 1.9109 | 16.703 | 9.4706 | 0 | 14.6676 | 0 | 5.2048 | 1.4198 | 0.63338 | 0.81736 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 95.5177 |  | STD2010 | 2.8834 | 0.56005 | 0.20649 | 0 | 0 | 4.2988 | 0 | 1.5254 | 0.41611 | 0.18563 | 0.23956 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 16.461 |  | STD2010 | 0 | 0 | 0.15998 | 0.094706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39353 |  | STD2010 | 30.1859 | 5.8632 | 19.648 | 10.3513 | 0 | 45.0045 | 0 | 15.9697 | 4.3562 | 1.9434 | 2.5079 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 215.3424
STD2007 | 0.35129 | 0.074022 | 0.17928 | 0.2204 | 0 | 0.54241 | 0 | 0.15978 | 0 | 0.048013 | 0.025377 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.4035 |  | STD2007 | 11.2757 | 2.3759 | 16.7211 | 22.4896 | 0 | 17.4102 | 0 | 5.1285 | 0 | 1.5411 | 0.81453 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 113.0441 |  | STD2007 | 3.3047 | 0.69635 | 0.21152 | 0 | 0 | 5.1026 | 0 | 1.5031 | 0 | 0.45168 | 0.23873 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 17.7817 |  | STD2007 | 0 | 0 | 0.15999 | 0.2249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.52373 |  | STD2007 | 34.5972 | 7.2901 | 19.7017 | 24.5812 | 0 | 53.4195 | 0 | 15.7356 | 0 | 4.7286 | 2.4992 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 243.4003
STD2004 | 0.35129 | 0.074022 | 0.17936 | 0.22982 | 0 | 0.61287 | 0 | 0.30235 | 0.099276 | 0.059459 | 0.025033 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.7364 |  | STD2004 | 11.2757 | 2.3759 | 16.7279 | 23.4507 | 0 | 19.672 | 0 | 9.7049 | 3.1865 | 1.9085 | 0.8035 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 124.393 |  | STD2004 | 3.3047 | 0.69635 | 0.21168 | 0 | 0 | 5.7655 | 0 | 2.8444 | 0.93392 | 0.55935 | 0.23549 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 20.8244 |  | STD2004 | 0 | 0 | 0.16006 | 0.23451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.5334 |  | STD2004 | 34.5972 | 7.2901 | 19.7102 | 25.6316 | 0 | 60.3592 | 0 | 29.7775 | 9.7772 | 5.8559 | 2.4654 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 276.3114
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 7.7889e-05 | 0.0094182 | 0 | 0.070464 | 0 | 0.14258 | 0.099276 | 0.011446 | -0.00034367 | 0 | 0 | 0 | 0 | 0 | 0.33292 |  | 2004-2007 | 0 | 0 | 0.0067525 | 0.96105 | 0 | 2.2617 | 0 | 4.5765 | 3.1865 | 0.36739 | -0.011031 | 0 | 0 | 0 | 0 | 0 | 11.3489 |  | 2004-2007 | 0 | 0 | 0.00016078 | 0 | 0 | 0.66288 | 0 | 1.3413 | 0.93392 | 0.10768 | -0.003233 | 0 | 0 | 0 | 0 | 0 | 3.0427 |  | 2004-2007 | 0 | 0 | 6.2039e-05 | 0.0096105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096725 |  | 2004-2007 | 0 | 0 | 0.008464 | 1.0504 | 0 | 6.9397 | 0 | 14.0419 | 9.7772 | 1.1273 | -0.033846 | 0 | 0 | 0 | 0 | 0 | 32.9111
2007-2010 | 0.044791 | 0.014488 | 0.00054425 | 0.12759 | 0 | 0.085445 | 0 | -0.0023765 | -0.044232 | 0.028281 | -8.8218e-05 | 0.0062158 | 0.0058966 | 0 | 0 | 0.0014415 | 0.26799 |  | 2007-2010 | 1.4377 | 0.46503 | 0.01816 | 13.0191 | 0 | 2.7426 | 0 | -0.076281 | -1.4198 | 0.90774 | -0.0028316 | 0.19952 | 0.18927 | 0 | 0 | 0.046269 | 17.5265 |  | 2007-2010 | 0.42137 | 0.13629 | 0.005027 | 0 | 0 | 0.80381 | 0 | -0.022357 | -0.41611 | 0.26604 | -0.0008299 | 0.058475 | 0.055471 | 0 | 0 | 0.013561 | 1.3208 |  | 2007-2010 | 0 | 0 | 1.0084e-05 | 0.13019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1302 |  | 2007-2010 | 4.4113 | 1.4269 | 0.05373 | 14.2298 | 0 | 8.4151 | 0 | -0.23405 | -4.3562 | 2.7852 | -0.0086882 | 0.61217 | 0.58073 | 0 | 0 | 0.14197 | 28.0579
2010-2013 | 0.085943 | 0 | -5.41e-06 | 0.035126 | 0 | 0.063047 | 0 | 0.027515 | -0.010222 | 0.0019691 | 0.0048958 | 0.00048856 | 0.00042084 | 0 | 0 | 0.019562 | 0.22874 |  | 2010-2013 | 2.7586 | 0 | -0.00054934 | 3.5843 | 0 | 2.0237 | 0 | 0.88317 | -0.32811 | 0.063203 | 0.15715 | 0.015682 | 0.013508 | 0 | 0 | 0.62789 | 9.7985 |  | 2010-2013 | 0.80849 | 0 | -3.6349e-07 | 0 | 0 | 0.5931 | 0 | 0.25884 | -0.096164 | 0.018524 | 0.046057 | 0.0045961 | 0.003959 | 0 | 0 | 0.18402 | 1.8214 |  | 2010-2013 | 0 | 0 | -5.481e-06 | 0.035843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035837 |  | 2010-2013 | 8.4641 | 0 | -0.00060288 | 3.9176 | 0 | 6.2092 | 0 | 2.7098 | -1.0067 | 0.19393 | 0.48217 | 0.048116 | 0.041447 | 0 | 0 | 1.9266 | 22.9856
2013-2016 | 0.020474 | 0.015327 | 8.4609e-05 | 0.00042535 | 0 | 0.012662 | 0 | 0.011952 | 0.0061217 | 0.0037579 | -3.7169e-06 | 0 | 0.0022542 | 0 | 0 | 0 | 0.073055 |  | 2013-2016 | 0.65717 | 0.49196 | 0.0086232 | 0.043403 | 0 | 0.40643 | 0 | 0.38364 | 0.19649 | 0.12062 | -0.0001193 | 0 | 0.072353 | 0 | 0 | 0 | 2.3806 |  | 2013-2016 | 0.19261 | 0.14419 | 1.3895e-06 | 0 | 0 | 0.11912 | 0 | 0.11244 | 0.057589 | 0.035351 | -3.4966e-05 | 0 | 0.021206 | 0 | 0 | 0 | 0.68246 |  | 2013-2016 | 0 | 0 | 8.6185e-05 | 0.00043403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00052022 |  | 2013-2016 | 2.0164 | 1.5095 | 0.0094345 | 0.04744 | 0 | 1.247 | 0 | 1.1771 | 0.60289 | 0.37009 | -0.00036606 | 0 | 0.222 | 0 | 0 | 0 | 7.2015
2016-2019 | 0.072772 | 0 | 0.00027196 | 0.034246 | 0 | 0.069136 | 0 | -0.046199 | 0.023756 | 0.0010267 | 0.0055387 | 0 | 7.2559e-05 | 0 | 0 | 0 | 0.16062 |  | 2016-2019 | 2.3358 | 0 | 0.024621 | 3.4945 | 0 | 2.2191 | 0 | -1.4829 | 0.76253 | 0.032953 | 0.17778 | 0 | 0.002329 | 0 | 0 | 0 | 7.5668 |  | 2016-2019 | 0.68459 | 0 | 0.00042107 | 0 | 0 | 0.65038 | 0 | -0.43461 | 0.22348 | 0.0096581 | 0.052104 | 0 | 0.00068258 | 0 | 0 | 0 | 1.1867 |  | 2016-2019 | 0 | 0 | 0.00023184 | 0.034945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035177 |  | 2016-2019 | 7.1669 | 0 | 0.029748 | 3.8195 | 0 | 6.8089 | 0 | -4.5499 | 2.3397 | 0.10111 | 0.54548 | 0 | 0.007146 | 0 | 0 | 0 | 16.2685
2004-2019 | 0.22398 | 0.029815 | 0.0009733 | 0.2068 | 0 | 0.30075 | 0 | 0.13347 | 0.0747 | 0.04648 | 0.0099989 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0633 |  | 2004-2019 | 7.1893 | 0.957 | 0.057607 | 21.1023 | 0 | 9.6535 | 0 | 4.2841 | 2.3977 | 1.4919 | 0.32094 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 48.6211 |  | 2004-2019 | 2.1071 | 0.28048 | 0.0056098 | 0 | 0 | 2.8293 | 0 | 1.2556 | 0.70272 | 0.43725 | 0.094063 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 8.054 |  | 2004-2019 | 0 | 0 | 0.00038467 | 0.21102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21141 |  | 2004-2019 | 22.0587 | 2.9363 | 0.10077 | 23.0648 | 0 | 29.6198 | 0 | 13.1448 | 7.3568 | 4.5776 | 0.98475 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 107.4246
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.04343% | 4.098% |  | 11.5% |  | 47.16% | 100% | 19.25% | -1.373% | 0% | 0% | 0% |  | 0% | 12.17% |  | 2004-2007 | 0% | 0% | 0.04037% | 4.098% |  | 11.5% |  | 47.16% | 100% | 19.25% | -1.373% | 0% | 0% | 0% |  | 0% | 9.123% |  | 2004-2007 | 0% | 0% | 0.07595% |  |  | 11.5% |  | 47.16% | 100% | 19.25% | -1.373% | 0% | 0% | 0% |  | 0% | 14.61% |  | 2004-2007 |  |  | 0.03876% | 4.098% | [9 empty] | 0% |  |  | 1.813% |  | 2004-2007 | 0% | 0% | 0.04294% | 4.098% |  | 11.5% |  | 47.16% | 100% | 19.25% | -1.373% | 0% | 0% | 0% |  | 0% | 11.91%
2007-2010 | 12.75% | 19.57% | 0.3036% | 57.89% |  | 15.75% |  | -1.487% |  | 58.9% | -0.3476% | 2.627% | 42.59% | 0% |  | 0.6211% | 11.15% |  | 2007-2010 | 12.75% | 19.57% | 0.1086% | 57.89% |  | 15.75% |  | -1.487% |  | 58.9% | -0.3476% | 2.627% | 42.59% | 0% |  | 0.6211% | 15.5% |  | 2007-2010 | 12.75% | 19.57% | 2.377% |  |  | 15.75% |  | -1.487% |  | 58.9% | -0.3476% | 2.627% | 42.59% | 0% |  | 0.6211% | 7.428% |  | 2007-2010 |  |  | 0.006303% | 57.89% | [9 empty] | 0% |  |  | 24.86% |  | 2007-2010 | 12.75% | 19.57% | 0.2727% | 57.89% |  | 15.75% |  | -1.487% |  | 58.9% | -0.3476% | 2.627% | 42.59% | 0% |  | 0.6211% | 11.53%
2010-2013 | 28.04% | 0% | -0.003027% | 37.85% |  | 13.8% |  | 16.97% | -23.11% | 9.979% | 19.23% | 0.2121% | 5.294% | 0% |  | 8.481% | 10.71% |  | 2010-2013 | 28.04% | 0% | -0.003289% | 37.85% |  | 13.8% |  | 16.97% | -23.11% | 9.979% | 19.23% | 0.2121% | 5.294% | 0% |  | 8.481% | 10.26% |  | 2010-2013 | 28.04% | 0% | -0.000176% |  |  | 13.8% |  | 16.97% | -23.11% | 9.979% | 19.23% | 0.2121% | 5.294% | 0% |  | 8.481% | 11.07% |  | 2010-2013 |  |  | -0.003426% | 37.85% | [9 empty] | 0% |  |  | 9.107% |  | 2010-2013 | 28.04% | 0% | -0.003068% | 37.85% |  | 13.8% |  | 16.97% | -23.11% | 9.979% | 19.23% | 0.2121% | 5.294% | 0% |  | 8.481% | 10.67%
2013-2016 | 9.283% | 25.75% | 0.04734% | 0.7374% |  | 3.214% |  | 8.877% | 11.24% | 21.15% | -0.01807% | 0% | 29.94% | 0% |  | 0% | 3.831% |  | 2013-2016 | 9.283% | 25.75% | 0.05163% | 0.7374% |  | 3.214% |  | 8.877% | 11.24% | 21.15% | -0.01807% | 0% | 29.94% | 0% |  | 0% | 2.777% |  | 2013-2016 | 9.283% | 25.75% | 0.0006729% |  |  | 3.214% |  | 8.877% | 11.24% | 21.15% | -0.01807% | 0% | 29.94% | 0% |  | 0% | 4.662% |  | 2013-2016 |  |  | 0.05387% | 0.7374% | [9 empty] | 0% |  |  | 0.1454% |  | 2013-2016 | 9.283% | 25.75% | 0.04802% | 0.7374% |  | 3.214% |  | 8.877% | 11.24% | 21.15% | -0.01807% | 0% | 29.94% | 0% |  | 0% | 3.744%
2016-2019 | 36.37% | 0% | 0.1522% | 59.81% |  | 18.13% |  | -37.66% | 49.15% | 7.33% | 26.92% | 0% | 1.376% | 0% |  | 0% | 8.76% |  | 2016-2019 | 36.37% | 0% | 0.1475% | 59.81% |  | 18.13% |  | -37.66% | 49.15% | 7.33% | 26.92% | 0% | 1.376% | 0% |  | 0% | 9.08% |  | 2016-2019 | 36.37% | 0% | 0.2039% |  |  | 18.13% |  | -37.66% | 49.15% | 7.33% | 26.92% | 0% | 1.376% | 0% |  | 0% | 8.503% |  | 2016-2019 |  |  | 0.145% | 59.81% | [9 empty] | 0% |  |  | 9.849% |  | 2016-2019 | 36.37% | 0% | 0.1515% | 59.81% |  | 18.13% |  | -37.66% | 49.15% | 7.33% | 26.92% | 0% | 1.376% | 0% |  | 0% | 8.786%
2004-2019 | 63.76% | 40.28% | 0.5427% | 89.99% |  | 49.07% |  | 44.14% | 75.24% | 78.17% | 39.94% | 2.834% | 62.43% | 0% |  | 9.05% | 38.86% |  | 2004-2019 | 63.76% | 40.28% | 0.3444% | 89.99% |  | 49.07% |  | 44.14% | 75.24% | 78.17% | 39.94% | 2.834% | 62.43% | 0% |  | 9.05% | 39.09% |  | 2004-2019 | 63.76% | 40.28% | 2.65% |  |  | 49.07% |  | 44.14% | 75.24% | 78.17% | 39.94% | 2.834% | 62.43% | 0% |  | 9.05% | 38.68% |  | 2004-2019 |  |  | 0.2403% | 89.99% | [9 empty] | 0% |  |  | 39.63% |  | 2004-2019 | 63.76% | 40.28% | 0.5113% | 89.99% |  | 49.07% |  | 44.14% | 75.24% | 78.17% | 39.94% | 2.834% | 62.43% | 0% |  | 9.05% | 38.88%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.12736 | 0.044275 | 0.15494 | 6.0849e-06 | 0 | 1.0913 | 0 | 0.19299 | 0.034279 | 0.022672 | 0.015029 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 2.4493 | 0% | CZ 0A | 4.088 | 1.4211 | 14.2779 | 0.00062091 | 0 | 35.0269 | 0 | 6.1946 | 1.1003 | 0.72773 | 0.48241 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 97.4401 | 0% | CZ 0A | 1.1981 | 0.41651 | 0.20607 | 0 | 0 | 10.2658 | 0 | 1.8155 | 0.32247 | 0.21328 | 0.14139 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 20.5102 | 0% | CZ 0A | 0 | 0 | 0.13575 | 6.2091e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.27459 | 0% | CZ 0A | 12.5431 | 4.3605 | 16.9946 | 0.00067865 | 0 | 107.4726 | 0 | 19.0068 | 3.376 | 2.2329 | 1.4802 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 244.7343 | 0%
CZ 0B | 0.12739 | 0.044282 | 0.15481 | 0.00017114 | 0 | 0.93115 | 0 | 0.18523 | 0.0324 | 0.020662 | 0.014899 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 2.2775 | 0% | CZ 0B | 4.0888 | 1.4214 | 14.2644 | 0.017463 | 0 | 29.888 | 0 | 5.9456 | 1.04 | 0.66321 | 0.47822 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 91.9277 | 0% | CZ 0B | 1.1984 | 0.41658 | 0.20612 | 0 | 0 | 8.7597 | 0 | 1.7426 | 0.3048 | 0.19438 | 0.14016 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 18.8937 | 0% | CZ 0B | 0 | 0 | 0.13561 | 0.00017463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.27462 | 0% | CZ 0B | 12.5457 | 4.3612 | 16.9801 | 0.019087 | 0 | 91.705 | 0 | 18.2429 | 3.1909 | 2.0349 | 1.4673 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 227.8142 | 0%
CZ 1A | 0.12754 | 0.044287 | 0.15988 | 1.9776e-05 | 0 | 0.71001 | 0 | 0.17532 | 0.032497 | 0.016684 | 0.01501 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 2.0478 | 4.246% | CZ 1A | 4.0936 | 1.4215 | 14.7821 | 0.002018 | 0 | 22.7898 | 0 | 5.6275 | 1.0431 | 0.53551 | 0.48179 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 84.8975 | 4.246% | CZ 1A | 1.1998 | 0.41663 | 0.20607 | 0 | 0 | 6.6793 | 0 | 1.6493 | 0.30571 | 0.15695 | 0.1412 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 16.686 | 4.246% | CZ 1A | 0 | 0 | 0.14079 | 2.018e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.27965 | 4.246% | CZ 1A | 12.5605 | 4.3617 | 17.5457 | 0.0022056 | 0 | 69.9256 | 0 | 17.2668 | 3.2004 | 1.6431 | 1.4783 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 205.2512 | 4.246%
CZ 1B | 0.12749 | 0.044232 | 0.16011 | 0.0042298 | 0 | 0.73478 | 0 | 0.17899 | 0.03263 | 0.01812 | 0.014901 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 2.082 | 0% | CZ 1B | 4.0922 | 1.4197 | 14.8054 | 0.43161 | 0 | 23.5848 | 0 | 5.7451 | 1.0473 | 0.58162 | 0.47829 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 86.3068 | 0% | CZ 1B | 1.1994 | 0.4161 | 0.20612 | 0 | 0 | 6.9123 | 0 | 1.6838 | 0.30696 | 0.17046 | 0.14018 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 16.9663 | 0% | CZ 1B | 0 | 0 | 0.14102 | 0.0043161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28418 | 0% | CZ 1B | 12.5562 | 4.3562 | 17.5715 | 0.47175 | 0 | 72.365 | 0 | 17.6277 | 3.2135 | 1.7846 | 1.4675 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 208.6809 | 0%
CZ 2A | 0.12734 | 0.044217 | 0.16569 | 0.0030797 | 0 | 0.59828 | 0 | 0.16848 | 0.026027 | 0.016957 | 0.015034 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.9316 | 16.73% | CZ 2A | 4.0873 | 1.4193 | 15.3746 | 0.31426 | 0 | 19.2035 | 0 | 5.4077 | 0.8354 | 0.54428 | 0.48256 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 81.7895 | 16.73% | CZ 2A | 1.1979 | 0.41597 | 0.20607 | 0 | 0 | 5.6282 | 0 | 1.5849 | 0.24484 | 0.15952 | 0.14143 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 15.5099 | 16.73% | CZ 2A | 0 | 0 | 0.14672 | 0.0031426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.2887 | 16.73% | CZ 2A | 12.5412 | 4.3547 | 18.1933 | 0.34348 | 0 | 58.9218 | 0 | 16.5924 | 2.5633 | 1.67 | 1.4806 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 193.9279 | 16.73%
CZ 2B | 0.12737 | 0.044249 | 0.16606 | 0.0034045 | 0 | 0.40505 | 0 | 0.18444 | 0.022539 | 0.012378 | 0.014896 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.7469 | 2.484% | CZ 2B | 4.0884 | 1.4203 | 15.4121 | 0.3474 | 0 | 13.0013 | 0 | 5.9202 | 0.72346 | 0.39732 | 0.47814 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 75.9093 | 2.484% | CZ 2B | 1.1983 | 0.41626 | 0.20609 | 0 | 0 | 3.8105 | 0 | 1.7351 | 0.21203 | 0.11645 | 0.14013 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 13.7659 | 2.484% | CZ 2B | 0 | 0 | 0.14709 | 0.003474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.2894 | 2.484% | CZ 2B | 12.5445 | 4.3578 | 18.2345 | 0.37971 | 0 | 39.8918 | 0 | 18.165 | 2.2198 | 1.2191 | 1.4671 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 175.7464 | 2.484%
CZ 3A | 0.12737 | 0.044241 | 0.1756 | 0.015882 | 0 | 0.33598 | 0 | 0.15982 | 0.02414 | 0.013626 | 0.014981 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.6782 | 13.33% | CZ 3A | 4.0883 | 1.4201 | 16.3866 | 1.6206 | 0 | 10.7841 | 0 | 5.1298 | 0.77485 | 0.43738 | 0.48086 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 75.243 | 13.33% | CZ 3A | 1.1982 | 0.41619 | 0.20609 | 0 | 0 | 3.1606 | 0 | 1.5035 | 0.2271 | 0.12819 | 0.14093 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 12.9118 | 13.33% | CZ 3A | 0 | 0 | 0.15683 | 0.016206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.31188 | 13.33% | CZ 3A | 12.544 | 4.3571 | 19.2995 | 1.7713 | 0 | 33.0886 | 0 | 15.7397 | 2.3775 | 1.342 | 1.4754 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 169.2622 | 13.33%
CZ 3B | 0.12739 | 0.044239 | 0.17301 | 0.007578 | 0 | 0.29214 | 0 | 0.19186 | 0.022157 | 0.011314 | 0.01508 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.6513 | 12.98% | CZ 3B | 4.0888 | 1.42 | 16.1218 | 0.77326 | 0 | 9.3769 | 0 | 6.1583 | 0.71119 | 0.36316 | 0.48404 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 73.6181 | 12.98% | CZ 3B | 1.1984 | 0.41617 | 0.20605 | 0 | 0 | 2.7482 | 0 | 1.8049 | 0.20844 | 0.10644 | 0.14186 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 12.7615 | 12.98% | CZ 3B | 0 | 0 | 0.15419 | 0.0077326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.30076 | 12.98% | CZ 3B | 12.5457 | 4.3569 | 19.0099 | 0.84518 | 0 | 28.7711 | 0 | 18.8956 | 2.1821 | 1.1143 | 1.4852 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 166.4729 | 12.98%
CZ 3C | 0.12743 | 0.044232 | 0.17686 | 0.049943 | 0 | 0.19446 | 0 | 0.14921 | 0 | 0.010494 | 0.014739 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.5339 | 2.16% | CZ 3C | 4.0902 | 1.4197 | 16.5142 | 5.0963 | 0 | 6.2417 | 0 | 4.7894 | 0 | 0.33685 | 0.47309 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 73.082 | 2.16% | CZ 3C | 1.1988 | 0.4161 | 0.20621 | 0 | 0 | 1.8293 | 0 | 1.4037 | 0 | 0.098724 | 0.13866 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 11.2225 | 2.16% | CZ 3C | 0 | 0 | 0.15811 | 0.050963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.34791 | 2.16% | CZ 3C | 12.55 | 4.3562 | 19.4398 | 5.5702 | 0 | 19.1514 | 0 | 14.6952 | 0 | 1.0335 | 1.4516 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 155.5149 | 2.16%
CZ 4A | 0.12728 | 0.044174 | 0.18338 | 0.026298 | 0 | 0.23234 | 0 | 0.16153 | 0.025899 | 0.01269 | 0.015092 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.5952 | 19.33% | CZ 4A | 4.0854 | 1.4179 | 17.1806 | 2.6835 | 0 | 7.4575 | 0 | 5.1848 | 0.83129 | 0.40734 | 0.48443 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 73.8533 | 19.33% | CZ 4A | 1.1974 | 0.41556 | 0.20605 | 0 | 0 | 2.1857 | 0 | 1.5196 | 0.24364 | 0.11938 | 0.14198 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 11.9603 | 19.33% | CZ 4A | 0 | 0 | 0.16478 | 0.026835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.33045 | 19.33% | CZ 4A | 12.5352 | 4.3505 | 20.1671 | 2.9331 | 0 | 22.8818 | 0 | 15.9086 | 2.5506 | 1.2498 | 1.4864 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 161.3301 | 19.33%
CZ 4B | 0.12723 | 0.044208 | 0.18116 | 0.011019 | 0 | 0.20255 | 0 | 0.208 | 0.023059 | 0.011542 | 0.01508 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.5904 | 0.5625% | CZ 4B | 4.0838 | 1.419 | 16.9544 | 1.1244 | 0 | 6.5015 | 0 | 6.6765 | 0.74015 | 0.37046 | 0.48404 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 72.4747 | 0.5625% | CZ 4B | 1.1969 | 0.41587 | 0.20603 | 0 | 0 | 1.9055 | 0 | 1.9568 | 0.21692 | 0.10858 | 0.14186 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 12.0794 | 0.5625% | CZ 4B | 0 | 0 | 0.16251 | 0.011244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3126 | 0.5625% | CZ 4B | 12.5302 | 4.3538 | 19.9197 | 1.229 | 0 | 19.9484 | 0 | 20.4853 | 2.271 | 1.1367 | 1.4852 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 160.6263 | 0.5625%
CZ 4C | 0.12733 | 0.044123 | 0.18575 | 0.018896 | 0 | 0.081938 | 0 | 0.15607 | 0.025998 | 0.0091206 | 0.015104 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.4309 | 3.179% | CZ 4C | 4.0869 | 1.4162 | 17.4222 | 1.9282 | 0 | 2.63 | 0 | 5.0095 | 0.83447 | 0.29275 | 0.48481 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 68.2257 | 3.179% | CZ 4C | 1.1978 | 0.41508 | 0.20605 | 0 | 0 | 0.77082 | 0 | 1.4682 | 0.24457 | 0.085801 | 0.14209 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 10.4614 | 3.179% | CZ 4C | 0 | 0 | 0.16719 | 0.019282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32531 | 3.179% | CZ 4C | 12.5397 | 4.3455 | 20.4312 | 2.1075 | 0 | 8.0697 | 0 | 15.3707 | 2.5604 | 0.89825 | 1.4876 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 145.0775 | 3.179%
CZ 5A | 0.12719 | 0.044188 | 0.19005 | 0.045402 | 0 | 0.14528 | 0 | 0.1584 | 0.024459 | 0.01197 | 0.015032 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.5285 | 15.41% | CZ 5A | 4.0826 | 1.4183 | 17.8607 | 4.6328 | 0 | 4.6631 | 0 | 5.0844 | 0.7851 | 0.3842 | 0.48249 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 73.5143 | 15.41% | CZ 5A | 1.1965 | 0.41569 | 0.20607 | 0 | 0 | 1.3667 | 0 | 1.4901 | 0.2301 | 0.1126 | 0.14141 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 11.0903 | 15.41% | CZ 5A | 0 | 0 | 0.17158 | 0.046328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35674 | 15.41% | CZ 5A | 12.5266 | 4.3519 | 20.9106 | 5.0637 | 0 | 14.3076 | 0 | 15.6003 | 2.4089 | 1.1788 | 1.4804 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 155.096 | 15.41%
CZ 5B | 0.12722 | 0.044188 | 0.18816 | 0.027943 | 0 | 0.15503 | 0 | 0.20232 | 0.025006 | 0.011058 | 0.015003 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.5625 | 4.56% | CZ 5B | 4.0836 | 1.4183 | 17.6679 | 2.8514 | 0 | 4.9762 | 0 | 6.4942 | 0.80264 | 0.35494 | 0.48155 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 73.2513 | 4.56% | CZ 5B | 1.1968 | 0.41569 | 0.20605 | 0 | 0 | 1.4584 | 0 | 1.9033 | 0.23524 | 0.10403 | 0.14114 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 11.5918 | 4.56% | CZ 5B | 0 | 0 | 0.16965 | 0.028514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.337 | 4.56% | CZ 5B | 12.5297 | 4.3519 | 20.6997 | 3.1165 | 0 | 15.2683 | 0 | 19.926 | 2.4627 | 1.089 | 1.4775 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 158.1886 | 4.56%
CZ 5C | 0.12726 | 0.04412 | 0.18948 | 0.019699 | 0 | 0.05639 | 0 | 0.15618 | 0.029306 | 0.011701 | 0.015109 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.4158 | 0.0501% | CZ 5C | 4.0849 | 1.4162 | 17.8029 | 2.0101 | 0 | 1.81 | 0 | 5.013 | 0.94067 | 0.37559 | 0.48497 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 68.0589 | 0.0501% | CZ 5C | 1.1972 | 0.41506 | 0.20603 | 0 | 0 | 0.53048 | 0 | 1.4692 | 0.2757 | 0.11008 | 0.14214 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 10.2769 | 0.0501% | CZ 5C | 0 | 0 | 0.171 | 0.020101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32994 | 0.0501% | CZ 5C | 12.5335 | 4.3452 | 20.8471 | 2.1971 | 0 | 5.5536 | 0 | 15.3814 | 2.8863 | 1.1524 | 1.488 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 143.6517 | 0.0501%
CZ 6A | 0.1272 | 0.044166 | 0.19499 | 0.08464 | 0 | 0.14918 | 0 | 0.16065 | 0.025753 | 0.0089295 | 0.015041 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.5771 | 3.403% | CZ 6A | 4.0829 | 1.4176 | 18.3654 | 8.6368 | 0 | 4.7882 | 0 | 5.1567 | 0.82663 | 0.28662 | 0.4828 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 78.1642 | 3.403% | CZ 6A | 1.1966 | 0.41549 | 0.20605 | 0 | 0 | 1.4033 | 0 | 1.5113 | 0.24227 | 0.084003 | 0.1415 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 11.1316 | 3.403% | CZ 6A | 0 | 0 | 0.17662 | 0.086368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.40183 | 3.403% | CZ 6A | 12.5276 | 4.3497 | 21.4621 | 9.44 | 0 | 14.6916 | 0 | 15.8221 | 2.5363 | 0.87943 | 1.4814 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 160.4573 | 3.403%
CZ 6B | 0.12715 | 0.044135 | 0.19371 | 0.061546 | 0 | 0.10484 | 0 | 0.18068 | 0.027113 | 0.007563 | 0.01502 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.5283 | 0.9897% | CZ 6B | 4.0814 | 1.4166 | 18.234 | 6.2802 | 0 | 3.3651 | 0 | 5.7995 | 0.87026 | 0.24276 | 0.4821 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 74.8925 | 0.9897% | CZ 6B | 1.1962 | 0.41519 | 0.20605 | 0 | 0 | 0.98626 | 0 | 1.6997 | 0.25506 | 0.071148 | 0.14129 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 10.902 | 0.9897% | CZ 6B | 0 | 0 | 0.17531 | 0.062802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37695 | 0.9897% | CZ 6B | 12.5228 | 4.3466 | 21.3185 | 6.8642 | 0 | 10.3252 | 0 | 17.7946 | 2.6702 | 0.74485 | 1.4792 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 155.3333 | 0.9897%
CZ 7 | 0.12715 | 0.044108 | 0.20086 | 0.11993 | 0 | 0.11822 | 0 | 0.15708 | 0.02675 | 0.012608 | 0.014995 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.5882 | 0.5763% | CZ 7 | 4.0812 | 1.4158 | 18.9637 | 12.2382 | 0 | 3.7947 | 0 | 5.0418 | 0.85861 | 0.4047 | 0.48132 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 81.4006 | 0.5763% | CZ 7 | 1.1961 | 0.41494 | 0.20607 | 0 | 0 | 1.1122 | 0 | 1.4777 | 0.25165 | 0.11861 | 0.14107 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 10.8494 | 0.5763% | CZ 7 | 0 | 0 | 0.18261 | 0.12238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.44383 | 0.5763% | CZ 7 | 12.5223 | 4.344 | 22.1161 | 13.3763 | 0 | 11.6434 | 0 | 15.4698 | 2.6345 | 1.2417 | 1.4768 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 162.0921 | 0.5763%
CZ 8 | 0.12726 | 0.043864 | 0.20882 | 0.19439 | 0 | 0.068909 | 0 | 0.14867 | 0.028961 | 0.010603 | 0.014959 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.613 | 0.01322% | CZ 8 | 4.0849 | 1.4079 | 19.7763 | 19.8362 | 0 | 2.2118 | 0 | 4.7719 | 0.92957 | 0.34034 | 0.48016 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 87.9597 | 0.01322% | CZ 8 | 1.1972 | 0.41264 | 0.20607 | 0 | 0 | 0.64825 | 0 | 1.3986 | 0.27244 | 0.099748 | 0.14073 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 10.3067 | 0.01322% | CZ 8 | 0 | 0 | 0.19073 | 0.19836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.52793 | 0.01322% | CZ 8 | 12.5335 | 4.32 | 23.0044 | 21.6809 | 0 | 6.7865 | 0 | 14.6416 | 2.8522 | 1.0443 | 1.4733 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 165.6037 | 0.01322%
US Weighted | 0.12731 | 0.044207 | 0.17838 | 0.023014 | 0 | 0.31212 | 0 | 0.16888 | 0.024576 | 0.012979 | 0.015034 | 0.22988 | 0.0052024 | 0.32037 | 0 | 0.21108 | 1.673 | 100% | US Weighted | 4.0865 | 1.4189 | 16.6703 | 2.3484 | 0 | 10.0184 | 0 | 5.4208 | 0.78884 | 0.4166 | 0.48256 | 7.3786 | 0.16699 | 19.7998 | 0 | 6.7752 | 75.7719 | 100% | US Weighted | 1.1977 | 0.41587 | 0.20607 | 0 | 0 | 2.9362 | 0 | 1.5888 | 0.2312 | 0.1221 | 0.14143 | 2.1625 | 0.048941 | 1.7339 | 0 | 1.9857 | 12.7704 | 100% | US Weighted | 0 | 0 | 0.15967 | 0.023484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32199 | 100% | US Weighted | 12.5384 | 4.3537 | 19.6094 | 2.5668 | 0 | 30.7394 | 0 | 16.6327 | 2.4204 | 1.2783 | 1.4806 | 22.6396 | 0.51237 | 33.3268 | 0 | 20.7883 | 168.8868 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.20012 | 0.044275 | 0.15511 | 0.0025808 | 0 | 1.2043 | 0 | 0.12991 | 0.073062 | 0.022822 | 0.020749 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 2.6195 | 0% | CZ 0A | 6.4235 | 1.4211 | 14.2921 | 0.26334 | 0 | 38.654 | 0 | 4.1699 | 2.3451 | 0.73254 | 0.66601 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 103.0906 | 0% | CZ 0A | 1.8826 | 0.41651 | 0.2065 | 0 | 0 | 11.3288 | 0 | 1.2221 | 0.68732 | 0.2147 | 0.1952 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 22.0855 | 0% | CZ 0A | 0 | 0 | 0.13588 | 0.0026334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.27735 | 0% | CZ 0A | 19.7093 | 4.3605 | 17.013 | 0.28783 | 0 | 118.6017 | 0 | 12.7944 | 7.1955 | 2.2476 | 2.0435 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 261.5275 | 0%
CZ 0B | 0.20021 | 0.044282 | 0.15497 | 0.0053638 | 0 | 1.0648 | 0 | 0.12192 | 0.071141 | 0.021509 | 0.020778 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 2.4715 | 0% | CZ 0B | 6.4264 | 1.4214 | 14.2784 | 0.54733 | 0 | 34.1767 | 0 | 3.9133 | 2.2835 | 0.69038 | 0.66694 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 98.5272 | 0% | CZ 0B | 1.8835 | 0.41658 | 0.20648 | 0 | 0 | 10.0166 | 0 | 1.1469 | 0.66925 | 0.20234 | 0.19547 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 20.6689 | 0% | CZ 0B | 0 | 0 | 0.13574 | 0.0054733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28005 | 0% | CZ 0B | 19.7181 | 4.3612 | 16.9979 | 0.59823 | 0 | 104.8641 | 0 | 12.0071 | 7.0064 | 2.1183 | 2.0464 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 246.9918 | 0%
CZ 1A | 0.20033 | 0.044287 | 0.16005 | 0.0046953 | 0 | 0.8428 | 0 | 0.12341 | 0.071211 | 0.018009 | 0.020718 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 2.2521 | 4.246% | CZ 1A | 6.4301 | 1.4215 | 14.7961 | 0.47911 | 0 | 27.052 | 0 | 3.9613 | 2.2857 | 0.57805 | 0.665 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 91.7918 | 4.246% | CZ 1A | 1.8845 | 0.41663 | 0.2065 | 0 | 0 | 7.9285 | 0 | 1.161 | 0.66991 | 0.16942 | 0.1949 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 18.5631 | 4.246% | CZ 1A | 0 | 0 | 0.14092 | 0.0047911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28455 | 4.246% | CZ 1A | 19.7293 | 4.3617 | 17.5639 | 0.52367 | 0 | 83.0034 | 0 | 12.1543 | 7.0133 | 1.7736 | 2.0404 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 225.4378 | 4.246%
CZ 1B | 0.20027 | 0.044232 | 0.16031 | 0.0096621 | 0 | 0.83919 | 0 | 0.11878 | 0.071296 | 0.019039 | 0.020759 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 2.2501 | 0% | CZ 1B | 6.4284 | 1.4197 | 14.8225 | 0.98593 | 0 | 26.9361 | 0 | 3.8124 | 2.2884 | 0.61112 | 0.66632 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 92.0939 | 0% | CZ 1B | 1.884 | 0.4161 | 0.20648 | 0 | 0 | 7.8945 | 0 | 1.1174 | 0.67071 | 0.17911 | 0.19529 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 18.4953 | 0% | CZ 1B | 0 | 0 | 0.14118 | 0.0098593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28988 | 0% | CZ 1B | 19.724 | 4.3562 | 17.5926 | 1.0776 | 0 | 82.6478 | 0 | 11.6977 | 7.0216 | 1.8751 | 2.0445 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 225.3113 | 0%
CZ 2A | 0.20016 | 0.044217 | 0.16589 | 0.029545 | 0 | 0.72251 | 0 | 0.11961 | 0.052798 | 0.018783 | 0.020643 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 2.1408 | 16.73% | CZ 2A | 6.4246 | 1.4193 | 15.3927 | 3.0148 | 0 | 23.1911 | 0 | 3.8393 | 1.6947 | 0.60289 | 0.66259 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 90.3648 | 16.73% | CZ 2A | 1.8829 | 0.41597 | 0.2065 | 0 | 0 | 6.7969 | 0 | 1.1252 | 0.49669 | 0.1767 | 0.19419 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 17.2269 | 16.73% | CZ 2A | 0 | 0 | 0.14688 | 0.030148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.31587 | 16.73% | CZ 2A | 19.7126 | 4.3547 | 18.2159 | 3.2952 | 0 | 71.1568 | 0 | 11.7801 | 5.1999 | 1.8499 | 2.033 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 214.8724 | 16.73%
CZ 2B | 0.20022 | 0.044249 | 0.16623 | 0.023112 | 0 | 0.466 | 0 | 0.12468 | 0.043937 | 0.013776 | 0.020522 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.8693 | 2.484% | CZ 2B | 6.4266 | 1.4203 | 15.4276 | 2.3584 | 0 | 14.9575 | 0 | 4.0019 | 1.4103 | 0.44219 | 0.65871 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 81.2263 | 2.484% | CZ 2B | 1.8835 | 0.41626 | 0.20648 | 0 | 0 | 4.3838 | 0 | 1.1729 | 0.41333 | 0.1296 | 0.19306 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 14.7307 | 2.484% | CZ 2B | 0 | 0 | 0.14723 | 0.023584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.30965 | 2.484% | CZ 2B | 19.7188 | 4.3578 | 18.254 | 2.5777 | 0 | 45.894 | 0 | 12.2789 | 4.3271 | 1.3568 | 2.0211 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 188.0604 | 2.484%
CZ 3A | 0.20024 | 0.044241 | 0.17586 | 0.059524 | 0 | 0.42706 | 0 | 0.11445 | 0.044423 | 0.015482 | 0.020524 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.8684 | 13.33% | CZ 3A | 6.4274 | 1.4201 | 16.4093 | 6.0739 | 0 | 13.7076 | 0 | 3.6736 | 1.4259 | 0.49693 | 0.65879 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 84.4164 | 13.33% | CZ 3A | 1.8838 | 0.41619 | 0.2065 | 0 | 0 | 4.0175 | 0 | 1.0767 | 0.4179 | 0.14564 | 0.19308 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 14.2889 | 13.33% | CZ 3A | 0 | 0 | 0.15705 | 0.060739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35663 | 13.33% | CZ 3A | 19.7212 | 4.3571 | 19.3272 | 6.6388 | 0 | 42.059 | 0 | 11.2716 | 4.375 | 1.5247 | 2.0214 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 188.57 | 13.33%
CZ 3B | 0.20021 | 0.044239 | 0.17325 | 0.033386 | 0 | 0.34425 | 0 | 0.12723 | 0.042048 | 0.012466 | 0.020546 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.7642 | 12.98% | CZ 3B | 6.4263 | 1.42 | 16.1438 | 3.4068 | 0 | 11.0498 | 0 | 4.0839 | 1.3496 | 0.40012 | 0.65949 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 79.0626 | 12.98% | CZ 3B | 1.8834 | 0.41617 | 0.20648 | 0 | 0 | 3.2385 | 0 | 1.1969 | 0.39556 | 0.11727 | 0.19328 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 13.5793 | 12.98% | CZ 3B | 0 | 0 | 0.15439 | 0.034068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3273 | 12.98% | CZ 3B | 19.7176 | 4.3569 | 19.0368 | 3.7236 | 0 | 33.904 | 0 | 12.5304 | 4.1411 | 1.2277 | 2.0235 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 177.9358 | 12.98%
CZ 3C | 0.20023 | 0.044232 | 0.17699 | 0.071703 | 0 | 0.24395 | 0 | 0.12205 | 0 | 0.01188 | 0.02067 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.6583 | 2.16% | CZ 3C | 6.4269 | 1.4197 | 16.5246 | 7.3166 | 0 | 7.8302 | 0 | 3.9174 | 0 | 0.38133 | 0.66345 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 78.6032 | 2.16% | CZ 3C | 1.8836 | 0.4161 | 0.20648 | 0 | 0 | 2.2949 | 0 | 1.1481 | 0 | 0.11176 | 0.19445 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 12.1872 | 2.16% | CZ 3C | 0 | 0 | 0.1582 | 0.073166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37021 | 2.16% | CZ 3C | 19.7195 | 4.3562 | 19.453 | 7.9971 | 0 | 24.0254 | 0 | 12.0197 | 0 | 1.17 | 2.0356 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 168.0508 | 2.16%
CZ 4A | 0.2 | 0.044174 | 0.1837 | 0.057499 | 0 | 0.29078 | 0 | 0.12392 | 0.053553 | 0.013184 | 0.02058 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.754 | 19.33% | CZ 4A | 6.4196 | 1.4179 | 17.2097 | 5.8672 | 0 | 9.3333 | 0 | 3.9774 | 1.7189 | 0.42317 | 0.66057 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 81.1506 | 19.33% | CZ 4A | 1.8815 | 0.41556 | 0.20648 | 0 | 0 | 2.7354 | 0 | 1.1657 | 0.50379 | 0.12403 | 0.1936 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 13.1578 | 19.33% | CZ 4A | 0 | 0 | 0.16505 | 0.058672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36256 | 19.33% | CZ 4A | 19.6971 | 4.3505 | 20.2018 | 6.4128 | 0 | 28.6372 | 0 | 12.2039 | 5.2742 | 1.2984 | 2.0268 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 177.3769 | 19.33%
CZ 4B | 0.19992 | 0.044208 | 0.18144 | 0.038621 | 0 | 0.23871 | 0 | 0.13223 | 0.04138 | 0.012185 | 0.020522 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.6758 | 0.5625% | CZ 4B | 6.4169 | 1.419 | 16.9791 | 3.9409 | 0 | 7.6619 | 0 | 4.2443 | 1.3282 | 0.39111 | 0.65871 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 77.1631 | 0.5625% | CZ 4B | 1.8807 | 0.41587 | 0.20648 | 0 | 0 | 2.2456 | 0 | 1.2439 | 0.38928 | 0.11463 | 0.19306 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 12.6213 | 0.5625% | CZ 4B | 0 | 0 | 0.16275 | 0.039409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.34099 | 0.5625% | CZ 4B | 19.689 | 4.3538 | 19.9497 | 4.3074 | 0 | 23.509 | 0 | 13.0228 | 4.0753 | 1.2 | 2.0211 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 169.4025 | 0.5625%
CZ 4C | 0.20015 | 0.044123 | 0.18607 | 0.055741 | 0 | 0.10797 | 0 | 0.12142 | 0.04161 | 0.009822 | 0.020643 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.5542 | 3.179% | CZ 4C | 6.4244 | 1.4162 | 17.4521 | 5.6878 | 0 | 3.4657 | 0 | 3.8972 | 1.3356 | 0.31527 | 0.66259 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 74.7798 | 3.179% | CZ 4C | 1.8829 | 0.41508 | 0.20648 | 0 | 0 | 1.0158 | 0 | 1.1422 | 0.39144 | 0.092399 | 0.19419 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 11.2721 | 3.179% | CZ 4C | 0 | 0 | 0.16748 | 0.056878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36319 | 3.179% | CZ 4C | 19.7119 | 4.3455 | 20.4667 | 6.2168 | 0 | 10.6339 | 0 | 11.9578 | 4.098 | 0.96732 | 2.033 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 157.7051 | 3.179%
CZ 5A | 0.1999 | 0.044188 | 0.19039 | 0.09053 | 0 | 0.18261 | 0 | 0.12372 | 0.048433 | 0.011992 | 0.020553 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.6789 | 15.41% | CZ 5A | 6.4162 | 1.4183 | 17.8923 | 9.2378 | 0 | 5.8612 | 0 | 3.9711 | 1.5546 | 0.3849 | 0.65972 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 81.5191 | 15.41% | CZ 5A | 1.8805 | 0.41569 | 0.20648 | 0 | 0 | 1.7178 | 0 | 1.1638 | 0.45562 | 0.11281 | 0.19335 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 12.0778 | 15.41% | CZ 5A | 0 | 0 | 0.17188 | 0.092378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.40309 | 15.41% | CZ 5A | 19.6869 | 4.3519 | 20.9479 | 10.0969 | 0 | 17.984 | 0 | 12.1843 | 4.7699 | 1.181 | 2.0242 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 170.5012 | 15.41%
CZ 5B | 0.19989 | 0.044188 | 0.18846 | 0.063654 | 0 | 0.18039 | 0 | 0.13266 | 0.046099 | 0.01122 | 0.020507 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.6537 | 4.56% | CZ 5B | 6.416 | 1.4183 | 17.6954 | 6.4953 | 0 | 5.7902 | 0 | 4.2581 | 1.4797 | 0.36014 | 0.65825 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 78.6943 | 4.56% | CZ 5B | 1.8804 | 0.41569 | 0.20646 | 0 | 0 | 1.697 | 0 | 1.248 | 0.43367 | 0.10555 | 0.19292 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 12.1114 | 4.56% | CZ 5B | 0 | 0 | 0.16991 | 0.064953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3737 | 4.56% | CZ 5B | 19.6862 | 4.3519 | 20.7325 | 7.0994 | 0 | 17.766 | 0 | 13.065 | 4.5401 | 1.105 | 2.0197 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 167.6399 | 4.56%
CZ 5C | 0.19997 | 0.04412 | 0.18985 | 0.057575 | 0 | 0.070094 | 0 | 0.12355 | 0.048888 | 0.0088134 | 0.020653 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.5301 | 0.0501% | CZ 5C | 6.4186 | 1.4162 | 17.8375 | 5.875 | 0 | 2.2499 | 0 | 3.9656 | 1.5692 | 0.28289 | 0.6629 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 74.4006 | 0.0501% | CZ 5C | 1.8812 | 0.41506 | 0.20648 | 0 | 0 | 0.6594 | 0 | 1.1623 | 0.4599 | 0.082911 | 0.19429 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 10.9932 | 0.0501% | CZ 5C | 0 | 0 | 0.17133 | 0.05875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36892 | 0.0501% | CZ 5C | 19.694 | 4.3452 | 20.888 | 6.4214 | 0 | 6.9032 | 0 | 12.1677 | 4.8147 | 0.868 | 2.034 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 155.4104 | 0.0501%
CZ 6A | 0.19984 | 0.044166 | 0.19536 | 0.15412 | 0 | 0.1939 | 0 | 0.12396 | 0.050281 | 0.010141 | 0.020462 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.7588 | 3.403% | CZ 6A | 6.4145 | 1.4176 | 18.3989 | 15.7265 | 0 | 6.2237 | 0 | 3.9788 | 1.6139 | 0.32551 | 0.65677 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 88.8792 | 3.403% | CZ 6A | 1.88 | 0.41549 | 0.2065 | 0 | 0 | 1.8241 | 0 | 1.1661 | 0.47301 | 0.095402 | 0.19249 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 12.1848 | 3.403% | CZ 6A | 0 | 0 | 0.17694 | 0.15726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.47305 | 3.403% | CZ 6A | 19.6816 | 4.3497 | 21.5018 | 17.189 | 0 | 19.0961 | 0 | 12.2082 | 4.9519 | 0.99877 | 2.0152 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 179.2665 | 3.403%
CZ 6B | 0.19977 | 0.044135 | 0.19405 | 0.12079 | 0 | 0.13082 | 0 | 0.12704 | 0.049541 | 0.0087409 | 0.020428 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.6619 | 0.9897% | CZ 6B | 6.4121 | 1.4166 | 18.2654 | 12.3259 | 0 | 4.1991 | 0 | 4.0776 | 1.5901 | 0.28056 | 0.65568 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 83.346 | 0.9897% | CZ 6B | 1.8793 | 0.41519 | 0.20648 | 0 | 0 | 1.2307 | 0 | 1.1951 | 0.46604 | 0.082228 | 0.19217 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 11.5989 | 0.9897% | CZ 6B | 0 | 0 | 0.17561 | 0.12326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.43771 | 0.9897% | CZ 6B | 19.6743 | 4.3466 | 21.3557 | 13.4722 | 0 | 12.8839 | 0 | 12.5111 | 4.879 | 0.86085 | 2.0118 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 169.2698 | 0.9897%
CZ 7 | 0.19971 | 0.044108 | 0.20125 | 0.21777 | 0 | 0.15384 | 0 | 0.12325 | 0.052133 | 0.016045 | 0.020382 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.7951 | 0.5763% | CZ 7 | 6.4104 | 1.4158 | 19.0008 | 22.2211 | 0 | 4.938 | 0 | 3.9561 | 1.6734 | 0.51501 | 0.65421 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 94.9078 | 0.5763% | CZ 7 | 1.8788 | 0.41494 | 0.2065 | 0 | 0 | 1.4473 | 0 | 1.1595 | 0.49044 | 0.15094 | 0.19174 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 11.8718 | 0.5763% | CZ 7 | 0 | 0 | 0.18296 | 0.22221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.54401 | 0.5763% | CZ 7 | 19.669 | 4.344 | 22.1597 | 24.2876 | 0 | 15.1513 | 0 | 12.1386 | 5.1344 | 1.5802 | 2.0073 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 183.7464 | 0.5763%
CZ 8 | 0.19994 | 0.043864 | 0.20917 | 0.34746 | 0 | 0.088296 | 0 | 0.12399 | 0.054363 | 0.013387 | 0.020304 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.8674 | 0.01322% | CZ 8 | 6.4176 | 1.4079 | 19.8084 | 35.4556 | 0 | 2.8341 | 0 | 3.9799 | 1.7449 | 0.4297 | 0.65172 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 106.8529 | 0.01322% | CZ 8 | 1.8809 | 0.41264 | 0.2065 | 0 | 0 | 0.83063 | 0 | 1.1664 | 0.51141 | 0.12594 | 0.19101 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 11.2572 | 0.01322% | CZ 8 | 0 | 0 | 0.19104 | 0.35456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.68443 | 0.01322% | CZ 8 | 19.6912 | 4.32 | 23.0424 | 38.753 | 0 | 8.6959 | 0 | 12.2115 | 5.354 | 1.3184 | 1.9997 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 192.6602 | 0.01322%
US Weighted | 0.20008 | 0.044207 | 0.17866 | 0.05726 | 0 | 0.38126 | 0 | 0.12269 | 0.048333 | 0.014006 | 0.020573 | 0.22988 | 0.005275 | 0.32037 | 0 | 0.21108 | 1.8337 | 100% | US Weighted | 6.4223 | 1.4189 | 16.6949 | 5.8429 | 0 | 12.2375 | 0 | 3.9379 | 1.5514 | 0.44956 | 0.66034 | 7.3786 | 0.16932 | 19.7998 | 0 | 6.7752 | 83.3386 | 100% | US Weighted | 1.8823 | 0.41587 | 0.20649 | 0 | 0 | 3.5866 | 0 | 1.1541 | 0.45468 | 0.13176 | 0.19353 | 2.1625 | 0.049624 | 1.7339 | 0 | 1.9857 | 13.9571 | 100% | US Weighted | 0 | 0 | 0.1599 | 0.058429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35717 | 100% | US Weighted | 19.7054 | 4.3537 | 19.6392 | 6.3863 | 0 | 37.5483 | 0 | 12.0827 | 4.7601 | 1.3794 | 2.0261 | 22.6396 | 0.51951 | 33.3268 | 0 | 20.7883 | 185.1553 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.22051 | 0.059626 | 0.1553 | 0.0031573 | 0 | 1.2623 | 0 | 0.14509 | 0.077449 | 0.029227 | 0.020732 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 2.7422 | 0% | CZ 0A | 7.0779 | 1.9139 | 14.312 | 0.32217 | 0 | 40.5167 | 0 | 4.6569 | 2.4859 | 0.93811 | 0.66546 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 107.0844 | 0% | CZ 0A | 2.0744 | 0.56092 | 0.2065 | 0 | 0 | 11.8748 | 0 | 1.3649 | 0.72859 | 0.27494 | 0.19504 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 23.233 | 0% | CZ 0A | 0 | 0 | 0.13607 | 0.0032217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.27814 | 0% | CZ 0A | 21.717 | 5.8723 | 17.0348 | 0.35214 | 0 | 124.317 | 0 | 14.2888 | 7.6276 | 2.8784 | 2.0418 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 273.6262 | 0%
CZ 0B | 0.2206 | 0.059636 | 0.15643 | 0.0059754 | 0 | 1.1052 | 0 | 0.13674 | 0.075035 | 0.02764 | 0.020764 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 2.5768 | 0% | CZ 0B | 7.0808 | 1.9142 | 14.4271 | 0.60973 | 0 | 35.4734 | 0 | 4.3889 | 2.4085 | 0.88718 | 0.66647 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 102.0514 | 0% | CZ 0B | 2.0753 | 0.56101 | 0.20648 | 0 | 0 | 10.3966 | 0 | 1.2863 | 0.70588 | 0.26002 | 0.19533 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 21.6399 | 0% | CZ 0B | 0 | 0 | 0.13723 | 0.0060973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28216 | 0% | CZ 0B | 21.7259 | 5.8733 | 17.1604 | 0.66644 | 0 | 108.8425 | 0 | 13.4666 | 7.3899 | 2.7221 | 2.0449 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 257.3881 | 0%
CZ 1A | 0.22088 | 0.059643 | 0.16023 | 0.0056658 | 0 | 0.88297 | 0 | 0.1373 | 0.075001 | 0.022781 | 0.020701 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 2.354 | 4.246% | CZ 1A | 7.0896 | 1.9144 | 14.8142 | 0.57814 | 0 | 28.3414 | 0 | 4.4072 | 2.4074 | 0.73122 | 0.66446 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 95.1433 | 4.246% | CZ 1A | 2.0779 | 0.56108 | 0.2065 | 0 | 0 | 8.3064 | 0 | 1.2917 | 0.70556 | 0.21431 | 0.19474 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 19.511 | 4.246% | CZ 1A | 0 | 0 | 0.1411 | 0.0057814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28572 | 4.246% | CZ 1A | 21.753 | 5.874 | 17.5837 | 0.63191 | 0 | 86.9596 | 0 | 13.5225 | 7.3865 | 2.2436 | 2.0387 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 235.4898 | 4.246%
CZ 1B | 0.22081 | 0.059568 | 0.16084 | 0.010806 | 0 | 0.86682 | 0 | 0.13306 | 0.075183 | 0.024578 | 0.020744 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 2.3413 | 0% | CZ 1B | 7.0877 | 1.912 | 14.8768 | 1.1027 | 0 | 27.823 | 0 | 4.2708 | 2.4132 | 0.7889 | 0.66585 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 95.1362 | 0% | CZ 1B | 2.0773 | 0.56038 | 0.20648 | 0 | 0 | 8.1545 | 0 | 1.2517 | 0.70727 | 0.23121 | 0.19515 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 19.3368 | 0% | CZ 1B | 0 | 0 | 0.14172 | 0.011027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.29159 | 0% | CZ 1B | 21.7471 | 5.8666 | 17.652 | 1.2052 | 0 | 85.369 | 0 | 13.104 | 7.4044 | 2.4206 | 2.043 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 234.308 | 0%
CZ 2A | 0.22068 | 0.059549 | 0.16597 | 0.029282 | 0 | 0.75123 | 0 | 0.13272 | 0.058801 | 0.023545 | 0.020628 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 2.2313 | 16.73% | CZ 2A | 7.0834 | 1.9114 | 15.4004 | 2.988 | 0 | 24.1127 | 0 | 4.2599 | 1.8874 | 0.75575 | 0.66213 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 93.2563 | 16.73% | CZ 2A | 2.076 | 0.5602 | 0.2065 | 0 | 0 | 7.067 | 0 | 1.2485 | 0.55317 | 0.2215 | 0.19406 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 18.0799 | 16.73% | CZ 2A | 0 | 0 | 0.14696 | 0.02988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.31568 | 16.73% | CZ 2A | 21.734 | 5.8647 | 18.2244 | 3.2658 | 0 | 73.9847 | 0 | 13.0707 | 5.7911 | 2.3189 | 2.0316 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 223.7821 | 16.73%
CZ 2B | 0.22076 | 0.05959 | 0.16631 | 0.018514 | 0 | 0.47806 | 0 | 0.13327 | 0.049468 | 0.01701 | 0.020517 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.9324 | 2.484% | CZ 2B | 7.0858 | 1.9127 | 15.4349 | 1.8892 | 0 | 15.3447 | 0 | 4.2777 | 1.5878 | 0.54599 | 0.65856 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 82.9326 | 2.484% | CZ 2B | 2.0767 | 0.56058 | 0.20648 | 0 | 0 | 4.4973 | 0 | 1.2537 | 0.46536 | 0.16002 | 0.19301 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 15.3661 | 2.484% | CZ 2B | 0 | 0 | 0.1473 | 0.018892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.30503 | 2.484% | CZ 2B | 21.7413 | 5.8687 | 18.2619 | 2.0649 | 0 | 47.0819 | 0 | 13.1252 | 4.8719 | 1.6753 | 2.0206 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 194.208 | 2.484%
CZ 3A | 0.22078 | 0.05958 | 0.17591 | 0.060953 | 0 | 0.44127 | 0 | 0.12779 | 0.052242 | 0.019259 | 0.020515 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.9472 | 13.33% | CZ 3A | 7.0867 | 1.9124 | 16.4143 | 6.2197 | 0 | 14.1637 | 0 | 4.1018 | 1.6769 | 0.61819 | 0.65848 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 87.0474 | 13.33% | CZ 3A | 2.077 | 0.56049 | 0.2065 | 0 | 0 | 4.1511 | 0 | 1.2022 | 0.49146 | 0.18118 | 0.19299 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 15.0158 | 13.33% | CZ 3A | 0 | 0 | 0.1571 | 0.062197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35813 | 13.33% | CZ 3A | 21.744 | 5.8678 | 19.3326 | 6.7982 | 0 | 43.4584 | 0 | 12.5855 | 5.1451 | 1.8968 | 2.0204 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 196.3448 | 13.33%
CZ 3B | 0.22074 | 0.059578 | 0.1733 | 0.026845 | 0 | 0.35233 | 0 | 0.1328 | 0.049083 | 0.015095 | 0.020558 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.8192 | 12.98% | CZ 3B | 7.0854 | 1.9123 | 16.1487 | 2.7393 | 0 | 11.3092 | 0 | 4.2626 | 1.5755 | 0.4845 | 0.65988 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 80.3726 | 12.98% | CZ 3B | 2.0766 | 0.56047 | 0.20648 | 0 | 0 | 3.3145 | 0 | 1.2493 | 0.46174 | 0.142 | 0.1934 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 14.1574 | 12.98% | CZ 3B | 0 | 0 | 0.15444 | 0.027393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.32067 | 12.98% | CZ 3B | 21.7399 | 5.8675 | 19.0421 | 2.994 | 0 | 34.6998 | 0 | 13.079 | 4.834 | 1.4866 | 2.0247 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 183.264 | 12.98%
CZ 3C | 0.22077 | 0.059568 | 0.17696 | 0.080172 | 0 | 0.2467 | 0 | 0.13444 | 0 | 0.014316 | 0.020653 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.7224 | 2.16% | CZ 3C | 7.0862 | 1.912 | 16.5222 | 8.1809 | 0 | 7.9185 | 0 | 4.3153 | 0 | 0.45951 | 0.6629 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 81.2528 | 2.16% | CZ 3C | 2.0768 | 0.56038 | 0.2065 | 0 | 0 | 2.3208 | 0 | 1.2647 | 0 | 0.13467 | 0.19429 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 12.7111 | 2.16% | CZ 3C | 0 | 0 | 0.15818 | 0.081809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37882 | 2.16% | CZ 3C | 21.7425 | 5.8666 | 19.4506 | 8.9417 | 0 | 24.2963 | 0 | 13.2405 | 0 | 1.4099 | 2.034 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 174.4782 | 2.16%
CZ 4A | 0.22038 | 0.059488 | 0.18377 | 0.058711 | 0 | 0.30235 | 0 | 0.13747 | 0.059399 | 0.017247 | 0.020578 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.8283 | 19.33% | CZ 4A | 7.0739 | 1.9094 | 17.2171 | 5.9909 | 0 | 9.7047 | 0 | 4.4124 | 1.9066 | 0.5536 | 0.6605 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 83.6244 | 19.33% | CZ 4A | 2.0732 | 0.55963 | 0.20648 | 0 | 0 | 2.8443 | 0 | 1.2932 | 0.55878 | 0.16225 | 0.19358 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 13.8444 | 19.33% | CZ 4A | 0 | 0 | 0.16513 | 0.059909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36387 | 19.33% | CZ 4A | 21.7047 | 5.8587 | 20.2099 | 6.5481 | 0 | 29.777 | 0 | 13.5385 | 5.8499 | 1.6986 | 2.0266 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 184.7082 | 19.33%
CZ 4B | 0.22029 | 0.059534 | 0.18146 | 0.030939 | 0 | 0.24672 | 0 | 0.13941 | 0.047724 | 0.014802 | 0.020544 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.7303 | 0.5625% | CZ 4B | 7.0709 | 1.9109 | 16.9815 | 3.1571 | 0 | 7.9191 | 0 | 4.4748 | 1.5318 | 0.47511 | 0.65941 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 78.376 | 0.5625% | CZ 4B | 2.0724 | 0.56006 | 0.20646 | 0 | 0 | 2.321 | 0 | 1.3115 | 0.44896 | 0.13925 | 0.19326 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 13.2057 | 0.5625% | CZ 4B | 0 | 0 | 0.16277 | 0.031571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.33318 | 0.5625% | CZ 4B | 21.6956 | 5.8633 | 19.9522 | 3.4507 | 0 | 24.2982 | 0 | 13.73 | 4.7001 | 1.4578 | 2.0233 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 174.6673 | 0.5625%
CZ 4C | 0.22052 | 0.059421 | 0.18615 | 0.054747 | 0 | 0.10753 | 0 | 0.13576 | 0.051084 | 0.012763 | 0.02067 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.6175 | 3.179% | CZ 4C | 7.0784 | 1.9073 | 17.4602 | 5.5865 | 0 | 3.4515 | 0 | 4.3576 | 1.6397 | 0.40967 | 0.66345 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 76.7494 | 3.179% | CZ 4C | 2.0746 | 0.55899 | 0.20648 | 0 | 0 | 1.0116 | 0 | 1.2771 | 0.48056 | 0.12007 | 0.19445 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 11.8767 | 3.179% | CZ 4C | 0 | 0 | 0.16756 | 0.055865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36226 | 3.179% | CZ 4C | 21.7185 | 5.8521 | 20.4756 | 6.106 | 0 | 10.5901 | 0 | 13.3703 | 5.031 | 1.257 | 2.0356 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 163.9324 | 3.179%
CZ 5A | 0.22032 | 0.059508 | 0.19052 | 0.094689 | 0 | 0.1861 | 0 | 0.13784 | 0.053986 | 0.015167 | 0.020549 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.7475 | 15.41% | CZ 5A | 7.0718 | 1.9101 | 17.9052 | 9.6622 | 0 | 5.9734 | 0 | 4.4243 | 1.7328 | 0.48683 | 0.65956 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 84.0215 | 15.41% | CZ 5A | 2.0726 | 0.55981 | 0.20648 | 0 | 0 | 1.7507 | 0 | 1.2967 | 0.50786 | 0.14268 | 0.19331 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 12.6831 | 15.41% | CZ 5A | 0 | 0 | 0.17201 | 0.096622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.40747 | 15.41% | CZ 5A | 21.6982 | 5.8606 | 20.962 | 10.5608 | 0 | 18.3282 | 0 | 13.5749 | 5.3168 | 1.4937 | 2.0237 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 177.3153 | 15.41%
CZ 5B | 0.22032 | 0.05951 | 0.18857 | 0.057073 | 0 | 0.18237 | 0 | 0.13766 | 0.050554 | 0.013532 | 0.020512 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.699 | 4.56% | CZ 5B | 7.0718 | 1.9101 | 17.7064 | 5.8237 | 0 | 5.8538 | 0 | 4.4185 | 1.6227 | 0.43435 | 0.6584 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 79.6951 | 4.56% | CZ 5B | 2.0726 | 0.55983 | 0.20648 | 0 | 0 | 1.7156 | 0 | 1.295 | 0.47558 | 0.1273 | 0.19297 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 12.5984 | 4.56% | CZ 5B | 0 | 0 | 0.17002 | 0.058237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3671 | 4.56% | CZ 5B | 21.6985 | 5.8609 | 20.7447 | 6.3653 | 0 | 17.9611 | 0 | 13.5573 | 4.9788 | 1.3327 | 2.0202 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 172.0157 | 4.56%
CZ 5C | 0.22041 | 0.059416 | 0.18998 | 0.057893 | 0 | 0.065208 | 0 | 0.13834 | 0.057781 | 0.011355 | 0.020686 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.5899 | 0.0501% | CZ 5C | 7.0746 | 1.9071 | 17.8506 | 5.9074 | 0 | 2.093 | 0 | 4.4403 | 1.8546 | 0.36448 | 0.66399 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 76.3514 | 0.0501% | CZ 5C | 2.0734 | 0.55894 | 0.20646 | 0 | 0 | 0.61344 | 0 | 1.3014 | 0.54356 | 0.10682 | 0.1946 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 11.5516 | 0.0501% | CZ 5C | 0 | 0 | 0.17146 | 0.059074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36937 | 0.0501% | CZ 5C | 21.7068 | 5.8516 | 20.9022 | 6.4568 | 0 | 6.4221 | 0 | 13.624 | 5.6906 | 1.1183 | 2.0373 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 161.3059 | 0.0501%
CZ 6A | 0.22032 | 0.059479 | 0.19553 | 0.16548 | 0 | 0.19468 | 0 | 0.13848 | 0.057283 | 0.01708 | 0.020454 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.8376 | 3.403% | CZ 6A | 7.0718 | 1.9091 | 18.4165 | 16.8859 | 0 | 6.2489 | 0 | 4.445 | 1.8386 | 0.54824 | 0.65654 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 92.2159 | 3.403% | CZ 6A | 2.0726 | 0.55954 | 0.2065 | 0 | 0 | 1.8315 | 0 | 1.3028 | 0.53888 | 0.16068 | 0.19242 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 12.8178 | 3.403% | CZ 6A | 0 | 0 | 0.17712 | 0.16886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.48482 | 3.403% | CZ 6A | 21.6982 | 5.8578 | 21.521 | 18.4563 | 0 | 19.1736 | 0 | 13.6385 | 5.6415 | 1.6822 | 2.0144 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 187.1797 | 3.403%
CZ 6B | 0.22023 | 0.059438 | 0.19422 | 0.12348 | 0 | 0.12583 | 0 | 0.13469 | 0.055976 | 0.013682 | 0.020425 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.7168 | 0.9897% | CZ 6B | 7.0691 | 1.9078 | 18.2833 | 12.5998 | 0 | 4.0387 | 0 | 4.3233 | 1.7967 | 0.43917 | 0.65561 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 85.3087 | 0.9897% | CZ 6B | 2.0718 | 0.55915 | 0.20648 | 0 | 0 | 1.1837 | 0 | 1.2671 | 0.52659 | 0.12871 | 0.19215 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 12.0886 | 0.9897% | CZ 6B | 0 | 0 | 0.17579 | 0.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.44062 | 0.9897% | CZ 6B | 21.6899 | 5.8537 | 21.3753 | 13.7716 | 0 | 12.392 | 0 | 13.265 | 5.5129 | 1.3475 | 2.0116 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 174.7157 | 0.9897%
CZ 7 | 0.22017 | 0.059401 | 0.20148 | 0.23499 | 0 | 0.15059 | 0 | 0.13857 | 0.057491 | 0.017015 | 0.020367 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.8689 | 0.5763% | CZ 7 | 7.067 | 1.9067 | 19.0237 | 23.9789 | 0 | 4.8336 | 0 | 4.4478 | 1.8453 | 0.54614 | 0.65374 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 98.4981 | 0.5763% | CZ 7 | 2.0712 | 0.55881 | 0.2065 | 0 | 0 | 1.4167 | 0 | 1.3036 | 0.54083 | 0.16007 | 0.1916 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 12.4022 | 0.5763% | CZ 7 | 0 | 0 | 0.18319 | 0.23979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.56182 | 0.5763% | CZ 7 | 21.6835 | 5.8502 | 22.1847 | 26.2089 | 0 | 14.831 | 0 | 13.6471 | 5.662 | 1.6757 | 2.0059 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 191.2451 | 0.5763%
CZ 8 | 0.22043 | 0.059072 | 0.20949 | 0.38234 | 0 | 0.078808 | 0 | 0.14079 | 0.060332 | 0.017445 | 0.020283 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.9578 | 0.01322% | CZ 8 | 7.0754 | 1.8961 | 19.8407 | 39.0143 | 0 | 2.5296 | 0 | 4.5189 | 1.9365 | 0.55996 | 0.65103 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 112.2178 | 0.01322% | CZ 8 | 2.0737 | 0.55571 | 0.2065 | 0 | 0 | 0.74138 | 0 | 1.3244 | 0.56757 | 0.16412 | 0.1908 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 11.7771 | 0.01322% | CZ 8 | 0 | 0 | 0.19136 | 0.39014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.72034 | 0.01322% | CZ 8 | 21.7094 | 5.8178 | 23.0776 | 42.6427 | 0 | 7.7615 | 0 | 13.8653 | 5.9419 | 1.7181 | 1.9975 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 202.028 | 0.01322%
US Weighted | 0.22056 | 0.059534 | 0.17874 | 0.057686 | 0 | 0.39392 | 0 | 0.13464 | 0.054454 | 0.017764 | 0.020569 | 0.22988 | 0.0075292 | 0.32037 | 0 | 0.21108 | 1.9067 | 100% | US Weighted | 7.0794 | 1.9109 | 16.7035 | 5.8863 | 0 | 12.644 | 0 | 4.3216 | 1.7479 | 0.57018 | 0.66022 | 7.3786 | 0.24167 | 19.7998 | 0 | 6.7752 | 85.7192 | 100% | US Weighted | 2.0749 | 0.56005 | 0.20649 | 0 | 0 | 3.7057 | 0 | 1.2666 | 0.51227 | 0.16711 | 0.1935 | 2.1625 | 0.070829 | 1.7339 | 0 | 1.9857 | 14.6395 | 100% | US Weighted | 0 | 0 | 0.15999 | 0.058863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35769 | 100% | US Weighted | 21.7218 | 5.8632 | 19.6486 | 6.4337 | 0 | 38.7953 | 0 | 13.2598 | 5.3629 | 1.7495 | 2.0257 | 22.6396 | 0.74151 | 33.3268 | 0 | 20.7883 | 192.3568 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.30653 | 0.059626 | 0.15529 | 0.0021214 | 0 | 1.4251 | 0 | 0.21771 | 0.077613 | 0.031892 | 0.025662 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 3.0909 | 0% | CZ 0A | 9.8388 | 1.9139 | 14.3105 | 0.21646 | 0 | 45.7432 | 0 | 6.9879 | 2.4912 | 1.0237 | 0.82368 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 118.2017 | 0% | CZ 0A | 2.8836 | 0.56092 | 0.2065 | 0 | 0 | 13.4066 | 0 | 2.048 | 0.73014 | 0.30002 | 0.24141 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 26.5227 | 0% | CZ 0A | 0 | 0 | 0.13606 | 0.0021646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.27706 | 0% | CZ 0A | 30.1883 | 5.8723 | 17.0331 | 0.2366 | 0 | 140.3533 | 0 | 21.441 | 7.6438 | 3.1409 | 2.5273 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 307.9489 | 0%
CZ 0B | 0.30654 | 0.059636 | 0.1564 | 0.0054559 | 0 | 1.6888 | 0 | 0.282 | 0.0088933 | 0.041003 | 0.025911 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 3.364 | 0% | CZ 0B | 9.8393 | 1.9142 | 14.4247 | 0.55672 | 0 | 54.2081 | 0 | 9.0516 | 0.28545 | 1.3161 | 0.83168 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 127.2801 | 0% | CZ 0B | 2.8837 | 0.56101 | 0.20644 | 0 | 0 | 15.8875 | 0 | 2.6529 | 0.083662 | 0.38573 | 0.24375 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 29.0502 | 0% | CZ 0B | 0 | 0 | 0.1372 | 0.0055672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28161 | 0% | CZ 0B | 30.1898 | 5.8733 | 17.1575 | 0.6085 | 0 | 166.326 | 0 | 27.7728 | 0.87586 | 4.0382 | 2.5518 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 334.906 | 0%
CZ 1A | 0.30666 | 0.059643 | 0.16021 | 0.0041142 | 0 | 1.0083 | 0 | 0.1968 | 0.075657 | 0.02518 | 0.025625 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.6515 | 4.246% | CZ 1A | 9.8432 | 1.9144 | 14.813 | 0.41981 | 0 | 32.3646 | 0 | 6.3168 | 2.4284 | 0.80823 | 0.82252 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 104.5834 | 4.246% | CZ 1A | 2.8849 | 0.56108 | 0.2065 | 0 | 0 | 9.4855 | 0 | 1.8513 | 0.71173 | 0.23688 | 0.24107 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 22.3245 | 4.246% | CZ 1A | 0 | 0 | 0.14108 | 0.0041981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28412 | 4.246% | CZ 1A | 30.2019 | 5.874 | 17.5824 | 0.45885 | 0 | 99.3038 | 0 | 19.3817 | 7.4511 | 2.4799 | 2.5237 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 264.7697 | 4.246%
CZ 1B | 0.30663 | 0.059568 | 0.16083 | 0.034249 | 0 | 1.3066 | 0 | 0.2433 | 0.0089537 | 0.034509 | 0.02578 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.9697 | 0% | CZ 1B | 9.8421 | 1.912 | 14.8757 | 3.4948 | 0 | 41.9386 | 0 | 7.8094 | 0.2874 | 1.1077 | 0.82748 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 116.9475 | 0% | CZ 1B | 2.8845 | 0.56038 | 0.20646 | 0 | 0 | 12.2915 | 0 | 2.2888 | 0.084231 | 0.32464 | 0.24252 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 25.0286 | 0% | CZ 1B | 0 | 0 | 0.14171 | 0.034948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3155 | 0% | CZ 1B | 30.1983 | 5.8666 | 17.6507 | 3.8198 | 0 | 128.6797 | 0 | 23.9616 | 0.88181 | 3.3986 | 2.539 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 296.5083 | 0%
CZ 2A | 0.30653 | 0.059549 | 0.16596 | 0.023702 | 0 | 0.84271 | 0 | 0.1678 | 0.063107 | 0.025103 | 0.025555 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.4693 | 16.73% | CZ 2A | 9.8391 | 1.9114 | 15.3993 | 2.4186 | 0 | 27.0491 | 0 | 5.386 | 2.0256 | 0.80575 | 0.82026 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 100.5074 | 16.73% | CZ 2A | 2.8837 | 0.5602 | 0.2065 | 0 | 0 | 7.9277 | 0 | 1.5785 | 0.59366 | 0.23615 | 0.24041 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 20.3723 | 16.73% | CZ 2A | 0 | 0 | 0.14695 | 0.024186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.30997 | 16.73% | CZ 2A | 30.1891 | 5.8647 | 18.2232 | 2.6435 | 0 | 82.9946 | 0 | 16.5257 | 6.2151 | 2.4723 | 2.5168 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 247.1573 | 16.73%
CZ 2B | 0.30656 | 0.05959 | 0.16631 | 0.06327 | 0 | 0.62682 | 0 | 0.16957 | 0.0084748 | 0.019622 | 0.025391 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.2349 | 2.484% | CZ 2B | 9.8401 | 1.9127 | 15.4348 | 6.4561 | 0 | 20.1196 | 0 | 5.4429 | 0.27202 | 0.62983 | 0.81499 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 95.7754 | 2.484% | CZ 2B | 2.884 | 0.56058 | 0.20648 | 0 | 0 | 5.8967 | 0 | 1.5952 | 0.079726 | 0.18459 | 0.23886 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 17.7916 | 2.484% | CZ 2B | 0 | 0 | 0.1473 | 0.064561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3507 | 2.484% | CZ 2B | 30.1922 | 5.8687 | 18.2619 | 7.0566 | 0 | 61.7327 | 0 | 16.7003 | 0.83465 | 1.9325 | 2.5006 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 224.5925 | 2.484%
CZ 3A | 0.30657 | 0.05958 | 0.1759 | 0.058379 | 0 | 0.4964 | 0 | 0.15382 | 0.057278 | 0.020498 | 0.025437 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.1432 | 13.33% | CZ 3A | 9.8401 | 1.9124 | 16.4133 | 5.957 | 0 | 15.9334 | 0 | 4.9373 | 1.8385 | 0.65793 | 0.81646 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 93.1587 | 13.33% | CZ 3A | 2.884 | 0.56049 | 0.2065 | 0 | 0 | 4.6698 | 0 | 1.447 | 0.53883 | 0.19283 | 0.23929 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 16.8843 | 13.33% | CZ 3A | 0 | 0 | 0.15709 | 0.05957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3555 | 13.33% | CZ 3A | 30.1924 | 5.8678 | 19.3315 | 6.511 | 0 | 48.8881 | 0 | 15.149 | 5.641 | 2.0187 | 2.5051 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 215.6169 | 13.33%
CZ 3B | 0.30658 | 0.059578 | 0.17329 | 0.13238 | 0 | 0.44938 | 0 | 0.15947 | 0 | 0.018302 | 0.0254 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.1137 | 12.98% | CZ 3B | 9.8405 | 1.9123 | 16.1473 | 13.5086 | 0 | 14.4241 | 0 | 5.1185 | 0 | 0.58744 | 0.8153 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 97.2064 | 12.98% | CZ 3B | 2.8841 | 0.56047 | 0.20648 | 0 | 0 | 4.2275 | 0 | 1.5002 | 0 | 0.17217 | 0.23895 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 15.9353 | 12.98% | CZ 3B | 0 | 0 | 0.15443 | 0.13509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.42835 | 12.98% | CZ 3B | 30.1936 | 5.8675 | 19.0406 | 14.7649 | 0 | 44.2573 | 0 | 15.7051 | 0 | 1.8024 | 2.5016 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 213.6454 | 12.98%
CZ 3C | 0.30662 | 0.059568 | 0.17695 | 0.07717 | 0 | 0.28942 | 0 | 0.15532 | 0 | 0.015515 | 0.025574 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 1.8955 | 2.16% | CZ 3C | 9.8418 | 1.912 | 16.5212 | 7.8745 | 0 | 9.2898 | 0 | 4.9856 | 0 | 0.49801 | 0.82089 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 86.5961 | 2.16% | CZ 3C | 2.8845 | 0.56038 | 0.20648 | 0 | 0 | 2.7227 | 0 | 1.4612 | 0 | 0.14596 | 0.24059 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 14.3673 | 2.16% | CZ 3C | 0 | 0 | 0.15817 | 0.078745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.37575 | 2.16% | CZ 3C | 30.1976 | 5.8666 | 19.4492 | 8.6068 | 0 | 28.5038 | 0 | 15.2971 | 0 | 1.528 | 2.5187 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 191.4803 | 2.16%
CZ 4A | 0.30645 | 0.059488 | 0.18377 | 0.060482 | 0 | 0.34503 | 0 | 0.16176 | 0.059225 | 0.018522 | 0.025483 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.0095 | 19.33% | CZ 4A | 9.8363 | 1.9094 | 17.2173 | 6.1716 | 0 | 11.0747 | 0 | 5.1921 | 1.901 | 0.59451 | 0.81794 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 89.5673 | 19.33% | CZ 4A | 2.8828 | 0.55963 | 0.20648 | 0 | 0 | 3.2458 | 0 | 1.5217 | 0.55715 | 0.17424 | 0.23972 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 15.5331 | 19.33% | CZ 4A | 0 | 0 | 0.16513 | 0.061716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36568 | 19.33% | CZ 4A | 30.1805 | 5.8587 | 20.2102 | 6.7456 | 0 | 33.9805 | 0 | 15.931 | 5.8328 | 1.8241 | 2.5097 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 202.5852 | 19.33%
CZ 4B | 0.30643 | 0.059534 | 0.1815 | 0.22135 | 0 | 0.30533 | 0 | 0.16134 | 0 | 0.019688 | 0.025333 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.0698 | 0.5625% | CZ 4B | 9.8356 | 1.9109 | 16.9847 | 22.587 | 0 | 9.8004 | 0 | 5.1785 | 0 | 0.63193 | 0.81312 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 102.5946 | 0.5625% | CZ 4B | 2.8827 | 0.56006 | 0.20648 | 0 | 0 | 2.8723 | 0 | 1.5177 | 0 | 0.18521 | 0.23831 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 14.6083 | 0.5625% | CZ 4B | 0 | 0 | 0.1628 | 0.22587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.52751 | 0.5625% | CZ 4B | 30.1786 | 5.8633 | 19.9559 | 24.6875 | 0 | 30.0704 | 0 | 15.8893 | 0 | 1.9389 | 2.4949 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 210.5912 | 0.5625%
CZ 4C | 0.30648 | 0.059421 | 0.18619 | 0.27427 | 0 | 0.13336 | 0 | 0.15176 | 0 | 0.017044 | 0.025468 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 1.9433 | 3.179% | CZ 4C | 9.8372 | 1.9073 | 17.4635 | 27.9868 | 0 | 4.2804 | 0 | 4.8713 | 0 | 0.54708 | 0.81747 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 102.5633 | 3.179% | CZ 4C | 2.8831 | 0.55899 | 0.20648 | 0 | 0 | 1.2545 | 0 | 1.4277 | 0 | 0.16034 | 0.23959 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 12.8762 | 3.179% | CZ 4C | 0 | 0 | 0.16759 | 0.27987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.5863 | 3.179% | CZ 4C | 30.1833 | 5.8521 | 20.4793 | 30.5895 | 0 | 13.1336 | 0 | 14.9465 | 0 | 1.6786 | 2.5082 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 198.8834 | 3.179%
CZ 5A | 0.3064 | 0.059508 | 0.19051 | 0.092909 | 0 | 0.21776 | 0 | 0.15837 | 0.053836 | 0.016265 | 0.025463 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 1.9103 | 15.41% | CZ 5A | 9.8348 | 1.9101 | 17.9042 | 9.4805 | 0 | 6.9897 | 0 | 5.0832 | 1.728 | 0.52208 | 0.81731 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 89.1222 | 15.41% | CZ 5A | 2.8824 | 0.55981 | 0.20648 | 0 | 0 | 2.0486 | 0 | 1.4898 | 0.50645 | 0.15301 | 0.23954 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 14.2316 | 15.41% | CZ 5A | 0 | 0 | 0.172 | 0.094805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.40564 | 15.41% | CZ 5A | 30.176 | 5.8606 | 20.9609 | 10.3622 | 0 | 21.4465 | 0 | 15.5968 | 5.3021 | 1.6019 | 2.5078 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 193.3269 | 15.41%
CZ 5B | 0.30644 | 0.05951 | 0.18857 | 0.35406 | 0 | 0.22791 | 0 | 0.16197 | 0 | 0.020108 | 0.025299 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.1332 | 4.56% | CZ 5B | 9.8359 | 1.9101 | 17.7072 | 36.1284 | 0 | 7.3154 | 0 | 5.1988 | 0 | 0.64544 | 0.81203 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 114.4057 | 4.56% | CZ 5B | 2.8828 | 0.55983 | 0.20648 | 0 | 0 | 2.144 | 0 | 1.5237 | 0 | 0.18917 | 0.23799 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 13.8894 | 4.56% | CZ 5B | 0 | 0 | 0.17003 | 0.36128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.67015 | 4.56% | CZ 5B | 30.1795 | 5.8609 | 20.7456 | 39.4884 | 0 | 22.4457 | 0 | 15.9514 | 0 | 1.9804 | 2.4916 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 218.6557 | 4.56%
CZ 5C | 0.30645 | 0.059416 | 0.18997 | 0.057666 | 0 | 0.08835 | 0 | 0.15498 | 0.057246 | 0.012843 | 0.025599 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 1.7418 | 0.0501% | CZ 5C | 9.8365 | 1.9071 | 17.8494 | 5.8843 | 0 | 2.8358 | 0 | 4.9745 | 1.8375 | 0.41223 | 0.82166 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 81.2114 | 0.0501% | CZ 5C | 2.8829 | 0.55894 | 0.20646 | 0 | 0 | 0.83114 | 0 | 1.458 | 0.53854 | 0.12082 | 0.24082 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 12.9831 | 0.0501% | CZ 5C | 0 | 0 | 0.17145 | 0.058843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.36913 | 0.0501% | CZ 5C | 30.1812 | 5.8516 | 20.9009 | 6.4315 | 0 | 8.7012 | 0 | 15.2633 | 5.6379 | 1.2648 | 2.5211 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 176.2658 | 0.0501%
CZ 6A | 0.30641 | 0.059479 | 0.19552 | 0.1668 | 0 | 0.22571 | 0 | 0.16301 | 0.057365 | 0.018159 | 0.025374 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.0072 | 3.403% | CZ 6A | 9.8352 | 1.9091 | 18.4162 | 17.02 | 0 | 7.2449 | 0 | 5.2323 | 1.8413 | 0.58286 | 0.81444 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 97.7487 | 3.403% | CZ 6A | 2.8825 | 0.55954 | 0.2065 | 0 | 0 | 2.1234 | 0 | 1.5335 | 0.53965 | 0.17083 | 0.2387 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 14.4001 | 3.403% | CZ 6A | 0 | 0 | 0.17712 | 0.1702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.48616 | 3.403% | CZ 6A | 30.1771 | 5.8578 | 21.5206 | 18.6029 | 0 | 22.2294 | 0 | 16.0543 | 5.6496 | 1.7884 | 2.4989 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 203.8915 | 3.403%
CZ 6B | 0.30638 | 0.059438 | 0.19421 | 0.12449 | 0 | 0.15339 | 0 | 0.15901 | 0.055916 | 0.014831 | 0.02534 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 1.8823 | 0.9897% | CZ 6B | 9.8341 | 1.9078 | 18.2824 | 12.7028 | 0 | 4.9234 | 0 | 5.1038 | 1.7948 | 0.47604 | 0.81335 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 90.6908 | 0.9897% | CZ 6B | 2.8822 | 0.55915 | 0.20648 | 0 | 0 | 1.443 | 0 | 1.4958 | 0.52602 | 0.13952 | 0.23838 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 13.636 | 0.9897% | CZ 6B | 0 | 0 | 0.17578 | 0.12703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.44165 | 0.9897% | CZ 6B | 30.1738 | 5.8537 | 21.3743 | 13.8841 | 0 | 15.1063 | 0 | 15.6599 | 5.5069 | 1.4606 | 2.4956 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 191.0277 | 0.9897%
CZ 7 | 0.30635 | 0.059401 | 0.20149 | 0.23659 | 0 | 0.17872 | 0 | 0.16453 | 0.057263 | 0.018154 | 0.025287 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.0371 | 0.5763% | CZ 7 | 9.8331 | 1.9067 | 19.0247 | 24.1422 | 0 | 5.7366 | 0 | 5.2809 | 1.838 | 0.58271 | 0.81165 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 104.0088 | 0.5763% | CZ 7 | 2.8819 | 0.55881 | 0.2065 | 0 | 0 | 1.6813 | 0 | 1.5478 | 0.53869 | 0.17078 | 0.23788 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 13.9691 | 0.5763% | CZ 7 | 0 | 0 | 0.1832 | 0.24142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.56346 | 0.5763% | CZ 7 | 30.1707 | 5.8502 | 22.1857 | 26.3874 | 0 | 17.6014 | 0 | 16.2035 | 5.6396 | 1.7879 | 2.4904 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 207.8291 | 0.5763%
CZ 8 | 0.30646 | 0.059072 | 0.20947 | 0.4072 | 0 | 0.097763 | 0 | 0.17372 | 0.06048 | 0.018885 | 0.025195 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.1476 | 0.01322% | CZ 8 | 9.8366 | 1.8961 | 19.8396 | 41.5511 | 0 | 3.138 | 0 | 5.5761 | 1.9413 | 0.60615 | 0.8087 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 120.046 | 0.01322% | CZ 8 | 2.883 | 0.55571 | 0.2065 | 0 | 0 | 0.91969 | 0 | 1.6343 | 0.56896 | 0.17765 | 0.23702 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 13.3282 | 0.01322% | CZ 8 | 0 | 0 | 0.19135 | 0.41551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.7457 | 0.01322% | CZ 8 | 30.1817 | 5.8178 | 23.0765 | 45.4154 | 0 | 9.6282 | 0 | 17.1091 | 5.9564 | 1.8599 | 2.4813 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 221.0385 | 0.01322%
US Weighted | 0.3065 | 0.059534 | 0.17873 | 0.092812 | 0 | 0.45697 | 0 | 0.16215 | 0.044232 | 0.019733 | 0.025465 | 0.23037 | 0.00795 | 0.32037 | 0 | 0.23064 | 2.1355 | 100% | US Weighted | 9.838 | 1.9109 | 16.703 | 9.4706 | 0 | 14.6676 | 0 | 5.2048 | 1.4198 | 0.63338 | 0.81736 | 7.3943 | 0.25518 | 19.7998 | 0 | 7.4031 | 95.5177 | 100% | US Weighted | 2.8834 | 0.56005 | 0.20649 | 0 | 0 | 4.2988 | 0 | 1.5254 | 0.41611 | 0.18563 | 0.23956 | 2.1671 | 0.074788 | 1.7339 | 0 | 2.1697 | 16.461 | 100% | US Weighted | 0 | 0 | 0.15998 | 0.094706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.39353 | 100% | US Weighted | 30.1859 | 5.8632 | 19.648 | 10.3513 | 0 | 45.0045 | 0 | 15.9697 | 4.3562 | 1.9434 | 2.5079 | 22.6877 | 0.78296 | 33.3268 | 0 | 22.7149 | 215.3424 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.35129 | 0.074135 | 0.15583 | 0.0013957 | 0 | 1.9501 | 0 | 0.22212 | 0 | 0.095552 | 0.025686 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 3.679 | 0% | CZ 0A | 11.2757 | 2.3796 | 14.3287 | 0.14242 | 0 | 62.5948 | 0 | 7.1296 | 0 | 3.067 | 0.82446 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 137.0297 | 0% | CZ 0A | 3.3047 | 0.69742 | 0.21146 | 0 | 0 | 18.3455 | 0 | 2.0896 | 0 | 0.89889 | 0.24163 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 32.0622 | 0% | CZ 0A | 0 | 0 | 0.13607 | 0.0014242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.27634 | 0% | CZ 0A | 34.5972 | 7.3013 | 17.0865 | 0.15567 | 0 | 192.0588 | 0 | 21.8757 | 0 | 9.4105 | 2.5297 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 365.8625 | 0%
CZ 0B | 0.35129 | 0.07415 | 0.15713 | 0.0061496 | 0 | 1.6834 | 0 | 0.22789 | 0 | 0.086969 | 0.02571 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 3.4156 | 0% | CZ 0B | 11.2757 | 2.3801 | 14.4613 | 0.62751 | 0 | 54.0339 | 0 | 7.3147 | 0 | 2.7915 | 0.82523 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 128.9972 | 0% | CZ 0B | 3.3047 | 0.69755 | 0.21144 | 0 | 0 | 15.8364 | 0 | 2.1438 | 0 | 0.81814 | 0.24186 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 29.527 | 0% | CZ 0B | 0 | 0 | 0.1374 | 0.0062751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28251 | 0% | CZ 0B | 34.5972 | 7.3027 | 17.2312 | 0.68586 | 0 | 165.7915 | 0 | 22.4435 | 0 | 8.5651 | 2.5321 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 339.9964 | 0%
CZ 1A | 0.35129 | 0.074157 | 0.16074 | 0.0028858 | 0 | 1.2171 | 0 | 0.19806 | 0 | 0.075379 | 0.025647 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.9081 | 4.246% | CZ 1A | 11.2757 | 2.3803 | 14.8295 | 0.29447 | 0 | 39.066 | 0 | 6.3573 | 0 | 2.4195 | 0.82321 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 112.7334 | 4.246% | CZ 1A | 3.3047 | 0.69762 | 0.21149 | 0 | 0 | 11.4496 | 0 | 1.8632 | 0 | 0.70911 | 0.24127 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 24.75 | 4.246% | CZ 1A | 0 | 0 | 0.14108 | 0.0029447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.28286 | 4.246% | CZ 1A | 34.5972 | 7.3034 | 17.634 | 0.32185 | 0 | 119.8658 | 0 | 19.5061 | 0 | 7.4237 | 2.5259 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 290.0251 | 4.246%
CZ 1B | 0.35129 | 0.074065 | 0.16146 | 0.030883 | 0 | 1.321 | 0 | 0.20868 | 0 | 0.072375 | 0.02564 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 3.0483 | 0% | CZ 1B | 11.2757 | 2.3773 | 14.9035 | 3.1513 | 0 | 42.4024 | 0 | 6.6983 | 0 | 2.3231 | 0.82298 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 119.242 | 0% | CZ 1B | 3.3047 | 0.69676 | 0.21146 | 0 | 0 | 12.4274 | 0 | 1.9632 | 0 | 0.68085 | 0.2412 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 25.7986 | 0% | CZ 1B | 0 | 0 | 0.14182 | 0.031513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.31217 | 0% | CZ 1B | 34.5972 | 7.2944 | 17.7148 | 3.4444 | 0 | 130.1027 | 0 | 20.5523 | 0 | 7.1279 | 2.5251 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 304.2058 | 0%
CZ 2A | 0.35129 | 0.074039 | 0.16647 | 0.043585 | 0 | 1.0763 | 0 | 0.16862 | 0 | 0.070762 | 0.025562 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.7795 | 16.73% | CZ 2A | 11.2757 | 2.3765 | 15.4144 | 4.4474 | 0 | 34.5467 | 0 | 5.4125 | 0 | 2.2713 | 0.8205 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 111.8524 | 16.73% | CZ 2A | 3.3047 | 0.69651 | 0.21151 | 0 | 0 | 10.1251 | 0 | 1.5863 | 0 | 0.66568 | 0.24047 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 23.1033 | 16.73% | CZ 2A | 0 | 0 | 0.14693 | 0.044474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.33024 | 16.73% | CZ 2A | 34.5972 | 7.2917 | 18.2734 | 4.861 | 0 | 105.9993 | 0 | 16.607 | 0 | 6.969 | 2.5175 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 277.9633 | 16.73%
CZ 2B | 0.35129 | 0.074094 | 0.16683 | 0.050132 | 0 | 0.6617 | 0 | 0.16701 | 0 | 0.049178 | 0.025354 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.3485 | 2.484% | CZ 2B | 11.2757 | 2.3783 | 15.4514 | 5.1155 | 0 | 21.2392 | 0 | 5.3607 | 0 | 1.5785 | 0.81382 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 98.5005 | 2.484% | CZ 2B | 3.3047 | 0.69703 | 0.21149 | 0 | 0 | 6.2249 | 0 | 1.5711 | 0 | 0.46263 | 0.23852 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 18.9834 | 2.484% | CZ 2B | 0 | 0 | 0.1473 | 0.051155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.33729 | 2.484% | CZ 2B | 34.5972 | 7.2972 | 18.3137 | 5.5913 | 0 | 65.168 | 0 | 16.4481 | 0 | 4.8433 | 2.497 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 235.603 | 2.484%
CZ 3A | 0.35129 | 0.07408 | 0.17642 | 0.16343 | 0 | 0.58831 | 0 | 0.15492 | 0 | 0.050924 | 0.025422 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.3877 | 13.33% | CZ 3A | 11.2757 | 2.3778 | 16.4294 | 16.677 | 0 | 18.8834 | 0 | 4.9725 | 0 | 1.6346 | 0.81599 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 108.3538 | 13.33% | CZ 3A | 3.3047 | 0.69689 | 0.21151 | 0 | 0 | 5.5344 | 0 | 1.4574 | 0 | 0.47906 | 0.23915 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 18.1961 | 13.33% | CZ 3A | 0 | 0 | 0.15708 | 0.16677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.46269 | 13.33% | CZ 3A | 34.5972 | 7.2958 | 19.3829 | 18.2279 | 0 | 57.9397 | 0 | 15.2571 | 0 | 5.0153 | 2.5037 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 241.0667 | 13.33%
CZ 3B | 0.35129 | 0.074077 | 0.17383 | 0.10588 | 0 | 0.46648 | 0 | 0.15435 | 0 | 0.041283 | 0.025359 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.1954 | 12.98% | CZ 3B | 11.2757 | 2.3777 | 16.1649 | 10.804 | 0 | 14.973 | 0 | 4.9542 | 0 | 1.3251 | 0.81398 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 97.976 | 12.98% | CZ 3B | 3.3047 | 0.69687 | 0.21149 | 0 | 0 | 4.3883 | 0 | 1.452 | 0 | 0.38837 | 0.23856 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 16.9533 | 12.98% | CZ 3B | 0 | 0 | 0.15443 | 0.10804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.40131 | 12.98% | CZ 3B | 34.5972 | 7.2955 | 19.0936 | 11.8087 | 0 | 45.9414 | 0 | 15.2009 | 0 | 4.0658 | 2.4975 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 221.3478 | 12.98%
CZ 3C | 0.35129 | 0.074065 | 0.17749 | 0.061632 | 0 | 0.32828 | 0 | 0.14685 | 0 | 0.038038 | 0.025487 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.006 | 2.16% | CZ 3C | 11.2757 | 2.3773 | 16.5382 | 6.289 | 0 | 10.5372 | 0 | 4.7136 | 0 | 1.2209 | 0.81809 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 89.0575 | 2.16% | CZ 3C | 3.3047 | 0.69676 | 0.21151 | 0 | 0 | 3.0883 | 0 | 1.3815 | 0 | 0.35783 | 0.23977 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 15.5534 | 2.16% | CZ 3C | 0 | 0 | 0.15817 | 0.06289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35989 | 2.16% | CZ 3C | 34.5972 | 7.2944 | 19.5018 | 6.8739 | 0 | 32.3312 | 0 | 14.4627 | 0 | 3.7461 | 2.5101 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 202.1646 | 2.16%
CZ 4A | 0.35129 | 0.073966 | 0.18433 | 0.30409 | 0 | 0.41344 | 0 | 0.15721 | 0 | 0.043504 | 0.025316 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.356 | 19.33% | CZ 4A | 11.2757 | 2.3742 | 17.2367 | 31.0301 | 0 | 13.2706 | 0 | 5.046 | 0 | 1.3964 | 0.81258 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 117.7296 | 19.33% | CZ 4A | 3.3047 | 0.69582 | 0.21153 | 0 | 0 | 3.8894 | 0 | 1.4789 | 0 | 0.40925 | 0.23815 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 16.5008 | 19.33% | CZ 4A | 0 | 0 | 0.16515 | 0.3103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.61429 | 19.33% | CZ 4A | 34.5972 | 7.2846 | 20.2654 | 33.9159 | 0 | 40.7181 | 0 | 15.4824 | 0 | 4.2845 | 2.4932 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 239.8884 | 19.33%
CZ 4B | 0.35129 | 0.074022 | 0.18202 | 0.18226 | 0 | 0.32046 | 0 | 0.15988 | 0 | 0.037757 | 0.025405 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.136 | 0.5625% | CZ 4B | 11.2757 | 2.3759 | 17.0015 | 18.5982 | 0 | 10.2861 | 0 | 5.1317 | 0 | 1.2119 | 0.81545 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 101.984 | 0.5625% | CZ 4B | 3.3047 | 0.69635 | 0.21142 | 0 | 0 | 3.0147 | 0 | 1.504 | 0 | 0.35519 | 0.23899 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 15.5984 | 0.5625% | CZ 4B | 0 | 0 | 0.1628 | 0.18598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.48762 | 0.5625% | CZ 4B | 34.5972 | 7.2901 | 20.0075 | 20.3279 | 0 | 31.5608 | 0 | 15.7456 | 0 | 3.7185 | 2.502 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 216.5969 | 0.5625%
CZ 4C | 0.35129 | 0.073882 | 0.18675 | 0.24615 | 0 | 0.1529 | 0 | 0.14388 | 0 | 0.029918 | 0.025374 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.013 | 3.179% | CZ 4C | 11.2757 | 2.3714 | 17.4837 | 25.1172 | 0 | 4.9078 | 0 | 4.6183 | 0 | 0.96031 | 0.81444 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 102.8362 | 3.179% | CZ 4C | 3.3047 | 0.69503 | 0.21151 | 0 | 0 | 1.4384 | 0 | 1.3535 | 0 | 0.28145 | 0.2387 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 13.7963 | 3.179% | CZ 4C | 0 | 0 | 0.16762 | 0.25117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.55763 | 3.179% | CZ 4C | 34.5972 | 7.2763 | 20.5352 | 27.453 | 0 | 15.0584 | 0 | 14.1702 | 0 | 2.9465 | 2.4989 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 205.383 | 3.179%
CZ 5A | 0.35129 | 0.073988 | 0.19109 | 0.42497 | 0 | 0.24987 | 0 | 0.15574 | 0 | 0.036923 | 0.025226 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.312 | 15.41% | CZ 5A | 11.2757 | 2.3749 | 17.9261 | 43.364 | 0 | 8.0204 | 0 | 4.999 | 0 | 1.1851 | 0.80971 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 125.2424 | 15.41% | CZ 5A | 3.3047 | 0.69603 | 0.21156 | 0 | 0 | 2.3507 | 0 | 1.4651 | 0 | 0.34734 | 0.23731 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 14.8857 | 15.41% | CZ 5A | 0 | 0 | 0.17204 | 0.43364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.74452 | 15.41% | CZ 5A | 34.5972 | 7.2867 | 21.0191 | 47.3969 | 0 | 24.609 | 0 | 15.3383 | 0 | 3.6363 | 2.4844 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 237.2151 | 15.41%
CZ 5B | 0.35129 | 0.073993 | 0.18909 | 0.30619 | 0 | 0.24649 | 0 | 0.15847 | 0 | 0.034444 | 0.025374 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.1882 | 4.56% | CZ 5B | 11.2757 | 2.375 | 17.7229 | 31.2444 | 0 | 7.9118 | 0 | 5.0864 | 0 | 1.1056 | 0.81444 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 112.8236 | 4.56% | CZ 5B | 3.3047 | 0.69608 | 0.21144 | 0 | 0 | 2.3188 | 0 | 1.4907 | 0 | 0.32402 | 0.2387 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 14.8575 | 4.56% | CZ 5B | 0 | 0 | 0.17001 | 0.31244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.6213 | 4.56% | CZ 5B | 34.5972 | 7.2872 | 20.7962 | 34.1501 | 0 | 24.2758 | 0 | 15.6065 | 0 | 3.3922 | 2.4989 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 223.4513 | 4.56%
CZ 5C | 0.35129 | 0.073877 | 0.19058 | 0.30408 | 0 | 0.097153 | 0 | 0.14183 | 0 | 0.025775 | 0.02535 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.0128 | 0.0501% | CZ 5C | 11.2757 | 2.3713 | 17.8741 | 31.0287 | 0 | 3.1184 | 0 | 4.5525 | 0 | 0.82733 | 0.81367 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 107.1491 | 0.0501% | CZ 5C | 3.3047 | 0.69498 | 0.21153 | 0 | 0 | 0.91396 | 0 | 1.3343 | 0 | 0.24248 | 0.23847 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 13.2134 | 0.0501% | CZ 5C | 0 | 0 | 0.17152 | 0.31029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.62065 | 0.0501% | CZ 5C | 34.5972 | 7.2758 | 20.9621 | 33.9143 | 0 | 9.5682 | 0 | 13.9684 | 0 | 2.5385 | 2.4966 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 206.1682 | 0.0501%
CZ 6A | 0.35129 | 0.073954 | 0.19612 | 0.56174 | 0 | 0.26294 | 0 | 0.16241 | 0 | 0.040773 | 0.02512 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.4772 | 3.403% | CZ 6A | 11.2757 | 2.3738 | 18.4387 | 57.3202 | 0 | 8.4398 | 0 | 5.213 | 0 | 1.3087 | 0.80629 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 140.4636 | 3.403% | CZ 6A | 3.3047 | 0.69571 | 0.2116 | 0 | 0 | 2.4736 | 0 | 1.5278 | 0 | 0.38357 | 0.23631 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 15.1063 | 3.403% | CZ 6A | 0 | 0 | 0.17717 | 0.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.88921 | 3.403% | CZ 6A | 34.5972 | 7.2834 | 21.5796 | 62.651 | 0 | 25.8958 | 0 | 15.995 | 0 | 4.0156 | 2.4739 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 255.3386 | 3.403%
CZ 6B | 0.35129 | 0.073901 | 0.19481 | 0.45904 | 0 | 0.17194 | 0 | 0.1515 | 0 | 0.032412 | 0.025132 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.2629 | 0.9897% | CZ 6B | 11.2757 | 2.3721 | 18.3053 | 46.8407 | 0 | 5.5189 | 0 | 4.863 | 0 | 1.0404 | 0.80668 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 126.3101 | 0.9897% | CZ 6B | 3.3047 | 0.69521 | 0.21153 | 0 | 0 | 1.6175 | 0 | 1.4253 | 0 | 0.30491 | 0.23642 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 14.0686 | 0.9897% | CZ 6B | 0 | 0 | 0.17584 | 0.46841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.78308 | 0.9897% | CZ 6B | 34.5972 | 7.2782 | 21.4334 | 51.1969 | 0 | 16.9335 | 0 | 14.921 | 0 | 3.1921 | 2.4751 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 232.8746 | 0.9897%
CZ 7 | 0.35129 | 0.073855 | 0.20209 | 0.66781 | 0 | 0.20466 | 0 | 0.16472 | 0 | 0.039554 | 0.02503 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.5319 | 0.5763% | CZ 7 | 11.2757 | 2.3706 | 19.0482 | 68.144 | 0 | 6.569 | 0 | 5.287 | 0 | 1.2696 | 0.80342 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 150.0549 | 0.5763% | CZ 7 | 3.3047 | 0.69478 | 0.21162 | 0 | 0 | 1.9253 | 0 | 1.5495 | 0 | 0.3721 | 0.23547 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 14.5665 | 0.5763% | CZ 7 | 0 | 0 | 0.18326 | 0.68144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 1.0035 | 0.5763% | CZ 7 | 34.5972 | 7.2736 | 22.2459 | 74.4814 | 0 | 20.1557 | 0 | 16.222 | 0 | 3.8955 | 2.4651 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 262.1836 | 0.5763%
CZ 8 | 0.35129 | 0.073449 | 0.21012 | 0.95239 | 0 | 0.10881 | 0 | 0.17632 | 0 | 0.037757 | 0.024946 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.738 | 0.01322% | CZ 8 | 11.2757 | 2.3575 | 19.8672 | 97.183 | 0 | 3.4927 | 0 | 5.6596 | 0 | 1.2119 | 0.8007 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 177.1358 | 0.01322% | CZ 8 | 3.3047 | 0.69096 | 0.21162 | 0 | 0 | 1.0236 | 0 | 1.6587 | 0 | 0.35519 | 0.23467 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 13.7526 | 0.01322% | CZ 8 | 0 | 0 | 0.19145 | 0.97183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 1.3021 | 0.01322% | CZ 8 | 34.5972 | 7.2336 | 23.1412 | 106.221 | 0 | 10.7166 | 0 | 17.3654 | 0 | 3.7185 | 2.4568 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 286.2974 | 0.01322%
US Weighted | 0.35129 | 0.074022 | 0.17928 | 0.2204 | 0 | 0.54241 | 0 | 0.15978 | 0 | 0.048013 | 0.025377 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.4035 | 100% | US Weighted | 11.2757 | 2.3759 | 16.7211 | 22.4896 | 0 | 17.4102 | 0 | 5.1285 | 0 | 1.5411 | 0.81453 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 113.0441 | 100% | US Weighted | 3.3047 | 0.69635 | 0.21152 | 0 | 0 | 5.1026 | 0 | 1.5031 | 0 | 0.45168 | 0.23873 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 17.7817 | 100% | US Weighted | 0 | 0 | 0.15999 | 0.2249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.52373 | 100% | US Weighted | 34.5972 | 7.2901 | 19.7017 | 24.5812 | 0 | 53.4195 | 0 | 15.7356 | 0 | 4.7286 | 2.4992 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 243.4003 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 122120 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.35129 | 0.074135 | 0.15598 | 0.048561 | 0 | 1.8735 | 0 | 0.34547 | 0.12017 | 0.11648 | 0.025405 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 3.9139 | 0% | CZ 0A | 11.2757 | 2.3796 | 14.3429 | 4.9552 | 0 | 60.1348 | 0 | 11.0888 | 3.8571 | 3.7388 | 0.81545 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 147.8758 | 0% | CZ 0A | 3.3047 | 0.69742 | 0.2116 | 0 | 0 | 17.6245 | 0 | 3.2499 | 1.1304 | 1.0958 | 0.23899 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 33.8264 | 0% | CZ 0A | 0 | 0 | 0.13621 | 0.049552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.3246 | 0% | CZ 0A | 34.5972 | 7.3013 | 17.1029 | 5.4161 | 0 | 184.511 | 0 | 34.0236 | 11.8347 | 11.4716 | 2.502 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 389.6076 | 0%
CZ 0B | 0.35129 | 0.07415 | 0.15721 | 0.069107 | 0 | 2.1694 | 0 | 0.3222 | 0.013987 | 0.10858 | 0.02547 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 4.0942 | 0% | CZ 0B | 11.2757 | 2.3801 | 14.4684 | 7.0517 | 0 | 69.6317 | 0 | 10.3418 | 0.44895 | 3.4852 | 0.81755 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 155.1886 | 0% | CZ 0B | 3.3047 | 0.69755 | 0.21156 | 0 | 0 | 20.4079 | 0 | 3.031 | 0.13158 | 1.0215 | 0.23961 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 35.3184 | 0% | CZ 0B | 0 | 0 | 0.13747 | 0.070517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.34682 | 0% | CZ 0B | 34.5972 | 7.3027 | 17.2398 | 7.7075 | 0 | 213.6501 | 0 | 31.7316 | 1.3775 | 10.6937 | 2.5085 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 407.6558 | 0%
CZ 1A | 0.35129 | 0.074157 | 0.16085 | 0.078027 | 0 | 1.3083 | 0 | 0.34251 | 0.1173 | 0.092781 | 0.025354 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 3.3535 | 4.246% | CZ 1A | 11.2757 | 2.3803 | 14.8396 | 7.962 | 0 | 41.994 | 0 | 10.9939 | 3.765 | 2.9781 | 0.81382 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 132.2898 | 4.246% | CZ 1A | 3.3047 | 0.69762 | 0.21162 | 0 | 0 | 12.3077 | 0 | 3.2221 | 1.1035 | 0.87282 | 0.23852 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 28.2316 | 4.246% | CZ 1A | 0 | 0 | 0.14118 | 0.07962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.35963 | 4.246% | CZ 1A | 34.5972 | 7.3034 | 17.6459 | 8.7025 | 0 | 128.8497 | 0 | 33.7325 | 11.5522 | 9.1375 | 2.497 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 334.8651 | 4.246%
CZ 1B | 0.35129 | 0.074065 | 0.16155 | 0.10622 | 0 | 1.6954 | 0 | 0.30575 | 0.013743 | 0.088744 | 0.025391 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 3.625 | 0% | CZ 1B | 11.2757 | 2.3773 | 14.912 | 10.8384 | 0 | 54.419 | 0 | 9.8139 | 0.44111 | 2.8485 | 0.81499 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 143.0284 | 0% | CZ 1B | 3.3047 | 0.69676 | 0.21158 | 0 | 0 | 15.9493 | 0 | 2.8763 | 0.12928 | 0.83484 | 0.23886 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 30.5146 | 0% | CZ 1B | 0 | 0 | 0.1419 | 0.10838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.38912 | 0% | CZ 1B | 34.5972 | 7.2944 | 17.7248 | 11.8464 | 0 | 166.9732 | 0 | 30.1119 | 1.3534 | 8.74 | 2.5006 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 361.989 | 0%
CZ 2A | 0.35129 | 0.074039 | 0.16655 | 0.14381 | 0 | 1.1758 | 0 | 0.30856 | 0.11614 | 0.093228 | 0.025246 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 3.2575 | 16.73% | CZ 2A | 11.2757 | 2.3765 | 15.4212 | 14.6748 | 0 | 37.7393 | 0 | 9.9043 | 3.728 | 2.9924 | 0.81033 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 134.2099 | 16.73% | CZ 2A | 3.3047 | 0.69651 | 0.21165 | 0 | 0 | 11.0608 | 0 | 2.9028 | 1.0926 | 0.87703 | 0.23749 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 26.6565 | 16.73% | CZ 2A | 0 | 0 | 0.14699 | 0.14675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.43258 | 16.73% | CZ 2A | 34.5972 | 7.2917 | 18.2818 | 16.0395 | 0 | 115.795 | 0 | 30.3891 | 11.4385 | 9.1816 | 2.4863 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 326.3481 | 16.73%
CZ 2B | 0.35129 | 0.074094 | 0.16692 | 0.15321 | 0 | 0.88863 | 0 | 0.27867 | 0.013223 | 0.063344 | 0.025108 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.8174 | 2.484% | CZ 2B | 11.2757 | 2.3783 | 15.4592 | 15.6341 | 0 | 28.5232 | 0 | 8.9447 | 0.42442 | 2.0332 | 0.8059 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 120.766 | 2.484% | CZ 2B | 3.3047 | 0.69703 | 0.21158 | 0 | 0 | 8.3597 | 0 | 2.6215 | 0.12439 | 0.59589 | 0.2362 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 22.424 | 2.484% | CZ 2B | 0 | 0 | 0.14737 | 0.15634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.44255 | 2.484% | CZ 2B | 34.5972 | 7.2972 | 18.3228 | 17.0881 | 0 | 87.5175 | 0 | 27.4448 | 1.3022 | 6.2384 | 2.4727 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 283.1281 | 2.484%
CZ 3A | 0.35129 | 0.07408 | 0.17648 | 0.19285 | 0 | 0.66378 | 0 | 0.29795 | 0.11552 | 0.064734 | 0.025093 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.7647 | 13.33% | CZ 3A | 11.2757 | 2.3778 | 16.4349 | 19.6787 | 0 | 21.306 | 0 | 9.5636 | 3.7079 | 2.0778 | 0.80544 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 122.5152 | 13.33% | CZ 3A | 3.3047 | 0.69689 | 0.21167 | 0 | 0 | 6.2444 | 0 | 2.8029 | 1.0867 | 0.60898 | 0.23606 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 21.4654 | 13.33% | CZ 3A | 0 | 0 | 0.15713 | 0.19679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.49275 | 13.33% | CZ 3A | 34.5972 | 7.2958 | 19.3899 | 21.5088 | 0 | 65.3729 | 0 | 29.3439 | 11.3768 | 6.3754 | 2.4713 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 278.5792 | 13.33%
CZ 3B | 0.35129 | 0.074077 | 0.17391 | 0.12258 | 0 | 0.52287 | 0 | 0.26371 | 0.082381 | 0.048972 | 0.025134 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.4678 | 12.98% | CZ 3B | 11.2757 | 2.3777 | 16.1732 | 12.5087 | 0 | 16.7829 | 0 | 8.4645 | 2.6442 | 1.5719 | 0.80676 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 107.893 | 12.98% | CZ 3B | 3.3047 | 0.69687 | 0.21158 | 0 | 0 | 4.9188 | 0 | 2.4808 | 0.77498 | 0.4607 | 0.23645 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 19.3579 | 12.98% | CZ 3B | 0 | 0 | 0.15451 | 0.12509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.41844 | 12.98% | CZ 3B | 34.5972 | 7.2955 | 19.1033 | 13.672 | 0 | 51.4947 | 0 | 25.9715 | 8.1133 | 4.823 | 2.4754 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 248.3931 | 12.98%
CZ 3C | 0.35129 | 0.074065 | 0.17756 | 0.21313 | 0 | 0.469 | 0 | 0.29706 | 0 | 0.051081 | 0.025183 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.4612 | 2.16% | CZ 3C | 11.2757 | 2.3773 | 16.5443 | 21.7476 | 0 | 15.0539 | 0 | 9.535 | 0 | 1.6396 | 0.80831 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 114.2691 | 2.16% | CZ 3C | 3.3047 | 0.69676 | 0.21165 | 0 | 0 | 4.4121 | 0 | 2.7945 | 0 | 0.48054 | 0.2369 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 18.4102 | 2.16% | CZ 3C | 0 | 0 | 0.15822 | 0.21748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.51454 | 2.16% | CZ 3C | 34.5972 | 7.2944 | 19.5093 | 23.7701 | 0 | 46.1898 | 0 | 29.256 | 0 | 5.0308 | 2.4801 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 248.9748 | 2.16%
CZ 4A | 0.35129 | 0.073966 | 0.1844 | 0.26726 | 0 | 0.47086 | 0 | 0.31885 | 0.1166 | 0.052994 | 0.024909 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.664 | 19.33% | CZ 4A | 11.2757 | 2.3742 | 17.2423 | 27.2716 | 0 | 15.1137 | 0 | 10.2343 | 3.7426 | 1.701 | 0.79954 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 125.0422 | 19.33% | CZ 4A | 3.3047 | 0.69582 | 0.21174 | 0 | 0 | 4.4296 | 0 | 2.9995 | 1.0969 | 0.49854 | 0.23433 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 19.7441 | 19.33% | CZ 4A | 0 | 0 | 0.1652 | 0.27272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.57675 | 19.33% | CZ 4A | 34.5972 | 7.2846 | 20.2728 | 29.8078 | 0 | 46.3732 | 0 | 31.4017 | 11.4833 | 5.2192 | 2.4532 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 269.7402 | 19.33%
CZ 4B | 0.35129 | 0.074022 | 0.18214 | 0.32232 | 0 | 0.38285 | 0 | 0.25696 | 0.013111 | 0.043146 | 0.024987 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.4537 | 0.5625% | CZ 4B | 11.2757 | 2.3759 | 17.0124 | 32.8896 | 0 | 12.2886 | 0 | 8.2477 | 0.42085 | 1.3849 | 0.80202 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 121.9851 | 0.5625% | CZ 4B | 3.3047 | 0.69635 | 0.21162 | 0 | 0 | 3.6016 | 0 | 2.4173 | 0.12334 | 0.40589 | 0.23506 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 17.2688 | 0.5625% | CZ 4B | 0 | 0 | 0.1629 | 0.3289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.63064 | 0.5625% | CZ 4B | 34.5972 | 7.2901 | 20.0208 | 35.9483 | 0 | 37.7049 | 0 | 25.3065 | 1.2913 | 4.2492 | 2.4608 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 249.7163 | 0.5625%
CZ 4C | 0.35129 | 0.073882 | 0.1868 | 0.2596 | 0 | 0.18384 | 0 | 0.29487 | 0.073746 | 0.034492 | 0.025006 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.2864 | 3.179% | CZ 4C | 11.2757 | 2.3714 | 17.4876 | 26.4894 | 0 | 5.9009 | 0 | 9.4646 | 2.3671 | 1.1071 | 0.80264 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 112.554 | 3.179% | CZ 4C | 3.3047 | 0.69503 | 0.21169 | 0 | 0 | 1.7295 | 0 | 2.7739 | 0.69375 | 0.32448 | 0.23524 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 16.2413 | 3.179% | CZ 4C | 0 | 0 | 0.16765 | 0.26489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.57139 | 3.179% | CZ 4C | 34.5972 | 7.2763 | 20.5407 | 28.953 | 0 | 18.1057 | 0 | 29.0402 | 7.2629 | 3.397 | 2.4627 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 232.4828 | 3.179%
CZ 5A | 0.35129 | 0.073988 | 0.19115 | 0.31812 | 0 | 0.30003 | 0 | 0.31863 | 0.11166 | 0.043533 | 0.024851 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.5361 | 15.41% | CZ 5A | 11.2757 | 2.3749 | 17.9312 | 32.461 | 0 | 9.6304 | 0 | 10.2274 | 3.5841 | 1.3973 | 0.79767 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 124.9669 | 15.41% | CZ 5A | 3.3047 | 0.69603 | 0.21174 | 0 | 0 | 2.8225 | 0 | 2.9975 | 1.0504 | 0.40953 | 0.23378 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 17.9992 | 15.41% | CZ 5A | 0 | 0 | 0.17209 | 0.32461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.63554 | 15.41% | CZ 5A | 34.5972 | 7.2867 | 21.0259 | 35.4798 | 0 | 29.5488 | 0 | 31.3805 | 10.9969 | 4.2873 | 2.4475 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 257.8978 | 15.41%
CZ 5B | 0.35129 | 0.073993 | 0.18926 | 0.48636 | 0 | 0.28349 | 0 | 0.25911 | 0.013639 | 0.038754 | 0.024859 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.5236 | 4.56% | CZ 5B | 11.2757 | 2.375 | 17.7381 | 49.6281 | 0 | 9.0993 | 0 | 8.3168 | 0.43777 | 1.2439 | 0.79791 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 136.1999 | 4.56% | CZ 5B | 3.3047 | 0.69608 | 0.21167 | 0 | 0 | 2.6669 | 0 | 2.4375 | 0.1283 | 0.36457 | 0.23385 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 16.3165 | 4.56% | CZ 5B | 0 | 0 | 0.17016 | 0.49628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.80528 | 4.56% | CZ 5B | 34.5972 | 7.2872 | 20.8143 | 54.2435 | 0 | 27.9193 | 0 | 25.5182 | 1.3432 | 3.8167 | 2.4482 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 258.8349 | 4.56%
CZ 5C | 0.35129 | 0.073877 | 0.19063 | 0.27108 | 0 | 0.11159 | 0 | 0.29867 | 0.085892 | 0.028029 | 0.024975 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.2389 | 0.0501% | CZ 5C | 11.2757 | 2.3713 | 17.8781 | 27.6615 | 0 | 3.5817 | 0 | 9.5866 | 2.757 | 0.89968 | 0.80163 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 112.1005 | 0.0501% | CZ 5C | 3.3047 | 0.69498 | 0.21171 | 0 | 0 | 1.0497 | 0 | 2.8097 | 0.80802 | 0.26368 | 0.23494 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 15.6505 | 0.0501% | CZ 5C | 0 | 0 | 0.17156 | 0.27661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.58701 | 0.0501% | CZ 5C | 34.5972 | 7.2758 | 20.9676 | 30.234 | 0 | 10.9898 | 0 | 29.4144 | 8.4591 | 2.7605 | 2.4596 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 228.0052 | 0.0501%
CZ 6A | 0.35129 | 0.073954 | 0.19619 | 0.3914 | 0 | 0.31234 | 0 | 0.31884 | 0.11223 | 0.047402 | 0.024738 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.6313 | 3.403% | CZ 6A | 11.2757 | 2.3738 | 18.4447 | 39.9383 | 0 | 10.0255 | 0 | 10.2341 | 3.6022 | 1.5215 | 0.79402 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 133.4973 | 3.403% | CZ 6A | 3.3047 | 0.69571 | 0.21178 | 0 | 0 | 2.9383 | 0 | 2.9995 | 1.0558 | 0.44593 | 0.23272 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 18.1574 | 3.403% | CZ 6A | 0 | 0 | 0.17722 | 0.39938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.71544 | 3.403% | CZ 6A | 34.5972 | 7.2834 | 21.5874 | 43.6526 | 0 | 30.7612 | 0 | 31.4012 | 11.0527 | 4.6685 | 2.4363 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 268.2876 | 3.403%
CZ 6B | 0.35129 | 0.073901 | 0.19489 | 0.31269 | 0 | 0.18708 | 0 | 0.27721 | 0.11242 | 0.03305 | 0.02481 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.3702 | 0.9897% | CZ 6B | 11.2757 | 2.3721 | 18.3126 | 31.9076 | 0 | 6.0048 | 0 | 8.898 | 3.6086 | 1.0608 | 0.79635 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 119.5239 | 0.9897% | CZ 6B | 3.3047 | 0.69521 | 0.21169 | 0 | 0 | 1.7599 | 0 | 2.6079 | 1.0576 | 0.31092 | 0.2334 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 16.4543 | 0.9897% | CZ 6B | 0 | 0 | 0.1759 | 0.31908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.63382 | 0.9897% | CZ 6B | 34.5972 | 7.2782 | 21.4424 | 34.875 | 0 | 18.4244 | 0 | 27.3016 | 11.0722 | 3.255 | 2.4434 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 241.5365 | 0.9897%
CZ 7 | 0.35129 | 0.073855 | 0.20216 | 0.49396 | 0 | 0.24086 | 0 | 0.30518 | 0.11654 | 0.042781 | 0.024648 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.6542 | 0.5763% | CZ 7 | 11.2757 | 2.3706 | 19.0536 | 50.4039 | 0 | 7.7312 | 0 | 9.7957 | 3.7406 | 1.3732 | 0.79115 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 141.823 | 0.5763% | CZ 7 | 3.3047 | 0.69478 | 0.21181 | 0 | 0 | 2.2659 | 0 | 2.871 | 1.0963 | 0.40245 | 0.23187 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 17.3518 | 0.5763% | CZ 7 | 0 | 0 | 0.18331 | 0.50404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.82619 | 0.5763% | CZ 7 | 34.5972 | 7.2736 | 22.2531 | 55.0915 | 0 | 23.7215 | 0 | 30.0561 | 11.4771 | 4.2133 | 2.4275 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 271.958 | 0.5763%
CZ 8 | 0.35129 | 0.073449 | 0.21021 | 0.68771 | 0 | 0.12108 | 0 | 0.31435 | 0.11682 | 0.036105 | 0.024467 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.7384 | 0.01322% | CZ 8 | 11.2757 | 2.3575 | 19.8746 | 70.1748 | 0 | 3.8864 | 0 | 10.09 | 3.7496 | 1.1589 | 0.78533 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 158.6402 | 0.01322% | CZ 8 | 3.3047 | 0.69096 | 0.21185 | 0 | 0 | 1.139 | 0 | 2.9572 | 1.0989 | 0.33965 | 0.23017 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 16.2455 | 0.01322% | CZ 8 | 0 | 0 | 0.19152 | 0.70175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 1.0321 | 0.01322% | CZ 8 | 34.5972 | 7.2336 | 23.1508 | 76.701 | 0 | 11.9245 | 0 | 30.9592 | 11.5048 | 3.5558 | 2.4096 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 282.8836 | 0.01322%
US Weighted | 0.35129 | 0.074022 | 0.17936 | 0.22982 | 0 | 0.61287 | 0 | 0.30235 | 0.099276 | 0.059459 | 0.025033 | 0.23658 | 0.013847 | 0.32037 | 0 | 0.23208 | 2.7364 | 100% | US Weighted | 11.2757 | 2.3759 | 16.7279 | 23.4507 | 0 | 19.672 | 0 | 9.7049 | 3.1865 | 1.9085 | 0.8035 | 7.5938 | 0.44445 | 19.7998 | 0 | 7.4494 | 124.393 | 100% | US Weighted | 3.3047 | 0.69635 | 0.21168 | 0 | 0 | 5.7655 | 0 | 2.8444 | 0.93392 | 0.55935 | 0.23549 | 2.2256 | 0.13026 | 1.7339 | 0 | 2.1833 | 20.8244 | 100% | US Weighted | 0 | 0 | 0.16006 | 0.23451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13884 | 0 | 0 | 0.5334 | 100% | US Weighted | 34.5972 | 7.2901 | 19.7102 | 25.6316 | 0 | 60.3592 | 0 | 29.7775 | 9.7772 | 5.8559 | 2.4654 | 23.2999 | 1.3637 | 33.3268 | 0 | 22.8568 | 276.3114 | 100%
Building Type: | Large Hotel |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Large Hotel |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 122120 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 122120 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 122120 | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.22393 | 0.02986 | 0.0010403 | 0.048555 | 0 | 0.78223 | 0 | 0.15248 | 0.085888 | 0.093809 | 0.010376 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.4645 | 0% | CZ 0A | 7.1878 | 0.95845 | 0.065045 | 4.9546 | 0 | 25.108 | 0 | 4.8942 | 2.7568 | 3.0111 | 0.33304 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 50.4357 | 0% | CZ 0A | 2.1066 | 0.28091 | 0.0055289 | 0 | 0 | 7.3587 | 0 | 1.4344 | 0.80797 | 0.88249 | 0.097609 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 13.3162 | 0% | CZ 0A | 0 | 0 | 0.0004618 | 0.049546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050008 | 0% | CZ 0A | 22.0541 | 2.9408 | 0.10836 | 5.4154 | 0 | 77.0384 | 0 | 15.0168 | 8.4587 | 9.2388 | 1.0219 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 144.8733 | 0%
CZ 0B | 0.22391 | 0.029868 | 0.0023959 | 0.068936 | 0 | 1.2382 | 0 | 0.13696 | -0.018413 | 0.087919 | 0.010572 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.8167 | 0% | CZ 0B | 7.1869 | 0.95868 | 0.20405 | 7.0343 | 0 | 39.7437 | 0 | 4.3962 | -0.59102 | 2.822 | 0.33933 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 63.2609 | 0% | CZ 0B | 2.1064 | 0.28097 | 0.0054379 | 0 | 0 | 11.6482 | 0 | 1.2884 | -0.17322 | 0.82709 | 0.099452 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 16.4247 | 0% | CZ 0B | 0 | 0 | 0.001855 | 0.070343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072198 | 0% | CZ 0B | 22.0515 | 2.9415 | 0.25968 | 7.6885 | 0 | 121.9451 | 0 | 13.4887 | -1.8134 | 8.6588 | 1.0412 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 179.8415 | 0%
CZ 1A | 0.22376 | 0.02987 | 0.00096817 | 0.078008 | 0 | 0.5983 | 0 | 0.16719 | 0.084802 | 0.076097 | 0.010344 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.3057 | 4.246% | CZ 1A | 7.1821 | 0.95876 | 0.057516 | 7.96 | 0 | 19.2042 | 0 | 5.3664 | 2.7219 | 2.4425 | 0.33203 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 47.3923 | 4.246% | CZ 1A | 2.1049 | 0.281 | 0.0055517 | 0 | 0 | 5.6284 | 0 | 1.5728 | 0.79776 | 0.71587 | 0.097314 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 11.5457 | 4.246% | CZ 1A | 0 | 0 | 0.00038574 | 0.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079985 | 4.246% | CZ 1A | 22.0367 | 2.9418 | 0.10028 | 8.7002 | 0 | 58.9241 | 0 | 16.4657 | 8.3517 | 7.4944 | 1.0188 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 129.6139 | 4.246%
CZ 1B | 0.2238 | 0.029834 | 0.0014422 | 0.10199 | 0 | 0.96063 | 0 | 0.12676 | -0.018887 | 0.070624 | 0.01049 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.543 | 0% | CZ 1B | 7.1835 | 0.9576 | 0.10657 | 10.4068 | 0 | 30.8342 | 0 | 4.0688 | -0.60623 | 2.2669 | 0.33669 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 56.7216 | 0% | CZ 1B | 2.1054 | 0.28066 | 0.0054607 | 0 | 0 | 9.037 | 0 | 1.1925 | -0.17768 | 0.66438 | 0.098679 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 13.5483 | 0% | CZ 1B | 0 | 0 | 0.00087936 | 0.10407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10495 | 0% | CZ 1B | 22.041 | 2.9382 | 0.15328 | 11.3747 | 0 | 94.6082 | 0 | 12.4842 | -1.8601 | 6.9554 | 1.0331 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 153.308 | 0%
CZ 2A | 0.22395 | 0.029822 | 0.00086258 | 0.14073 | 0 | 0.57748 | 0 | 0.14009 | 0.090118 | 0.076271 | 0.010211 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.3259 | 16.73% | CZ 2A | 7.1884 | 0.95721 | 0.046573 | 14.3605 | 0 | 18.5358 | 0 | 4.4965 | 2.8926 | 2.4481 | 0.32776 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 52.4204 | 16.73% | CZ 2A | 2.1068 | 0.28054 | 0.0055744 | 0 | 0 | 5.4325 | 0 | 1.3179 | 0.84777 | 0.71751 | 0.096062 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 11.1466 | 16.73% | CZ 2A | 0 | 0 | 0.00027553 | 0.14361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14388 | 16.73% | CZ 2A | 22.056 | 2.937 | 0.088474 | 15.6961 | 0 | 56.8733 | 0 | 13.7967 | 8.8753 | 7.5116 | 1.0057 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 132.4202 | 16.73%
CZ 2B | 0.22392 | 0.029846 | 0.00086051 | 0.14981 | 0 | 0.48358 | 0 | 0.094225 | -0.0093165 | 0.050965 | 0.010211 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0705 | 2.484% | CZ 2B | 7.1873 | 0.95798 | 0.047038 | 15.2867 | 0 | 15.5219 | 0 | 3.0244 | -0.29904 | 1.6359 | 0.32776 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 44.8567 | 2.484% | CZ 2B | 2.1065 | 0.28077 | 0.0054834 | 0 | 0 | 4.5492 | 0 | 0.8864 | -0.087644 | 0.47945 | 0.096062 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 8.6582 | 2.484% | CZ 2B | 0 | 0 | 0.00028329 | 0.15287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15315 | 2.484% | CZ 2B | 22.0527 | 2.9394 | 0.088369 | 16.7084 | 0 | 47.6257 | 0 | 9.2797 | -0.91754 | 5.0193 | 1.0057 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 107.3818 | 2.484%
CZ 3A | 0.22392 | 0.029838 | 0.00087931 | 0.17697 | 0 | 0.32781 | 0 | 0.13813 | 0.091378 | 0.051108 | 0.010112 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0865 | 13.33% | CZ 3A | 7.1874 | 0.95775 | 0.04828 | 18.0581 | 0 | 10.5219 | 0 | 4.4338 | 2.933 | 1.6405 | 0.32458 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 47.2722 | 13.33% | CZ 3A | 2.1065 | 0.2807 | 0.0055744 | 0 | 0 | 3.0838 | 0 | 1.2995 | 0.85962 | 0.48079 | 0.095129 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 8.5536 | 13.33% | CZ 3A | 0 | 0 | 0.0002926 | 0.18058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18087 | 13.33% | CZ 3A | 22.0531 | 2.9387 | 0.09034 | 19.7375 | 0 | 32.2842 | 0 | 13.6042 | 8.9994 | 5.0334 | 0.99591 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 109.3169 | 13.33%
CZ 3B | 0.22391 | 0.029838 | 0.00090642 | 0.11501 | 0 | 0.23073 | 0 | 0.071847 | 0.060224 | 0.037658 | 0.010054 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 0.81652 | 12.98% | CZ 3B | 7.1869 | 0.95775 | 0.051385 | 11.7354 | 0 | 7.406 | 0 | 2.3061 | 1.933 | 1.2087 | 0.32272 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 34.2749 | 12.98% | CZ 3B | 2.1064 | 0.2807 | 0.0055289 | 0 | 0 | 2.1706 | 0 | 0.67589 | 0.56654 | 0.35426 | 0.094583 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 6.5964 | 12.98% | CZ 3B | 0 | 0 | 0.0003252 | 0.11735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11768 | 12.98% | CZ 3B | 22.0515 | 2.9387 | 0.093427 | 12.8268 | 0 | 22.7237 | 0 | 7.0759 | 5.9311 | 3.7088 | 0.99019 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 81.9202 | 12.98%
CZ 3C | 0.22386 | 0.029834 | 0.00069138 | 0.16318 | 0 | 0.27454 | 0 | 0.14785 | 0 | 0.040587 | 0.010444 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 0.92734 | 2.16% | CZ 3C | 7.1855 | 0.9576 | 0.030119 | 16.6513 | 0 | 8.8122 | 0 | 4.7456 | 0 | 1.3027 | 0.33522 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 41.1871 | 2.16% | CZ 3C | 2.1059 | 0.28066 | 0.0054379 | 0 | 0 | 2.5827 | 0 | 1.3909 | 0 | 0.38181 | 0.098246 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 7.1876 | 2.16% | CZ 3C | 0 | 0 | 0.00011564 | 0.16651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16663 | 2.16% | CZ 3C | 22.0472 | 2.9382 | 0.069569 | 18.1999 | 0 | 27.0384 | 0 | 14.5608 | 0 | 3.9972 | 1.0285 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 93.4599 | 2.16%
CZ 4A | 0.22401 | 0.029793 | 0.0010192 | 0.24096 | 0 | 0.23853 | 0 | 0.15731 | 0.090701 | 0.040304 | 0.0098172 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0688 | 19.33% | CZ 4A | 7.1903 | 0.95628 | 0.061708 | 24.5881 | 0 | 7.6562 | 0 | 5.0494 | 2.9113 | 1.2937 | 0.31511 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 51.1889 | 19.33% | CZ 4A | 2.1074 | 0.28027 | 0.0056882 | 0 | 0 | 2.2439 | 0 | 1.4799 | 0.85325 | 0.37915 | 0.092353 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 7.7839 | 19.33% | CZ 4A | 0 | 0 | 0.00042299 | 0.24588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2463 | 19.33% | CZ 4A | 22.062 | 2.9341 | 0.10578 | 26.8748 | 0 | 23.4914 | 0 | 15.4932 | 8.9327 | 3.9693 | 0.96685 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 108.4102 | 19.33%
CZ 4B | 0.22406 | 0.029814 | 0.00097605 | 0.3113 | 0 | 0.1803 | 0 | 0.048953 | -0.0099478 | 0.031604 | 0.0099067 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 0.86332 | 0.5625% | CZ 4B | 7.1919 | 0.95697 | 0.057982 | 31.7652 | 0 | 5.7871 | 0 | 1.5713 | -0.3193 | 1.0144 | 0.31798 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 49.5104 | 0.5625% | CZ 4B | 2.1078 | 0.28047 | 0.0055972 | 0 | 0 | 1.6961 | 0 | 0.46052 | -0.093582 | 0.29731 | 0.093195 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 5.1894 | 0.5625% | CZ 4B | 0 | 0 | 0.00038884 | 0.31765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31804 | 0.5625% | CZ 4B | 22.067 | 2.9363 | 0.1011 | 34.7194 | 0 | 17.7565 | 0 | 4.8211 | -0.97971 | 3.1125 | 0.97566 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 89.09 | 0.5625%
CZ 4C | 0.22397 | 0.029759 | 0.0010516 | 0.2407 | 0 | 0.1019 | 0 | 0.1388 | 0.047748 | 0.025371 | 0.0099018 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 0.85555 | 3.179% | CZ 4C | 7.1888 | 0.95519 | 0.065355 | 24.5613 | 0 | 3.2709 | 0 | 4.4551 | 1.5326 | 0.81436 | 0.31783 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 44.3283 | 3.179% | CZ 4C | 2.1069 | 0.27995 | 0.0056427 | 0 | 0 | 0.95864 | 0 | 1.3057 | 0.44918 | 0.23868 | 0.09315 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 5.7799 | 3.179% | CZ 4C | 0 | 0 | 0.00046102 | 0.24561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24607 | 3.179% | CZ 4C | 22.0574 | 2.9308 | 0.10946 | 26.8455 | 0 | 10.036 | 0 | 13.6695 | 4.7025 | 2.4987 | 0.97519 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 87.4052 | 3.179%
CZ 5A | 0.2241 | 0.0298 | 0.0011042 | 0.27272 | 0 | 0.15476 | 0 | 0.16023 | 0.087201 | 0.031563 | 0.0098196 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0076 | 15.41% | CZ 5A | 7.1931 | 0.95651 | 0.070555 | 27.8281 | 0 | 4.9673 | 0 | 5.143 | 2.799 | 1.0131 | 0.31519 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 51.4527 | 15.41% | CZ 5A | 2.1082 | 0.28034 | 0.0056654 | 0 | 0 | 1.4558 | 0 | 1.5073 | 0.82033 | 0.29692 | 0.092376 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 6.9089 | 15.41% | CZ 5A | 0 | 0 | 0.00051225 | 0.27828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27879 | 15.41% | CZ 5A | 22.0705 | 2.9348 | 0.1153 | 30.4161 | 0 | 15.2411 | 0 | 15.7802 | 8.588 | 3.1085 | 0.96709 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 102.8018 | 15.41%
CZ 5B | 0.22407 | 0.029805 | 0.0010971 | 0.45841 | 0 | 0.12846 | 0 | 0.056782 | -0.011368 | 0.027696 | 0.0098559 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 0.96115 | 4.56% | CZ 5B | 7.1921 | 0.95666 | 0.070167 | 46.7767 | 0 | 4.1231 | 0 | 1.8226 | -0.36487 | 0.88897 | 0.31635 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 62.9486 | 4.56% | CZ 5B | 2.1079 | 0.28038 | 0.0056199 | 0 | 0 | 1.2084 | 0 | 0.53417 | -0.10694 | 0.26054 | 0.092717 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 4.7248 | 4.56% | CZ 5B | 0 | 0 | 0.00050992 | 0.46777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46828 | 4.56% | CZ 5B | 22.0674 | 2.9353 | 0.11457 | 51.1269 | 0 | 12.651 | 0 | 5.5922 | -1.1195 | 2.7276 | 0.97066 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 100.6463 | 4.56%
CZ 5C | 0.22403 | 0.029756 | 0.0011515 | 0.25138 | 0 | 0.055198 | 0 | 0.14249 | 0.056586 | 0.016328 | 0.0098655 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 0.82314 | 0.0501% | CZ 5C | 7.1909 | 0.95511 | 0.075212 | 25.6514 | 0 | 1.7717 | 0 | 4.5736 | 1.8163 | 0.5241 | 0.31666 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 44.0417 | 0.0501% | CZ 5C | 2.1075 | 0.27993 | 0.0056882 | 0 | 0 | 0.51926 | 0 | 1.3404 | 0.53232 | 0.1536 | 0.092808 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 5.3735 | 0.0501% | CZ 5C | 0 | 0 | 0.00055804 | 0.25651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25707 | 0.0501% | CZ 5C | 22.0636 | 2.9306 | 0.12054 | 28.0369 | 0 | 5.4362 | 0 | 14.033 | 5.5729 | 1.6081 | 0.97161 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 84.3535 | 0.0501%
CZ 6A | 0.22409 | 0.029788 | 0.0011952 | 0.30676 | 0 | 0.16317 | 0 | 0.15819 | 0.086473 | 0.038473 | 0.0096962 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0542 | 3.403% | CZ 6A | 7.1928 | 0.95612 | 0.079326 | 31.3016 | 0 | 5.2373 | 0 | 5.0775 | 2.7756 | 1.2349 | 0.31123 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 55.3331 | 3.403% | CZ 6A | 2.1081 | 0.28022 | 0.0057337 | 0 | 0 | 1.535 | 0 | 1.4881 | 0.81348 | 0.36193 | 0.091216 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 7.0257 | 3.403% | CZ 6A | 0 | 0 | 0.00059762 | 0.31302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31361 | 3.403% | CZ 6A | 22.0696 | 2.9337 | 0.12535 | 34.2126 | 0 | 16.0696 | 0 | 15.5791 | 8.5163 | 3.789 | 0.95494 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 107.8303 | 3.403%
CZ 6B | 0.22414 | 0.029766 | 0.0011809 | 0.25115 | 0 | 0.082238 | 0 | 0.096532 | 0.085312 | 0.025487 | 0.0097906 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 0.84194 | 0.9897% | CZ 6B | 7.1944 | 0.95542 | 0.07855 | 25.6274 | 0 | 2.6397 | 0 | 3.0985 | 2.7383 | 0.81809 | 0.31426 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 44.6313 | 0.9897% | CZ 6B | 2.1085 | 0.28002 | 0.0056427 | 0 | 0 | 0.77364 | 0 | 0.90811 | 0.80256 | 0.23977 | 0.092103 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 5.5524 | 0.9897% | CZ 6B | 0 | 0 | 0.00059297 | 0.25627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25687 | 0.9897% | CZ 6B | 22.0743 | 2.9315 | 0.12388 | 28.0107 | 0 | 8.0992 | 0 | 9.507 | 8.402 | 2.5101 | 0.96423 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 86.2032 | 0.9897%
CZ 7 | 0.22414 | 0.029747 | 0.0012994 | 0.37402 | 0 | 0.12264 | 0 | 0.14811 | 0.089786 | 0.030172 | 0.0096527 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0659 | 0.5763% | CZ 7 | 7.1945 | 0.9548 | 0.089959 | 38.1657 | 0 | 3.9364 | 0 | 4.7539 | 2.8819 | 0.96846 | 0.30983 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 60.4224 | 0.5763% | CZ 7 | 2.1086 | 0.27984 | 0.0057337 | 0 | 0 | 1.1537 | 0 | 1.3933 | 0.84465 | 0.28384 | 0.090806 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 6.5024 | 0.5763% | CZ 7 | 0 | 0 | 0.00070396 | 0.38166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38236 | 0.5763% | CZ 7 | 22.0748 | 2.9296 | 0.13697 | 41.7151 | 0 | 12.0781 | 0 | 14.5863 | 8.8426 | 2.9715 | 0.95065 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 109.8659 | 0.5763%
CZ 8 | 0.22403 | 0.029585 | 0.0013841 | 0.49332 | 0 | 0.05217 | 0 | 0.16569 | 0.087856 | 0.025502 | 0.0095076 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.1254 | 0.01322% | CZ 8 | 7.1909 | 0.9496 | 0.098264 | 50.3386 | 0 | 1.6745 | 0 | 5.3181 | 2.82 | 0.81856 | 0.30517 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 70.6805 | 0.01322% | CZ 8 | 2.1075 | 0.27831 | 0.0057792 | 0 | 0 | 0.49078 | 0 | 1.5587 | 0.82649 | 0.23991 | 0.089441 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 5.9389 | 0.01322% | CZ 8 | 0 | 0 | 0.00078545 | 0.50339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50417 | 0.01322% | CZ 8 | 22.0636 | 2.9136 | 0.14635 | 55.0201 | 0 | 5.1379 | 0 | 16.3176 | 8.6526 | 2.5116 | 0.93636 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 117.2798 | 0.01322%
US Weighted | 0.22398 | 0.029815 | 0.0009733 | 0.2068 | 0 | 0.30075 | 0 | 0.13347 | 0.0747 | 0.04648 | 0.0099989 | 0.0067044 | 0.0086441 | 0 | 0 | 0.021003 | 1.0633 | 100% | US Weighted | 7.1893 | 0.957 | 0.057607 | 21.1023 | 0 | 9.6535 | 0 | 4.2841 | 2.3977 | 1.4919 | 0.32094 | 0.2152 | 0.27746 | 0 | 0 | 0.67416 | 48.6211 | 100% | US Weighted | 2.1071 | 0.28048 | 0.0056098 | 0 | 0 | 2.8293 | 0 | 1.2556 | 0.70272 | 0.43725 | 0.094063 | 0.063071 | 0.081318 | 0 | 0 | 0.19758 | 8.054 | 100% | US Weighted | 0 | 0 | 0.00038467 | 0.21102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21141 | 100% | US Weighted | 22.0587 | 2.9363 | 0.10077 | 23.0648 | 0 | 29.6198 | 0 | 13.1448 | 7.3568 | 4.5776 | 0.98475 | 0.66029 | 0.85132 | 0 | 0 | 2.0685 | 107.4246 | 100%
Building Type: | Large Hotel |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Large Hotel |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Large Hotel |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Large Hotel |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 122120 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 122120 | [17 empty] | Prototype Floor Area: | 122120 | Building Type: | Large Hotel | [15 empty] | Prototype Floor Area: | 122120 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 63.75% | 40.28% | 0.6669% | 99.99% |  | 41.75% |  | 44.14% | 71.47% | 80.54% | 40.84% | 2.834% | 62.43% | 0% |  | 9.05% | 37.42% | 0% | CZ 0A | 63.75% | 40.28% | 0.4535% | 99.99% |  | 41.75% |  | 44.14% | 71.47% | 80.54% | 40.84% | 2.834% | 62.43% | 0% |  | 9.05% | 34.11% | 0% | CZ 0A | 63.75% | 40.28% | 2.613% |  |  | 41.75% |  | 44.14% | 71.47% | 80.54% | 40.84% | 2.834% | 62.43% | 0% |  | 9.05% | 39.37% | 0% | CZ 0A |  |  | 0.339% | 99.99% | [9 empty] | 0% |  |  | 15.41% | 0% | CZ 0A | 63.75% | 40.28% | 0.6336% | 99.99% |  | 41.75% |  | 44.14% | 71.47% | 80.54% | 40.84% | 2.834% | 62.43% | 0% |  | 9.05% | 37.18% | 0%
CZ 0B | 63.74% | 40.28% | 1.524% | 99.75% |  | 57.08% |  | 42.51% | -131.6% | 80.97% | 41.51% | 2.834% | 62.43% | 0% |  | 9.05% | 44.37% | 0% | CZ 0B | 63.74% | 40.28% | 1.41% | 99.75% |  | 57.08% |  | 42.51% | -131.6% | 80.97% | 41.51% | 2.834% | 62.43% | 0% |  | 9.05% | 40.76% | 0% | CZ 0B | 63.74% | 40.28% | 2.57% |  |  | 57.08% |  | 42.51% | -131.6% | 80.97% | 41.51% | 2.834% | 62.43% | 0% |  | 9.05% | 46.5% | 0% | CZ 0B |  |  | 1.349% | 99.75% | [9 empty] | 0% |  |  | 20.82% | 0% | CZ 0B | 63.74% | 40.28% | 1.506% | 99.75% |  | 57.08% |  | 42.51% | -131.6% | 80.97% | 41.51% | 2.834% | 62.43% | 0% |  | 9.05% | 44.12% | 0%
CZ 1A | 63.7% | 40.28% | 0.6019% | 99.97% |  | 45.73% |  | 48.81% | 72.3% | 82.02% | 40.8% | 2.834% | 62.43% | 0% |  | 9.05% | 38.94% | 4.246% | CZ 1A | 63.7% | 40.28% | 0.3876% | 99.97% |  | 45.73% |  | 48.81% | 72.3% | 82.02% | 40.8% | 2.834% | 62.43% | 0% |  | 9.05% | 35.82% | 4.246% | CZ 1A | 63.7% | 40.28% | 2.623% |  |  | 45.73% |  | 48.81% | 72.3% | 82.02% | 40.8% | 2.834% | 62.43% | 0% |  | 9.05% | 40.9% | 4.246% | CZ 1A |  |  | 0.2732% | 99.97% | [9 empty] | 0% |  |  | 22.24% | 4.246% | CZ 1A | 63.7% | 40.28% | 0.5683% | 99.97% |  | 45.73% |  | 48.81% | 72.3% | 82.02% | 40.8% | 2.834% | 62.43% | 0% |  | 9.05% | 38.71% | 4.246%
CZ 1B | 63.71% | 40.28% | 0.8927% | 96.02% |  | 56.66% |  | 41.46% | -137.4% | 79.58% | 41.31% | 2.834% | 62.43% | 0% |  | 9.05% | 42.57% | 0% | CZ 1B | 63.71% | 40.28% | 0.7146% | 96.02% |  | 56.66% |  | 41.46% | -137.4% | 79.58% | 41.31% | 2.834% | 62.43% | 0% |  | 9.05% | 39.66% | 0% | CZ 1B | 63.71% | 40.28% | 2.581% |  |  | 56.66% |  | 41.46% | -137.4% | 79.58% | 41.31% | 2.834% | 62.43% | 0% |  | 9.05% | 44.4% | 0% | CZ 1B |  |  | 0.6197% | 96.02% | [9 empty] | 0% |  |  | 26.97% | 0% | CZ 1B | 63.71% | 40.28% | 0.8648% | 96.02% |  | 56.66% |  | 41.46% | -137.4% | 79.58% | 41.31% | 2.834% | 62.43% | 0% |  | 9.05% | 42.35% | 0%
CZ 2A | 63.75% | 40.28% | 0.5179% | 97.86% |  | 49.12% |  | 45.4% | 77.59% | 81.81% | 40.45% | 2.834% | 62.43% | 0% |  | 9.05% | 40.7% | 16.73% | CZ 2A | 63.75% | 40.28% | 0.302% | 97.86% |  | 49.12% |  | 45.4% | 77.59% | 81.81% | 40.45% | 2.834% | 62.43% | 0% |  | 9.05% | 39.06% | 16.73% | CZ 2A | 63.75% | 40.28% | 2.634% |  |  | 49.12% |  | 45.4% | 77.59% | 81.81% | 40.45% | 2.834% | 62.43% | 0% |  | 9.05% | 41.82% | 16.73% | CZ 2A |  |  | 0.1874% | 97.86% | [9 empty] | 0% |  |  | 33.26% | 16.73% | CZ 2A | 63.75% | 40.28% | 0.4839% | 97.86% |  | 49.12% |  | 45.4% | 77.59% | 81.81% | 40.45% | 2.834% | 62.43% | 0% |  | 9.05% | 40.58% | 16.73%
CZ 2B | 63.74% | 40.28% | 0.5155% | 97.78% |  | 54.42% |  | 33.81% | -70.46% | 80.46% | 40.67% | 2.834% | 62.43% | 0% |  | 9.05% | 37.99% | 2.484% | CZ 2B | 63.74% | 40.28% | 0.3043% | 97.78% |  | 54.42% |  | 33.81% | -70.46% | 80.46% | 40.67% | 2.834% | 62.43% | 0% |  | 9.05% | 37.14% | 2.484% | CZ 2B | 63.74% | 40.28% | 2.592% |  |  | 54.42% |  | 33.81% | -70.46% | 80.46% | 40.67% | 2.834% | 62.43% | 0% |  | 9.05% | 38.61% | 2.484% | CZ 2B |  |  | 0.1922% | 97.78% | [9 empty] | 0% |  |  | 34.61% | 2.484% | CZ 2B | 63.74% | 40.28% | 0.4823% | 97.78% |  | 54.42% |  | 33.81% | -70.46% | 80.46% | 40.67% | 2.834% | 62.43% | 0% |  | 9.05% | 37.93% | 2.484%
CZ 3A | 63.74% | 40.28% | 0.4982% | 91.76% |  | 49.38% |  | 46.36% | 79.1% | 78.95% | 40.3% | 2.834% | 62.43% | 0% |  | 9.05% | 39.3% | 13.33% | CZ 3A | 63.74% | 40.28% | 0.2938% | 91.76% |  | 49.38% |  | 46.36% | 79.1% | 78.95% | 40.3% | 2.834% | 62.43% | 0% |  | 9.05% | 38.58% | 13.33% | CZ 3A | 63.74% | 40.28% | 2.634% |  |  | 49.38% |  | 46.36% | 79.1% | 78.95% | 40.3% | 2.834% | 62.43% | 0% |  | 9.05% | 39.85% | 13.33% | CZ 3A |  |  | 0.1862% | 91.76% | [9 empty] | 0% |  |  | 36.71% | 13.33% | CZ 3A | 63.74% | 40.28% | 0.4659% | 91.76% |  | 49.38% |  | 46.36% | 79.1% | 78.95% | 40.3% | 2.834% | 62.43% | 0% |  | 9.05% | 39.24% | 13.33%
CZ 3B | 63.74% | 40.28% | 0.5212% | 93.82% |  | 44.13% |  | 27.24% | 73.1% | 76.9% | 40% | 2.834% | 62.43% | 0% |  | 9.05% | 33.09% | 12.98% | CZ 3B | 63.74% | 40.28% | 0.3177% | 93.82% |  | 44.13% |  | 27.24% | 73.1% | 76.9% | 40% | 2.834% | 62.43% | 0% |  | 9.05% | 31.77% | 12.98% | CZ 3B | 63.74% | 40.28% | 2.613% |  |  | 44.13% |  | 27.24% | 73.1% | 76.9% | 40% | 2.834% | 62.43% | 0% |  | 9.05% | 34.08% | 12.98% | CZ 3B |  |  | 0.2105% | 93.82% | [9 empty] | 0% |  |  | 28.12% | 12.98% | CZ 3B | 63.74% | 40.28% | 0.4891% | 93.82% |  | 44.13% |  | 27.24% | 73.1% | 76.9% | 40% | 2.834% | 62.43% | 0% |  | 9.05% | 32.98% | 12.98%
CZ 3C | 63.73% | 40.28% | 0.3894% | 76.57% |  | 58.54% |  | 49.77% |  | 79.46% | 41.47% | 2.834% | 62.43% | 0% |  | 9.05% | 37.68% | 2.16% | CZ 3C | 63.73% | 40.28% | 0.182% | 76.57% |  | 58.54% |  | 49.77% |  | 79.46% | 41.47% | 2.834% | 62.43% | 0% |  | 9.05% | 36.04% | 2.16% | CZ 3C | 63.73% | 40.28% | 2.569% |  |  | 58.54% |  | 49.77% |  | 79.46% | 41.47% | 2.834% | 62.43% | 0% |  | 9.05% | 39.04% | 2.16% | CZ 3C |  |  | 0.07309% | 76.57% | [9 empty] | 0% |  |  | 32.38% | 2.16% | CZ 3C | 63.73% | 40.28% | 0.3566% | 76.57% |  | 58.54% |  | 49.77% |  | 79.46% | 41.47% | 2.834% | 62.43% | 0% |  | 9.05% | 37.54% | 2.16%
CZ 4A | 63.77% | 40.28% | 0.5527% | 90.16% |  | 50.66% |  | 49.34% | 77.79% | 76.05% | 39.41% | 2.834% | 62.43% | 0% |  | 9.05% | 40.12% | 19.33% | CZ 4A | 63.77% | 40.28% | 0.3579% | 90.16% |  | 50.66% |  | 49.34% | 77.79% | 76.05% | 39.41% | 2.834% | 62.43% | 0% |  | 9.05% | 40.94% | 19.33% | CZ 4A | 63.77% | 40.28% | 2.686% |  |  | 50.66% |  | 49.34% | 77.79% | 76.05% | 39.41% | 2.834% | 62.43% | 0% |  | 9.05% | 39.42% | 19.33% | CZ 4A |  |  | 0.2561% | 90.16% | [9 empty] | 0% |  |  | 42.71% | 19.33% | CZ 4A | 63.77% | 40.28% | 0.5218% | 90.16% |  | 50.66% |  | 49.34% | 77.79% | 76.05% | 39.41% | 2.834% | 62.43% | 0% |  | 9.05% | 40.19% | 19.33%
CZ 4B | 63.78% | 40.28% | 0.5359% | 96.58% |  | 47.09% |  | 19.05% | -75.87% | 73.25% | 39.65% | 2.834% | 62.43% | 0% |  | 9.05% | 35.18% | 0.5625% | CZ 4B | 63.78% | 40.28% | 0.3408% | 96.58% |  | 47.09% |  | 19.05% | -75.87% | 73.25% | 39.65% | 2.834% | 62.43% | 0% |  | 9.05% | 40.59% | 0.5625% | CZ 4B | 63.78% | 40.28% | 2.645% |  |  | 47.09% |  | 19.05% | -75.87% | 73.25% | 39.65% | 2.834% | 62.43% | 0% |  | 9.05% | 30.05% | 0.5625% | CZ 4B |  |  | 0.2387% | 96.58% | [9 empty] | 0% |  |  | 50.43% | 0.5625% | CZ 4B | 63.78% | 40.28% | 0.505% | 96.58% |  | 47.09% |  | 19.05% | -75.87% | 73.25% | 39.65% | 2.834% | 62.43% | 0% |  | 9.05% | 35.68% | 0.5625%
CZ 4C | 63.76% | 40.28% | 0.563% | 92.72% |  | 55.43% |  | 47.07% | 64.75% | 73.56% | 39.6% | 2.834% | 62.43% | 0% |  | 9.05% | 37.42% | 3.179% | CZ 4C | 63.76% | 40.28% | 0.3737% | 92.72% |  | 55.43% |  | 47.07% | 64.75% | 73.56% | 39.6% | 2.834% | 62.43% | 0% |  | 9.05% | 39.38% | 3.179% | CZ 4C | 63.76% | 40.28% | 2.666% |  |  | 55.43% |  | 47.07% | 64.75% | 73.56% | 39.6% | 2.834% | 62.43% | 0% |  | 9.05% | 35.59% | 3.179% | CZ 4C |  |  | 0.275% | 92.72% | [9 empty] | 0% |  |  | 43.07% | 3.179% | CZ 4C | 63.76% | 40.28% | 0.5329% | 92.72% |  | 55.43% |  | 47.07% | 64.75% | 73.56% | 39.6% | 2.834% | 62.43% | 0% |  | 9.05% | 37.6% | 3.179%
CZ 5A | 63.79% | 40.28% | 0.5777% | 85.73% |  | 51.58% |  | 50.29% | 78.09% | 72.5% | 39.51% | 2.834% | 62.43% | 0% |  | 9.05% | 39.73% | 15.41% | CZ 5A | 63.79% | 40.28% | 0.3935% | 85.73% |  | 51.58% |  | 50.29% | 78.09% | 72.5% | 39.51% | 2.834% | 62.43% | 0% |  | 9.05% | 41.17% | 15.41% | CZ 5A | 63.79% | 40.28% | 2.676% |  |  | 51.58% |  | 50.29% | 78.09% | 72.5% | 39.51% | 2.834% | 62.43% | 0% |  | 9.05% | 38.38% | 15.41% | CZ 5A |  |  | 0.2977% | 85.73% | [9 empty] | 0% |  |  | 43.87% | 15.41% | CZ 5A | 63.79% | 40.28% | 0.5484% | 85.73% |  | 51.58% |  | 50.29% | 78.09% | 72.5% | 39.51% | 2.834% | 62.43% | 0% |  | 9.05% | 39.86% | 15.41%
CZ 5B | 63.78% | 40.28% | 0.5797% | 94.25% |  | 45.31% |  | 21.91% | -83.35% | 71.47% | 39.65% | 2.834% | 62.43% | 0% |  | 9.05% | 38.09% | 4.56% | CZ 5B | 63.78% | 40.28% | 0.3956% | 94.25% |  | 45.31% |  | 21.91% | -83.35% | 71.47% | 39.65% | 2.834% | 62.43% | 0% |  | 9.05% | 46.22% | 4.56% | CZ 5B | 63.78% | 40.28% | 2.655% |  |  | 45.31% |  | 21.91% | -83.35% | 71.47% | 39.65% | 2.834% | 62.43% | 0% |  | 9.05% | 28.96% | 4.56% | CZ 5B |  |  | 0.2997% | 94.25% | [9 empty] | 0% |  |  | 58.15% | 4.56% | CZ 5B | 63.78% | 40.28% | 0.5504% | 94.25% |  | 45.31% |  | 21.91% | -83.35% | 71.47% | 39.65% | 2.834% | 62.43% | 0% |  | 9.05% | 38.88% | 4.56%
CZ 5C | 63.77% | 40.28% | 0.6041% | 92.73% |  | 49.47% |  | 47.71% | 65.88% | 58.25% | 39.5% | 2.834% | 62.43% | 0% |  | 9.05% | 36.76% | 0.0501% | CZ 5C | 63.77% | 40.28% | 0.4207% | 92.73% |  | 49.47% |  | 47.71% | 65.88% | 58.25% | 39.5% | 2.834% | 62.43% | 0% |  | 9.05% | 39.29% | 0.0501% | CZ 5C | 63.77% | 40.28% | 2.687% |  |  | 49.47% |  | 47.71% | 65.88% | 58.25% | 39.5% | 2.834% | 62.43% | 0% |  | 9.05% | 34.33% | 0.0501% | CZ 5C |  |  | 0.3253% | 92.73% | [9 empty] | 0% |  |  | 43.79% | 0.0501% | CZ 5C | 63.77% | 40.28% | 0.5749% | 92.73% |  | 49.47% |  | 47.71% | 65.88% | 58.25% | 39.5% | 2.834% | 62.43% | 0% |  | 9.05% | 37% | 0.0501%
CZ 6A | 63.79% | 40.28% | 0.6092% | 78.37% |  | 52.24% |  | 49.61% | 77.05% | 81.16% | 39.2% | 2.834% | 62.43% | 0% |  | 9.05% | 40.06% | 3.403% | CZ 6A | 63.79% | 40.28% | 0.4301% | 78.37% |  | 52.24% |  | 49.61% | 77.05% | 81.16% | 39.2% | 2.834% | 62.43% | 0% |  | 9.05% | 41.45% | 3.403% | CZ 6A | 63.79% | 40.28% | 2.707% |  |  | 52.24% |  | 49.61% | 77.05% | 81.16% | 39.2% | 2.834% | 62.43% | 0% |  | 9.05% | 38.69% | 3.403% | CZ 6A |  |  | 0.3372% | 78.37% | [9 empty] | 0% |  |  | 43.83% | 3.403% | CZ 6A | 63.79% | 40.28% | 0.5806% | 78.37% |  | 52.24% |  | 49.61% | 77.05% | 81.16% | 39.2% | 2.834% | 62.43% | 0% |  | 9.05% | 40.19% | 3.403%
CZ 6B | 63.8% | 40.28% | 0.606% | 80.32% |  | 43.96% |  | 34.82% | 75.88% | 77.12% | 39.46% | 2.834% | 62.43% | 0% |  | 9.05% | 35.52% | 0.9897% | CZ 6B | 63.8% | 40.28% | 0.4289% | 80.32% |  | 43.96% |  | 34.82% | 75.88% | 77.12% | 39.46% | 2.834% | 62.43% | 0% |  | 9.05% | 37.34% | 0.9897% | CZ 6B | 63.8% | 40.28% | 2.666% |  |  | 43.96% |  | 34.82% | 75.88% | 77.12% | 39.46% | 2.834% | 62.43% | 0% |  | 9.05% | 33.74% | 0.9897% | CZ 6B |  |  | 0.3371% | 80.32% | [9 empty] | 0% |  |  | 40.53% | 0.9897% | CZ 6B | 63.8% | 40.28% | 0.5778% | 80.32% |  | 43.96% |  | 34.82% | 75.88% | 77.12% | 39.46% | 2.834% | 62.43% | 0% |  | 9.05% | 35.69% | 0.9897%
CZ 7 | 63.81% | 40.28% | 0.6427% | 75.72% |  | 50.92% |  | 48.53% | 77.05% | 70.53% | 39.16% | 2.834% | 62.43% | 0% |  | 9.05% | 40.16% | 0.5763% | CZ 7 | 63.81% | 40.28% | 0.4721% | 75.72% |  | 50.92% |  | 48.53% | 77.05% | 70.53% | 39.16% | 2.834% | 62.43% | 0% |  | 9.05% | 42.6% | 0.5763% | CZ 7 | 63.81% | 40.28% | 2.707% |  |  | 50.92% |  | 48.53% | 77.05% | 70.53% | 39.16% | 2.834% | 62.43% | 0% |  | 9.05% | 37.47% | 0.5763% | CZ 7 |  |  | 0.384% | 75.72% | [9 empty] | 0% |  |  | 46.28% | 0.5763% | CZ 7 | 63.81% | 40.28% | 0.6155% | 75.72% |  | 50.92% |  | 48.53% | 77.05% | 70.53% | 39.16% | 2.834% | 62.43% | 0% |  | 9.05% | 40.4% | 0.5763%
CZ 8 | 63.77% | 40.28% | 0.6584% | 71.73% |  | 43.09% |  | 52.71% | 75.21% | 70.63% | 38.86% | 2.834% | 62.43% | 0% |  | 9.05% | 41.1% | 0.01322% | CZ 8 | 63.77% | 40.28% | 0.4944% | 71.73% |  | 43.09% |  | 52.71% | 75.21% | 70.63% | 38.86% | 2.834% | 62.43% | 0% |  | 9.05% | 44.55% | 0.01322% | CZ 8 | 63.77% | 40.28% | 2.728% |  |  | 43.09% |  | 52.71% | 75.21% | 70.63% | 38.86% | 2.834% | 62.43% | 0% |  | 9.05% | 36.56% | 0.01322% | CZ 8 |  |  | 0.4101% | 71.73% | [9 empty] | 0% |  |  | 48.85% | 0.01322% | CZ 8 | 63.77% | 40.28% | 0.6322% | 71.73% |  | 43.09% |  | 52.71% | 75.21% | 70.63% | 38.86% | 2.834% | 62.43% | 0% |  | 9.05% | 41.46% | 0.01322%
US Weighted | 63.76% | 40.28% | 0.5415% | 91.49% | 0% | 49.45% | 0% | 43.53% | 63.09% | 77.24% | 39.94% | 2.834% | 62.43% | 0% | 0% | 9.05% | 38.72% | 100% | US Weighted | 63.76% | 40.28% | 0.3424% | 91.49% | 0% | 49.45% | 0% | 43.53% | 63.09% | 77.24% | 39.94% | 2.834% | 62.43% | 0% | 0% | 9.05% | 38.92% | 100% | US Weighted | 63.76% | 40.28% | 2.65% | 0% | 0% | 49.45% | 0% | 43.53% | 63.09% | 77.24% | 39.94% | 2.834% | 62.43% | 0% | 0% | 9.05% | 38.31% | 100% | US Weighted | 0% | 0% | 0.2378% | 91.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.12% | 100% | US Weighted | 63.76% | 40.28% | 0.51% | 91.49% | 0% | 49.45% | 0% | 43.53% | 63.09% | 77.24% | 39.94% | 2.834% | 62.43% | 0% | 0% | 9.05% | 38.75% | 100%

## Whse
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Warehouse |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 52045 |  | Building Type: | Warehouse |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 |  | Building Type: | Warehouse |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Warehouse |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Warehouse | [14 empty] | Prototype Floor Area: | 52045 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.095425 | 0.032254 | 0.014068 | 0.067865 | 0 | 0.019223 | 0 | 0.027909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.33421 |  | STD2019 | 3.0629 | 1.0353 | 0.45156 | 6.925 | 0 | 0.617 | 0 | 0.89582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.4741 |  | STD2019 | 0.89769 | 0.30343 | 0.13234 | 0 | 0 | 0.18083 | 0 | 0.26255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5056 |  | STD2019 | 0 | 0 | 0 | 0.06925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06925 |  | STD2019 | 9.3979 | 3.1766 | 1.3855 | 7.569 | 0 | 1.8931 | 0 | 2.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 33.8
STD2016 | 0.10314 | 0.032254 | 0.014068 | 0.067574 | 0 | 0.020065 | 0 | 0.027801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.34237 |  | STD2016 | 3.3105 | 1.0353 | 0.45156 | 6.8953 | 0 | 0.64404 | 0 | 0.89236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.7155 |  | STD2016 | 0.97026 | 0.30343 | 0.13234 | 0 | 0 | 0.18876 | 0 | 0.26154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5851 |  | STD2016 | 0 | 0 | 0 | 0.068953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068953 |  | STD2016 | 10.1576 | 3.1766 | 1.3855 | 7.5365 | 0 | 1.9761 | 0 | 2.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 34.5996
STD2013 | 0.17399 | 0.047513 | 0.014064 | 0.066139 | 0 | 0.023259 | 0 | 0.030214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.43265 |  | STD2013 | 5.5848 | 1.5251 | 0.45141 | 6.7489 | 0 | 0.74656 | 0 | 0.96981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 18.513 |  | STD2013 | 1.6368 | 0.44697 | 0.1323 | 0 | 0 | 0.2188 | 0 | 0.28423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.4479 |  | STD2013 | 0 | 0 | 0 | 0.067489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067489 |  | STD2013 | 17.1359 | 4.6793 | 1.3851 | 7.3766 | 0 | 2.2907 | 0 | 2.9756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 43.4723
STD2010 | 0.1777 | 0.047513 | 0.014071 | 0.072624 | 0 | 0.025962 | 0 | 0.035294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.45095 |  | STD2010 | 5.7038 | 1.5251 | 0.45164 | 7.4106 | 0 | 0.83334 | 0 | 1.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 19.554 |  | STD2010 | 1.6717 | 0.44697 | 0.13237 | 0 | 0 | 0.24424 | 0 | 0.33203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.559 |  | STD2010 | 0 | 0 | 0 | 0.074106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074106 |  | STD2010 | 17.501 | 4.6793 | 1.3858 | 8.0998 | 0 | 2.5569 | 0 | 3.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 45.3592
STD2007 | 0.27352 | 0.070064 | 0.01452 | 0.089428 | 0 | 0.036896 | 0 | 0.040392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.60386 |  | STD2007 | 8.7793 | 2.2489 | 0.46605 | 9.1253 | 0 | 1.1843 | 0 | 1.2965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.6375 |  | STD2007 | 2.5731 | 0.65912 | 0.13659 | 0 | 0 | 0.34709 | 0 | 0.37999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.8394 |  | STD2007 | 0 | 0 | 0 | 0.091253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091253 |  | STD2007 | 26.9375 | 6.9003 | 1.43 | 9.9739 | 0 | 3.6337 | 0 | 3.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 60.6381
STD2004 | 0.27352 | 0.070064 | 0.01452 | 0.11022 | 0 | 0.037126 | 0 | 0.040931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.62542 |  | STD2004 | 8.7793 | 2.2489 | 0.46606 | 11.2466 | 0 | 1.1916 | 0 | 1.3138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 27.7835 |  | STD2004 | 2.5731 | 0.65912 | 0.13659 | 0 | 0 | 0.34925 | 0 | 0.38505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.8467 |  | STD2004 | 0 | 0 | 0 | 0.11247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11247 |  | STD2004 | 26.9375 | 6.9003 | 1.43 | 12.2926 | 0 | 3.6563 | 0 | 4.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 63.0325
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 2.0237e-07 | 0.020789 | 0 | 0.00022999 | 0 | 0.00053875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021558 |  | 2004-2007 | 0 | 0 | 6.4956e-06 | 2.1214 | 0 | 0.0073823 | 0 | 0.017293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.146 |  | 2004-2007 | 0 | 0 | 1.9037e-06 | 0 | 0 | 0.0021636 | 0 | 0.0050682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072337 |  | 2004-2007 | 0 | 0 | 0 | 0.021214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021214 |  | 2004-2007 | 0 | 0 | 1.993e-05 | 2.3187 | 0 | 0.022651 | 0 | 0.053059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3944
2007-2010 | 0.095817 | 0.022552 | 0.00044911 | 0.016804 | 0 | 0.010933 | 0 | 0.0050981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012599 | 0.15291 |  | 2007-2010 | 3.0755 | 0.72386 | 0.014415 | 1.7147 | 0 | 0.35093 | 0 | 0.16364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040439 | 6.0835 |  | 2007-2010 | 0.90138 | 0.21215 | 0.0042249 | 0 | 0 | 0.10285 | 0 | 0.04796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011852 | 1.2804 |  | 2007-2010 | 0 | 0 | 0 | 0.017147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017147 |  | 2007-2010 | 9.4366 | 2.221 | 0.044231 | 1.8741 | 0 | 1.0768 | 0 | 0.50209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12408 | 15.2789
2010-2013 | 0.0037071 | 0 | 7.1587e-06 | 0.0064846 | 0 | 0.0027035 | 0 | 0.0050802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00031781 | 0.0183 |  | 2010-2013 | 0.11899 | 0 | 0.00022978 | 0.66169 | 0 | 0.086776 | 0 | 0.16306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010201 | 1.041 |  | 2010-2013 | 0.034874 | 0 | 6.7345e-05 | 0 | 0 | 0.025433 | 0 | 0.047791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029897 | 0.11115 |  | 2010-2013 | 0 | 0 | 0 | 0.0066169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0066169 |  | 2010-2013 | 0.3651 | 0 | 0.00070503 | 0.72323 | 0 | 0.26625 | 0 | 0.50033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031299 | 1.8869
2013-2016 | 0.070856 | 0.015258 | -4.7157e-06 | -0.0014344 | 0 | 0.003194 | 0 | 0.0024127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090282 |  | 2013-2016 | 2.2743 | 0.48976 | -0.00015136 | -0.14636 | 0 | 0.10252 | 0 | 0.077442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7975 |  | 2013-2016 | 0.66656 | 0.14354 | -4.4362e-05 | 0 | 0 | 0.030047 | 0 | 0.022697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8628 |  | 2013-2016 | 0 | 0 | 0 | -0.0014636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0014636 |  | 2013-2016 | 6.9783 | 1.5027 | -0.00046443 | -0.15998 | 0 | 0.31457 | 0 | 0.23761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8727
2016-2019 | 0.0077138 | 0 | 0 | -0.00029122 | 0 | 0.00084235 | 0 | -0.00010773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081572 |  | 2016-2019 | 0.2476 | 0 | 0 | -0.029716 | 0 | 0.027038 | 0 | -0.0034579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24146 |  | 2016-2019 | 0.072566 | 0 | 0 | 0 | 0 | 0.0079243 | 0 | -0.0010135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079477 |  | 2016-2019 | 0 | 0 | 0 | -0.00029716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00029716 |  | 2016-2019 | 0.7597 | 0 | 0 | -0.03248 | 0 | 0.08296 | 0 | -0.01061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79957
2004-2019 | 0.17809 | 0.03781 | 0.00045175 | 0.042352 | 0 | 0.017903 | 0 | 0.013022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.29121 |  | 2004-2019 | 5.7164 | 1.2136 | 0.0145 | 4.3217 | 0 | 0.57465 | 0 | 0.41798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 12.3095 |  | 2004-2019 | 1.6754 | 0.35569 | 0.0042498 | 0 | 0 | 0.16842 | 0 | 0.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.3411 |  | 2004-2019 | 0 | 0 | 0 | 0.043217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043217 |  | 2004-2019 | 17.5396 | 3.7237 | 0.044491 | 4.7236 | 0 | 1.7632 | 0 | 1.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 29.2324
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.001394% | 18.86% |  | 0.6195% |  | 1.316% | [7 empty] | 0% | 3.447% |  | 2004-2007 | 0% | 0% | 0.001394% | 18.86% |  | 0.6195% |  | 1.316% | [7 empty] | 0% | 7.724% |  | 2004-2007 | 0% | 0% | 0.001394% |  |  | 0.6195% |  | 1.316% | [7 empty] | 0% | 0.1493% |  | 2004-2007 |  |  |  | 18.86% | [12 empty] | 18.86% |  | 2004-2007 | 0% | 0% | 0.001394% | 18.86% |  | 0.6195% |  | 1.316% | [7 empty] | 0% | 3.799%
2007-2010 | 35.03% | 32.19% | 3.093% | 18.79% |  | 29.63% |  | 12.62% | [7 empty] | 1.594% | 25.32% |  | 2007-2010 | 35.03% | 32.19% | 3.093% | 18.79% |  | 29.63% |  | 12.62% | [7 empty] | 1.594% | 23.73% |  | 2007-2010 | 35.03% | 32.19% | 3.093% |  |  | 29.63% |  | 12.62% | [7 empty] | 1.594% | 26.46% |  | 2007-2010 |  |  |  | 18.79% | [12 empty] | 18.79% |  | 2007-2010 | 35.03% | 32.19% | 3.093% | 18.79% |  | 29.63% |  | 12.62% | [7 empty] | 1.594% | 25.2%
2010-2013 | 2.086% | 0% | 0.05088% | 8.929% |  | 10.41% |  | 14.39% | [7 empty] | 0.4086% | 4.058% |  | 2010-2013 | 2.086% | 0% | 0.05088% | 8.929% |  | 10.41% |  | 14.39% | [7 empty] | 0.4086% | 5.323% |  | 2010-2013 | 2.086% | 0% | 0.05088% |  |  | 10.41% |  | 14.39% | [7 empty] | 0.4086% | 3.123% |  | 2010-2013 |  |  |  | 8.929% | [12 empty] | 8.929% |  | 2010-2013 | 2.086% | 0% | 0.05088% | 8.929% |  | 10.41% |  | 14.39% | [7 empty] | 0.4086% | 4.16%
2013-2016 | 40.72% | 32.11% | -0.03353% | -2.169% |  | 13.73% |  | 7.985% | [7 empty] | 0% | 20.87% |  | 2013-2016 | 40.72% | 32.11% | -0.03353% | -2.169% |  | 13.73% |  | 7.985% | [7 empty] | 0% | 15.11% |  | 2013-2016 | 40.72% | 32.11% | -0.03353% |  |  | 13.73% |  | 7.985% | [7 empty] | 0% | 25.02% |  | 2013-2016 |  |  |  | -2.169% | [12 empty] | -2.169% |  | 2013-2016 | 40.72% | 32.11% | -0.03353% | -2.169% |  | 13.73% |  | 7.985% | [7 empty] | 0% | 20.41%
2016-2019 | 7.479% | 0% | 0% | -0.431% |  | 4.198% |  | -0.3875% | [7 empty] | 0% | 2.383% |  | 2016-2019 | 7.479% | 0% | 0% | -0.431% |  | 4.198% |  | -0.3875% | [7 empty] | 0% | 1.536% |  | 2016-2019 | 7.479% | 0% | 0% |  |  | 4.198% |  | -0.3875% | [7 empty] | 0% | 3.074% |  | 2016-2019 |  |  |  | -0.431% | [12 empty] | -0.431% |  | 2016-2019 | 7.479% | 0% | 0% | -0.431% |  | 4.198% |  | -0.3875% | [7 empty] | 0% | 2.311%
2004-2019 | 65.11% | 53.96% | 3.111% | 38.43% |  | 48.22% |  | 31.81% | [7 empty] | 1.996% | 46.56% |  | 2004-2019 | 65.11% | 53.96% | 3.111% | 38.43% |  | 48.22% |  | 31.81% | [7 empty] | 1.996% | 44.3% |  | 2004-2019 | 65.11% | 53.96% | 3.111% |  |  | 48.22% |  | 31.81% | [7 empty] | 1.996% | 48.3% |  | 2004-2019 |  |  |  | 38.43% | [12 empty] | 38.43% |  | 2004-2019 | 65.11% | 53.96% | 3.111% | 38.43% |  | 48.22% |  | 31.81% | [7 empty] | 1.996% | 46.38%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.088838 | 0.032235 | 0.012514 | 0 | 0 | 0.094048 | 0 | 0.045418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.35052 | 0% | CZ 0A | 2.8515 | 1.0347 | 0.40166 | 0 | 0 | 3.0187 | 0 | 1.4578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.2509 | 0% | CZ 0A | 0.83573 | 0.30324 | 0.11772 | 0 | 0 | 0.88474 | 0 | 0.42726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.2974 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 8.7493 | 3.1746 | 1.2324 | 0 | 0 | 9.2624 | 0 | 4.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 34.5209 | 0%
CZ 0B | 0.090978 | 0.032218 | 0.012497 | 3.5695e-06 | 0 | 0.098401 | 0 | 0.055758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.36732 | 0% | CZ 0B | 2.9202 | 1.0341 | 0.40111 | 0.00036423 | 0 | 3.1585 | 0 | 1.7897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.7904 | 0% | CZ 0B | 0.85586 | 0.30308 | 0.11756 | 0 | 0 | 0.92569 | 0 | 0.52453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.4555 | 0% | CZ 0B | 0 | 0 | 0 | 3.6423e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6423e-06 | 0% | CZ 0B | 8.96 | 3.173 | 1.2307 | 0.0003981 | 0 | 9.6911 | 0 | 5.4914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 36.1757 | 0%
CZ 1A | 0.092777 | 0.032229 | 0.012848 | 0 | 0 | 0.053289 | 0 | 0.034278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.30289 | 2.875% | CZ 1A | 2.9779 | 1.0345 | 0.41241 | 0 | 0 | 1.7105 | 0 | 1.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.722 | 2.875% | CZ 1A | 0.87278 | 0.30319 | 0.12087 | 0 | 0 | 0.50131 | 0 | 0.32246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.8494 | 2.875% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.875% | CZ 1A | 9.1372 | 3.1741 | 1.2654 | 0 | 0 | 5.2482 | 0 | 3.3759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 29.8299 | 2.875%
CZ 1B | 0.091784 | 0.032178 | 0.01286 | 0.00035159 | 0 | 0.068459 | 0 | 0.047989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.33109 | 0% | CZ 1B | 2.9461 | 1.0328 | 0.41277 | 0.035877 | 0 | 2.1974 | 0 | 1.5403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 10.6517 | 0% | CZ 1B | 0.86344 | 0.30271 | 0.12098 | 0 | 0 | 0.64402 | 0 | 0.45145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.1113 | 0% | CZ 1B | 0 | 0 | 0 | 0.00035877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00035877 | 0% | CZ 1B | 9.0394 | 3.1691 | 1.2665 | 0.039213 | 0 | 6.7422 | 0 | 4.7262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 32.6118 | 0%
CZ 2A | 0.093185 | 0.032172 | 0.01324 | 0.00031054 | 0 | 0.038716 | 0 | 0.031826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.28692 | 19% | CZ 2A | 2.9911 | 1.0327 | 0.42498 | 0.031688 | 0 | 1.2427 | 0 | 1.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.2311 | 19% | CZ 2A | 0.87663 | 0.30266 | 0.12455 | 0 | 0 | 0.36421 | 0 | 0.2994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.6962 | 19% | CZ 2A | 0 | 0 | 0 | 0.00031688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00031688 | 19% | CZ 2A | 9.1774 | 3.1685 | 1.304 | 0.034635 | 0 | 3.8129 | 0 | 3.1344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 28.261 | 19%
CZ 2B | 0.097544 | 0.032206 | 0.013268 | 0.00070497 | 0 | 0.038687 | 0 | 0.039811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.29969 | 3.369% | CZ 2B | 3.131 | 1.0338 | 0.42589 | 0.071935 | 0 | 1.2418 | 0 | 1.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.6686 | 3.369% | CZ 2B | 0.91763 | 0.30298 | 0.12482 | 0 | 0 | 0.36394 | 0 | 0.37452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.8126 | 3.369% | CZ 2B | 0 | 0 | 0 | 0.00071935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00071935 | 3.369% | CZ 2B | 9.6067 | 3.1719 | 1.3067 | 0.078625 | 0 | 3.8101 | 0 | 3.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 29.524 | 3.369%
CZ 3A | 0.095211 | 0.032235 | 0.01391 | 0.031177 | 0 | 0.019454 | 0 | 0.028625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.29808 | 14.95% | CZ 3A | 3.0561 | 1.0347 | 0.44647 | 3.1814 | 0 | 0.62444 | 0 | 0.91881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.7483 | 14.95% | CZ 3A | 0.89569 | 0.30324 | 0.13085 | 0 | 0 | 0.18301 | 0 | 0.26929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5108 | 14.95% | CZ 3A | 0 | 0 | 0 | 0.031814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031814 | 14.95% | CZ 3A | 9.3769 | 3.1746 | 1.3699 | 3.4772 | 0 | 1.916 | 0 | 2.8192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 29.7631 | 14.95%
CZ 3B | 0.096108 | 0.032172 | 0.013739 | 0.005497 | 0 | 0.023353 | 0 | 0.03547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.2838 | 12.03% | CZ 3B | 3.0849 | 1.0327 | 0.44101 | 0.56091 | 0 | 0.74958 | 0 | 1.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.494 | 12.03% | CZ 3B | 0.90412 | 0.30266 | 0.12925 | 0 | 0 | 0.21969 | 0 | 0.33367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.6181 | 12.03% | CZ 3B | 0 | 0 | 0 | 0.0056091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056091 | 12.03% | CZ 3B | 9.4653 | 3.1685 | 1.3531 | 0.61308 | 0 | 2.2999 | 0 | 3.4932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 28.0223 | 12.03%
CZ 3C | 0.095268 | 0.032274 | 0.013978 | 0.00063179 | 0 | 0.0064526 | 0 | 0.020272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.24634 | 0.9851% | CZ 3C | 3.0579 | 1.0359 | 0.44866 | 0.064469 | 0 | 0.20711 | 0 | 0.65067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 7.9512 | 0.9851% | CZ 3C | 0.89622 | 0.30362 | 0.13149 | 0 | 0 | 0.060702 | 0 | 0.1907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.3115 | 0.9851% | CZ 3C | 0 | 0 | 0 | 0.00064469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00064469 | 0.9851% | CZ 3C | 9.3825 | 3.1786 | 1.3766 | 0.070464 | 0 | 0.63549 | 0 | 1.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 24.2693 | 0.9851%
CZ 4A | 0.093918 | 0.032343 | 0.014438 | 0.10488 | 0 | 0.010346 | 0 | 0.023489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.35688 | 19.91% | CZ 4A | 3.0146 | 1.0381 | 0.46341 | 10.7025 | 0 | 0.33208 | 0 | 0.75396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 18.7911 | 19.91% | CZ 4A | 0.88351 | 0.30426 | 0.13582 | 0 | 0 | 0.097326 | 0 | 0.22097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.3706 | 19.91% | CZ 4A | 0 | 0 | 0 | 0.10703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10703 | 19.91% | CZ 4A | 9.2495 | 3.1853 | 1.4219 | 11.6979 | 0 | 1.0189 | 0 | 2.3134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 36.516 | 19.91%
CZ 4B | 0.095132 | 0.032178 | 0.014284 | 0.035402 | 0 | 0.012502 | 0 | 0.029494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.29646 | 0.283% | CZ 4B | 3.0535 | 1.0328 | 0.45849 | 3.6124 | 0 | 0.4013 | 0 | 0.94668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.9917 | 0.283% | CZ 4B | 0.89494 | 0.30271 | 0.13438 | 0 | 0 | 0.11761 | 0 | 0.27746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.4558 | 0.283% | CZ 4B | 0 | 0 | 0 | 0.036124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036124 | 0.283% | CZ 4B | 9.3691 | 3.1691 | 1.4068 | 3.9484 | 0 | 1.2313 | 0 | 2.9047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 29.6586 | 0.283%
CZ 4C | 0.097606 | 0.032422 | 0.014602 | 0.046601 | 0 | 0.0017877 | 0 | 0.018944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.28943 | 2.916% | CZ 4C | 3.133 | 1.0407 | 0.4687 | 4.7552 | 0 | 0.05738 | 0 | 0.60805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.5494 | 2.916% | CZ 4C | 0.91822 | 0.305 | 0.13737 | 0 | 0 | 0.016817 | 0 | 0.17821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.2844 | 2.916% | CZ 4C | 0 | 0 | 0 | 0.047552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047552 | 2.916% | CZ 4C | 9.6128 | 3.1931 | 1.4381 | 5.1974 | 0 | 0.17606 | 0 | 1.8657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 29.1124 | 2.916%
CZ 5A | 0.094332 | 0.03228 | 0.014874 | 0.17759 | 0 | 0.0042053 | 0 | 0.021957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.4227 | 16.91% | CZ 5A | 3.0278 | 1.0361 | 0.47744 | 18.1212 | 0 | 0.13498 | 0 | 0.70477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 25.9888 | 16.91% | CZ 5A | 0.88741 | 0.30367 | 0.13993 | 0 | 0 | 0.03956 | 0 | 0.20656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.3059 | 16.91% | CZ 5A | 0 | 0 | 0 | 0.18121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18121 | 16.91% | CZ 5A | 9.2903 | 3.1791 | 1.4649 | 19.8064 | 0 | 0.41416 | 0 | 2.1624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 43.9466 | 16.91%
CZ 5B | 0.09587 | 0.032303 | 0.01475 | 0.089848 | 0 | 0.0067761 | 0 | 0.027496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.34451 | 4.393% | CZ 5B | 3.0772 | 1.0368 | 0.47343 | 9.1682 | 0 | 0.2175 | 0 | 0.88256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.3422 | 4.393% | CZ 5B | 0.90188 | 0.30388 | 0.13875 | 0 | 0 | 0.063745 | 0 | 0.25866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.3957 | 4.393% | CZ 5B | 0 | 0 | 0 | 0.091682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091682 | 4.393% | CZ 5B | 9.4418 | 3.1814 | 1.4526 | 10.0209 | 0 | 0.66735 | 0 | 2.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 35.1011 | 4.393%
CZ 5C | 0.09709 | 0.032405 | 0.014852 | 0.041786 | 0 | 0.00065831 | 0 | 0.016963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.28122 | 0.0163% | CZ 5C | 3.1164 | 1.0401 | 0.47671 | 4.2639 | 0 | 0.02113 | 0 | 0.54447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.9491 | 0.0163% | CZ 5C | 0.91336 | 0.30484 | 0.13972 | 0 | 0 | 0.006193 | 0 | 0.15958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.2524 | 0.0163% | CZ 5C | 0 | 0 | 0 | 0.042639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042639 | 0.0163% | CZ 5C | 9.5619 | 3.1914 | 1.4627 | 4.6604 | 0 | 0.064834 | 0 | 1.6706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 28.2411 | 0.0163%
CZ 6A | 0.12845 | 0.03232 | 0.015198 | 0.26857 | 0 | 0.0041996 | 0 | 0.023637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.54984 | 1.997% | CZ 6A | 4.123 | 1.0374 | 0.48782 | 27.4047 | 0 | 0.1348 | 0 | 0.75869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 36.4328 | 1.997% | CZ 6A | 1.2084 | 0.30404 | 0.14297 | 0 | 0 | 0.039507 | 0 | 0.22236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.646 | 1.997% | CZ 6A | 0 | 0 | 0 | 0.27405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27405 | 1.997% | CZ 6A | 12.6505 | 3.183 | 1.4968 | 29.9533 | 0 | 0.4136 | 0 | 2.3279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 57.6543 | 1.997%
CZ 6B | 0.12888 | 0.032325 | 0.015119 | 0.16153 | 0 | 0.0031213 | 0 | 0.024119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.44255 | 0.1627% | CZ 6B | 4.1367 | 1.0376 | 0.48527 | 16.4823 | 0 | 0.10019 | 0 | 0.77418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 25.5026 | 0.1627% | CZ 6B | 1.2124 | 0.3041 | 0.14223 | 0 | 0 | 0.029363 | 0 | 0.2269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.6437 | 0.1627% | CZ 6B | 0 | 0 | 0 | 0.16482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16482 | 0.1627% | CZ 6B | 12.6924 | 3.1836 | 1.489 | 18.0152 | 0 | 0.3074 | 0 | 2.3754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 45.6922 | 0.1627%
CZ 7 | 0.12873 | 0.032416 | 0.015584 | 0.24646 | 0 | 0.0022927 | 0 | 0.020686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.52363 | 0.1966% | CZ 7 | 4.1321 | 1.0405 | 0.50021 | 25.1486 | 0 | 0.073592 | 0 | 0.66397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 34.0454 | 0.1966% | CZ 7 | 1.211 | 0.30495 | 0.1466 | 0 | 0 | 0.021569 | 0 | 0.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.6075 | 0.1966% | CZ 7 | 0 | 0 | 0 | 0.25149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25149 | 0.1966% | CZ 7 | 12.6785 | 3.1925 | 1.5348 | 27.4874 | 0 | 0.2258 | 0 | 2.0373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 54.7855 | 0.1966%
CZ 8 | 0.13041 | 0.033273 | 0.0161 | 0.25469 | 0 | 0.00060156 | 0 | 0.01799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.53053 | 0.01103% | CZ 8 | 4.186 | 1.068 | 0.51679 | 25.9885 | 0 | 0.019309 | 0 | 0.57744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 34.8426 | 0.01103% | CZ 8 | 1.2269 | 0.31301 | 0.15146 | 0 | 0 | 0.0056591 | 0 | 0.16924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.595 | 0.01103% | CZ 8 | 0 | 0 | 0 | 0.25989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25989 | 0.01103% | CZ 8 | 12.8439 | 3.2769 | 1.5856 | 28.4055 | 0 | 0.059245 | 0 | 1.7718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 55.5722 | 0.01103%
US Weighted | 0.095425 | 0.032254 | 0.014068 | 0.067865 | 0 | 0.019223 | 0 | 0.027909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.33421 | 100% | US Weighted | 3.0629 | 1.0353 | 0.45156 | 6.925 | 0 | 0.617 | 0 | 0.89582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.4741 | 100% | US Weighted | 0.89769 | 0.30343 | 0.13234 | 0 | 0 | 0.18083 | 0 | 0.26255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5056 | 100% | US Weighted | 0 | 0 | 0 | 0.06925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06925 | 100% | US Weighted | 9.3979 | 3.1766 | 1.3855 | 7.569 | 0 | 1.8931 | 0 | 2.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 33.8 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.092834 | 0.032235 | 0.012514 | 0 | 0 | 0.095796 | 0 | 0.046201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.35704 | 0% | CZ 0A | 2.9798 | 1.0347 | 0.40166 | 0 | 0 | 3.0748 | 0 | 1.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.4604 | 0% | CZ 0A | 0.87332 | 0.30324 | 0.11772 | 0 | 0 | 0.90119 | 0 | 0.43463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.3588 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 9.1428 | 3.1746 | 1.2324 | 0 | 0 | 9.4345 | 0 | 4.5501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 35.1637 | 0%
CZ 0B | 0.095098 | 0.032218 | 0.012497 | 3.5695e-06 | 0 | 0.099956 | 0 | 0.056252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.37349 | 0% | CZ 0B | 3.0524 | 1.0341 | 0.40111 | 0.00036423 | 0 | 3.2084 | 0 | 1.8056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 11.9884 | 0% | CZ 0B | 0.89462 | 0.30308 | 0.11756 | 0 | 0 | 0.94032 | 0 | 0.52918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.5135 | 0% | CZ 0B | 0 | 0 | 0 | 3.6423e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6423e-06 | 0% | CZ 0B | 9.3658 | 3.173 | 1.2307 | 0.0003981 | 0 | 9.8442 | 0 | 5.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 36.7833 | 0%
CZ 1A | 0.097816 | 0.032229 | 0.012848 | 0 | 0 | 0.054998 | 0 | 0.035186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.31054 | 2.875% | CZ 1A | 3.1397 | 1.0345 | 0.41241 | 0 | 0 | 1.7653 | 0 | 1.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.9677 | 2.875% | CZ 1A | 0.92019 | 0.30319 | 0.12087 | 0 | 0 | 0.51738 | 0 | 0.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.9214 | 2.875% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.875% | CZ 1A | 9.6335 | 3.1741 | 1.2654 | 0 | 0 | 5.4165 | 0 | 3.4653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 30.5839 | 2.875%
CZ 1B | 0.096415 | 0.032178 | 0.01286 | 0.0003391 | 0 | 0.069855 | 0 | 0.048505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.33762 | 0% | CZ 1B | 3.0947 | 1.0328 | 0.41277 | 0.034602 | 0 | 2.2422 | 0 | 1.5569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 10.8605 | 0% | CZ 1B | 0.907 | 0.30271 | 0.12098 | 0 | 0 | 0.65715 | 0 | 0.45631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.1729 | 0% | CZ 1B | 0 | 0 | 0 | 0.00034602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034602 | 0% | CZ 1B | 9.4954 | 3.1691 | 1.2665 | 0.03782 | 0 | 6.8797 | 0 | 4.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 33.2548 | 0%
CZ 2A | 0.098554 | 0.032172 | 0.01324 | 0.00037301 | 0 | 0.040742 | 0 | 0.028455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.291 | 19% | CZ 2A | 3.1634 | 1.0327 | 0.42498 | 0.038062 | 0 | 1.3077 | 0 | 0.91335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.3666 | 19% | CZ 2A | 0.92713 | 0.30266 | 0.12455 | 0 | 0 | 0.38327 | 0 | 0.26769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.734 | 19% | CZ 2A | 0 | 0 | 0 | 0.00038062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00038062 | 19% | CZ 2A | 9.7061 | 3.1685 | 1.304 | 0.041602 | 0 | 4.0125 | 0 | 2.8024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 28.6643 | 19%
CZ 2B | 0.10379 | 0.032206 | 0.013268 | 0.00068533 | 0 | 0.03976 | 0 | 0.040327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.30751 | 3.369% | CZ 2B | 3.3315 | 1.0338 | 0.42589 | 0.069932 | 0 | 1.2762 | 0 | 1.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.9182 | 3.369% | CZ 2B | 0.97641 | 0.30298 | 0.12482 | 0 | 0 | 0.37403 | 0 | 0.37937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.8864 | 3.369% | CZ 2B | 0 | 0 | 0 | 0.00069932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00069932 | 3.369% | CZ 2B | 10.222 | 3.1719 | 1.3067 | 0.076436 | 0 | 3.9158 | 0 | 3.9717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 30.2937 | 3.369%
CZ 3A | 0.10109 | 0.032235 | 0.01391 | 0.031433 | 0 | 0.02013 | 0 | 0.029164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.30542 | 14.95% | CZ 3A | 3.2446 | 1.0347 | 0.44647 | 3.2074 | 0 | 0.64612 | 0 | 0.93612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.0019 | 14.95% | CZ 3A | 0.95094 | 0.30324 | 0.13085 | 0 | 0 | 0.18937 | 0 | 0.27436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5775 | 14.95% | CZ 3A | 0 | 0 | 0 | 0.032074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032074 | 14.95% | CZ 3A | 9.9554 | 3.1746 | 1.3699 | 3.5057 | 0 | 1.9825 | 0 | 2.8723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 30.4896 | 14.95%
CZ 3B | 0.10204 | 0.032172 | 0.013739 | 0.0053131 | 0 | 0.024221 | 0 | 0.036099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.29105 | 12.03% | CZ 3B | 3.2752 | 1.0327 | 0.44101 | 0.54216 | 0 | 0.77745 | 0 | 1.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 9.7137 | 12.03% | CZ 3B | 0.95991 | 0.30266 | 0.12925 | 0 | 0 | 0.22786 | 0 | 0.3396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.688 | 12.03% | CZ 3B | 0 | 0 | 0 | 0.0054216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054216 | 12.03% | CZ 3B | 10.0493 | 3.1685 | 1.3531 | 0.59258 | 0 | 2.3855 | 0 | 3.5553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 28.7335 | 12.03%
CZ 3C | 0.10084 | 0.032274 | 0.013978 | 0.00053363 | 0 | 0.0070598 | 0 | 0.020987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.25313 | 0.9851% | CZ 3C | 3.2366 | 1.0359 | 0.44866 | 0.054452 | 0 | 0.22661 | 0 | 0.67362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 8.1624 | 0.9851% | CZ 3C | 0.94859 | 0.30362 | 0.13149 | 0 | 0 | 0.066414 | 0 | 0.19743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.3763 | 0.9851% | CZ 3C | 0 | 0 | 0 | 0.00054452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00054452 | 0.9851% | CZ 3C | 9.9308 | 3.1786 | 1.3766 | 0.059516 | 0 | 0.69529 | 0 | 2.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 24.9369 | 0.9851%
CZ 4A | 0.10408 | 0.032343 | 0.014438 | 0.10416 | 0 | 0.010788 | 0 | 0.024307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.36758 | 19.91% | CZ 4A | 3.3406 | 1.0381 | 0.46341 | 10.6286 | 0 | 0.34628 | 0 | 0.78019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 19.0837 | 19.91% | CZ 4A | 0.97908 | 0.30426 | 0.13582 | 0 | 0 | 0.10149 | 0 | 0.22866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.478 | 19.91% | CZ 4A | 0 | 0 | 0 | 0.10629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10629 | 19.91% | CZ 4A | 10.25 | 3.1853 | 1.4219 | 11.6171 | 0 | 1.0625 | 0 | 2.3938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 37.5597 | 19.91%
CZ 4B | 0.1057 | 0.032178 | 0.014284 | 0.034695 | 0 | 0.013024 | 0 | 0.030231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.30758 | 0.283% | CZ 4B | 3.3929 | 1.0328 | 0.45849 | 3.5403 | 0 | 0.41806 | 0 | 0.97036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.2994 | 0.283% | CZ 4B | 0.9944 | 0.30271 | 0.13438 | 0 | 0 | 0.12252 | 0 | 0.2844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5672 | 0.283% | CZ 4B | 0 | 0 | 0 | 0.035403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035403 | 0.283% | CZ 4B | 10.4104 | 3.1691 | 1.4068 | 3.8696 | 0 | 1.2827 | 0 | 2.9773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 30.7451 | 0.283%
CZ 4C | 0.10846 | 0.032422 | 0.014602 | 0.045552 | 0 | 0.0019749 | 0 | 0.0195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.29997 | 2.916% | CZ 4C | 3.4812 | 1.0407 | 0.4687 | 4.6481 | 0 | 0.063391 | 0 | 0.6259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.8145 | 2.916% | CZ 4C | 1.0203 | 0.305 | 0.13737 | 0 | 0 | 0.018579 | 0 | 0.18344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.3934 | 2.916% | CZ 4C | 0 | 0 | 0 | 0.046481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046481 | 2.916% | CZ 4C | 10.6815 | 3.1931 | 1.4381 | 5.0804 | 0 | 0.1945 | 0 | 1.9204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 30.1372 | 2.916%
CZ 5A | 0.10456 | 0.03228 | 0.014874 | 0.177 | 0 | 0.0044947 | 0 | 0.022536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.43321 | 16.91% | CZ 5A | 3.3561 | 1.0361 | 0.47744 | 18.0616 | 0 | 0.14427 | 0 | 0.72335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 26.2854 | 16.91% | CZ 5A | 0.98362 | 0.30367 | 0.13993 | 0 | 0 | 0.042283 | 0 | 0.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.4102 | 16.91% | CZ 5A | 0 | 0 | 0 | 0.18062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18062 | 16.91% | CZ 5A | 10.2975 | 3.1791 | 1.4649 | 19.7413 | 0 | 0.44266 | 0 | 2.2195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 44.9742 | 16.91%
CZ 5B | 0.10635 | 0.032303 | 0.01475 | 0.088903 | 0 | 0.0072471 | 0 | 0.02841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.35543 | 4.393% | CZ 5B | 3.4137 | 1.0368 | 0.47343 | 9.0717 | 0 | 0.23262 | 0 | 0.91189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 17.6266 | 4.393% | CZ 5B | 1.0005 | 0.30388 | 0.13875 | 0 | 0 | 0.068176 | 0 | 0.26726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5073 | 4.393% | CZ 5B | 0 | 0 | 0 | 0.090717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090717 | 4.393% | CZ 5B | 10.4741 | 3.1814 | 1.4526 | 9.9154 | 0 | 0.71374 | 0 | 2.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 36.1643 | 4.393%
CZ 5C | 0.10765 | 0.032405 | 0.014852 | 0.040802 | 0 | 0.00077182 | 0 | 0.017536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.29148 | 0.0163% | CZ 5C | 3.4554 | 1.0401 | 0.47671 | 4.1635 | 0 | 0.024774 | 0 | 0.56287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.2098 | 0.0163% | CZ 5C | 1.0127 | 0.30484 | 0.13972 | 0 | 0 | 0.0072607 | 0 | 0.16497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.3582 | 0.0163% | CZ 5C | 0 | 0 | 0 | 0.041635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041635 | 0.0163% | CZ 5C | 10.6021 | 3.1914 | 1.4627 | 4.5507 | 0 | 0.076013 | 0 | 1.7271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 29.2392 | 0.0163%
CZ 6A | 0.13402 | 0.03232 | 0.015198 | 0.26858 | 0 | 0.0039783 | 0 | 0.023909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.55548 | 1.997% | CZ 6A | 4.3019 | 1.0374 | 0.48782 | 27.4063 | 0 | 0.12769 | 0 | 0.76744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 36.615 | 1.997% | CZ 6A | 1.2608 | 0.30404 | 0.14297 | 0 | 0 | 0.037425 | 0 | 0.22492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.6989 | 1.997% | CZ 6A | 0 | 0 | 0 | 0.27406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27406 | 1.997% | CZ 6A | 13.1994 | 3.183 | 1.4968 | 29.9551 | 0 | 0.3918 | 0 | 2.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 58.21 | 1.997%
CZ 6B | 0.13459 | 0.032325 | 0.015119 | 0.1612 | 0 | 0.0032348 | 0 | 0.024437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.44837 | 0.1627% | CZ 6B | 4.3199 | 1.0376 | 0.48527 | 16.4492 | 0 | 0.10383 | 0 | 0.78438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 25.6666 | 0.1627% | CZ 6B | 1.2661 | 0.3041 | 0.14223 | 0 | 0 | 0.030431 | 0 | 0.22989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.7015 | 0.1627% | CZ 6B | 0 | 0 | 0 | 0.16449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16449 | 0.1627% | CZ 6B | 13.2547 | 3.1836 | 1.489 | 17.9789 | 0 | 0.31858 | 0 | 2.4067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 46.2607 | 0.1627%
CZ 7 | 0.13434 | 0.032416 | 0.015584 | 0.24639 | 0 | 0.0024346 | 0 | 0.02106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.52969 | 0.1966% | CZ 7 | 4.3119 | 1.0405 | 0.50021 | 25.1421 | 0 | 0.078146 | 0 | 0.67599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 34.2353 | 0.1966% | CZ 7 | 1.2637 | 0.30495 | 0.1466 | 0 | 0 | 0.022903 | 0 | 0.19812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.6651 | 0.1966% | CZ 7 | 0 | 0 | 0 | 0.25142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25142 | 0.1966% | CZ 7 | 13.2301 | 3.1925 | 1.5348 | 27.4803 | 0 | 0.23978 | 0 | 2.0741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 55.3808 | 0.1966%
CZ 8 | 0.13613 | 0.033273 | 0.0161 | 0.25505 | 0 | 0.00066966 | 0 | 0.018336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.53702 | 0.01103% | CZ 8 | 4.3694 | 1.068 | 0.51679 | 26.0251 | 0 | 0.021495 | 0 | 0.58856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 35.0759 | 0.01103% | CZ 8 | 1.2806 | 0.31301 | 0.15146 | 0 | 0 | 0.0062998 | 0 | 0.1725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.6526 | 0.01103% | CZ 8 | 0 | 0 | 0 | 0.26025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26025 | 0.01103% | CZ 8 | 13.4067 | 3.2769 | 1.5856 | 28.4455 | 0 | 0.065952 | 0 | 1.8059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 56.2158 | 0.01103%
US Weighted | 0.10314 | 0.032254 | 0.014068 | 0.067574 | 0 | 0.020065 | 0 | 0.027801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.34237 | 100% | US Weighted | 3.3105 | 1.0353 | 0.45156 | 6.8953 | 0 | 0.64404 | 0 | 0.89236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.7155 | 100% | US Weighted | 0.97026 | 0.30343 | 0.13234 | 0 | 0 | 0.18876 | 0 | 0.26154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 2.5851 | 100% | US Weighted | 0 | 0 | 0 | 0.068953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068953 | 100% | US Weighted | 10.1576 | 3.1766 | 1.3855 | 7.5365 | 0 | 1.9761 | 0 | 2.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 34.5996 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.15494 | 0.047558 | 0.012514 | 0 | 0 | 0.10665 | 0 | 0.050957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.45008 | 0% | CZ 0A | 4.9733 | 1.5265 | 0.40166 | 0 | 0 | 3.4231 | 0 | 1.6356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.4467 | 0% | CZ 0A | 1.4576 | 0.44739 | 0.11772 | 0 | 0 | 1.0033 | 0 | 0.47937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 4.2341 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 15.2595 | 4.6837 | 1.2324 | 0 | 0 | 10.5032 | 0 | 5.0185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 44.3266 | 0%
CZ 0B | 0.15802 | 0.047546 | 0.012491 | 1.7847e-06 | 0 | 0.1156 | 0 | 0.081041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.49216 | 0% | CZ 0B | 5.072 | 1.5261 | 0.40093 | 0.00018211 | 0 | 3.7104 | 0 | 2.6012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.7974 | 0% | CZ 0B | 1.4865 | 0.44728 | 0.11751 | 0 | 0 | 1.0875 | 0 | 0.76238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 4.6299 | 0% | CZ 0B | 0 | 0 | 0 | 1.8211e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8211e-06 | 0% | CZ 0B | 15.5625 | 4.6826 | 1.2302 | 0.00019905 | 0 | 11.3846 | 0 | 7.9813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 48.4706 | 0%
CZ 1A | 0.16583 | 0.047552 | 0.012843 | 0 | 0 | 0.064861 | 0 | 0.034437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.40299 | 2.875% | CZ 1A | 5.3229 | 1.5263 | 0.41223 | 0 | 0 | 2.0819 | 0 | 1.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.9351 | 2.875% | CZ 1A | 1.56 | 0.44734 | 0.12082 | 0 | 0 | 0.61017 | 0 | 0.32396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.7911 | 2.875% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.875% | CZ 1A | 16.3321 | 4.6832 | 1.2648 | 0 | 0 | 6.3879 | 0 | 3.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 39.6887 | 2.875%
CZ 1B | 0.16367 | 0.047484 | 0.01286 | 0.00019454 | 0 | 0.083141 | 0 | 0.051978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.43679 | 0% | CZ 1B | 5.2535 | 1.5241 | 0.41277 | 0.019851 | 0 | 2.6686 | 0 | 1.6684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.0337 | 0% | CZ 1B | 1.5397 | 0.4467 | 0.12098 | 0 | 0 | 0.78213 | 0 | 0.48898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 4.1072 | 0% | CZ 1B | 0 | 0 | 0 | 0.00019851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019851 | 0% | CZ 1B | 16.1192 | 4.6765 | 1.2665 | 0.021697 | 0 | 8.1881 | 0 | 5.1191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 43.0203 | 0%
CZ 2A | 0.16684 | 0.047461 | 0.013234 | 0.00025522 | 0 | 0.046491 | 0 | 0.031338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.38308 | 19% | CZ 2A | 5.3551 | 1.5234 | 0.42479 | 0.026042 | 0 | 1.4922 | 0 | 1.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.3139 | 19% | CZ 2A | 1.5695 | 0.44648 | 0.1245 | 0 | 0 | 0.43735 | 0 | 0.29481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.6014 | 19% | CZ 2A | 0 | 0 | 0 | 0.00026042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026042 | 19% | CZ 2A | 16.431 | 4.6742 | 1.3034 | 0.028464 | 0 | 4.5786 | 0 | 3.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 37.7313 | 19%
CZ 2B | 0.17465 | 0.047506 | 0.013263 | 0.00045511 | 0 | 0.044436 | 0 | 0.043205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.40098 | 3.369% | CZ 2B | 5.6058 | 1.5249 | 0.42571 | 0.046439 | 0 | 1.4263 | 0 | 1.3868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.9023 | 3.369% | CZ 2B | 1.643 | 0.44691 | 0.12477 | 0 | 0 | 0.41803 | 0 | 0.40644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.7678 | 3.369% | CZ 2B | 0 | 0 | 0 | 0.00046439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00046439 | 3.369% | CZ 2B | 17.2001 | 4.6787 | 1.3062 | 0.050758 | 0 | 4.3763 | 0 | 4.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 39.4963 | 3.369%
CZ 3A | 0.17069 | 0.047495 | 0.013904 | 0.028995 | 0 | 0.023172 | 0 | 0.031559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.39328 | 14.95% | CZ 3A | 5.4788 | 1.5245 | 0.44629 | 2.9586 | 0 | 0.74376 | 0 | 1.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.6514 | 14.95% | CZ 3A | 1.6057 | 0.4468 | 0.1308 | 0 | 0 | 0.21798 | 0 | 0.29689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.427 | 14.95% | CZ 3A | 0 | 0 | 0 | 0.029586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029586 | 14.95% | CZ 3A | 16.8105 | 4.6776 | 1.3693 | 3.2338 | 0 | 2.2821 | 0 | 3.1081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 39.1106 | 14.95%
CZ 3B | 0.17207 | 0.047489 | 0.013734 | 0.0033892 | 0 | 0.027496 | 0 | 0.038943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.38059 | 12.03% | CZ 3B | 5.5231 | 1.5243 | 0.44082 | 0.34584 | 0 | 0.88256 | 0 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 12.453 | 12.03% | CZ 3B | 1.6187 | 0.44675 | 0.1292 | 0 | 0 | 0.25866 | 0 | 0.36635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.5484 | 12.03% | CZ 3B | 0 | 0 | 0 | 0.0034584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034584 | 12.03% | CZ 3B | 16.9464 | 4.677 | 1.3526 | 0.378 | 0 | 2.708 | 0 | 3.8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 37.5264 | 12.03%
CZ 3C | 0.17026 | 0.047563 | 0.013972 | 0.00029626 | 0 | 0.0090121 | 0 | 0.023302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.34188 | 0.9851% | CZ 3C | 5.4651 | 1.5267 | 0.44848 | 0.030231 | 0 | 0.28927 | 0 | 0.74795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 10.9942 | 0.9851% | CZ 3C | 1.6017 | 0.44744 | 0.13144 | 0 | 0 | 0.08478 | 0 | 0.21921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.2134 | 0.9851% | CZ 3C | 0 | 0 | 0 | 0.00030231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00030231 | 0.9851% | CZ 3C | 16.7686 | 4.6843 | 1.3761 | 0.033043 | 0 | 0.88756 | 0 | 2.2949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 33.6737 | 0.9851%
CZ 4A | 0.17554 | 0.047575 | 0.014432 | 0.10147 | 0 | 0.012905 | 0 | 0.026599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.45598 | 19.91% | CZ 4A | 5.6344 | 1.527 | 0.46323 | 10.3541 | 0 | 0.41423 | 0 | 0.85378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 21.7333 | 19.91% | CZ 4A | 1.6513 | 0.44755 | 0.13577 | 0 | 0 | 0.1214 | 0 | 0.25023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.335 | 19.91% | CZ 4A | 0 | 0 | 0 | 0.10354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10354 | 19.91% | CZ 4A | 17.2878 | 4.6854 | 1.4213 | 11.3171 | 0 | 1.271 | 0 | 2.6196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 46.2315 | 19.91%
CZ 4B | 0.17804 | 0.047472 | 0.014279 | 0.030342 | 0 | 0.015385 | 0 | 0.033006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.39599 | 0.283% | CZ 4B | 5.7147 | 1.5238 | 0.45831 | 3.0961 | 0 | 0.49383 | 0 | 1.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.8326 | 0.283% | CZ 4B | 1.6749 | 0.44659 | 0.13432 | 0 | 0 | 0.14473 | 0 | 0.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.4398 | 0.283% | CZ 4B | 0 | 0 | 0 | 0.030961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030961 | 0.283% | CZ 4B | 17.5343 | 4.6753 | 1.4062 | 3.3841 | 0 | 1.5152 | 0 | 3.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 39.3951 | 0.283%
CZ 4C | 0.18223 | 0.047563 | 0.014596 | 0.038852 | 0 | 0.0027468 | 0 | 0.021679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.38513 | 2.916% | CZ 4C | 5.8491 | 1.5267 | 0.46851 | 3.9645 | 0 | 0.088165 | 0 | 0.69585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 15.0793 | 2.916% | CZ 4C | 1.7143 | 0.44744 | 0.13731 | 0 | 0 | 0.02584 | 0 | 0.20394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.2576 | 2.916% | CZ 4C | 0 | 0 | 0 | 0.039645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039645 | 2.916% | CZ 4C | 17.9468 | 4.6843 | 1.4375 | 4.3332 | 0 | 0.27052 | 0 | 2.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 38.4366 | 2.916%
CZ 5A | 0.17618 | 0.047501 | 0.014874 | 0.17784 | 0 | 0.005834 | 0 | 0.024653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.52435 | 16.91% | CZ 5A | 5.6549 | 1.5247 | 0.47744 | 18.147 | 0 | 0.18726 | 0 | 0.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 29.2691 | 16.91% | CZ 5A | 1.6574 | 0.44686 | 0.13993 | 0 | 0 | 0.054883 | 0 | 0.23192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.2597 | 16.91% | CZ 5A | 0 | 0 | 0 | 0.18147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18147 | 16.91% | CZ 5A | 17.351 | 4.6781 | 1.4649 | 19.8347 | 0 | 0.57457 | 0 | 2.4279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 53.9605 | 16.91%
CZ 5B | 0.17917 | 0.047552 | 0.014744 | 0.084403 | 0 | 0.0089724 | 0 | 0.030998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.44331 | 4.393% | CZ 5B | 5.7511 | 1.5263 | 0.47325 | 8.6126 | 0 | 0.28799 | 0 | 0.99495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 20.1327 | 4.393% | CZ 5B | 1.6856 | 0.44734 | 0.1387 | 0 | 0 | 0.084406 | 0 | 0.2916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.3763 | 4.393% | CZ 5B | 0 | 0 | 0 | 0.086126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086126 | 4.393% | CZ 5B | 17.6461 | 4.6832 | 1.4521 | 9.4135 | 0 | 0.88365 | 0 | 3.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 44.7606 | 4.393%
CZ 5C | 0.18094 | 0.04754 | 0.014846 | 0.032502 | 0 | 0.0011464 | 0 | 0.019165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.3736 | 0.0163% | CZ 5C | 5.8078 | 1.5259 | 0.47653 | 3.3165 | 0 | 0.036796 | 0 | 0.61515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 14.2652 | 0.0163% | CZ 5C | 1.7022 | 0.44723 | 0.13966 | 0 | 0 | 0.010784 | 0 | 0.18029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.2089 | 0.0163% | CZ 5C | 0 | 0 | 0 | 0.033165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033165 | 0.0163% | CZ 5C | 17.8199 | 4.682 | 1.4621 | 3.6249 | 0 | 0.1129 | 0 | 1.8875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 37.2186 | 0.0163%
CZ 6A | 0.22363 | 0.047529 | 0.015192 | 0.27033 | 0 | 0.0057375 | 0 | 0.026798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.66668 | 1.997% | CZ 6A | 7.1782 | 1.5256 | 0.48764 | 27.5844 | 0 | 0.18416 | 0 | 0.86016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 40.3066 | 1.997% | CZ 6A | 2.1038 | 0.44712 | 0.14292 | 0 | 0 | 0.053975 | 0 | 0.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.7287 | 1.997% | CZ 6A | 0 | 0 | 0 | 0.27584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27584 | 1.997% | CZ 6A | 22.0247 | 4.6809 | 1.4962 | 30.1498 | 0 | 0.56506 | 0 | 2.6392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 69.185 | 1.997%
CZ 6B | 0.2245 | 0.047472 | 0.015113 | 0.15492 | 0 | 0.0045628 | 0 | 0.027377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.55141 | 0.1627% | CZ 6B | 7.2058 | 1.5238 | 0.48509 | 15.8087 | 0 | 0.14646 | 0 | 0.87874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 28.535 | 0.1627% | CZ 6B | 2.1119 | 0.44659 | 0.14217 | 0 | 0 | 0.042924 | 0 | 0.25754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.7299 | 0.1627% | CZ 6B | 0 | 0 | 0 | 0.15809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15809 | 0.1627% | CZ 6B | 22.1096 | 4.6753 | 1.4884 | 17.2789 | 0 | 0.44937 | 0 | 2.6962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 56.327 | 0.1627%
CZ 7 | 0.22415 | 0.04754 | 0.015578 | 0.23203 | 0 | 0.0036775 | 0 | 0.023206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.62365 | 0.1966% | CZ 7 | 7.1947 | 1.5259 | 0.50003 | 23.6766 | 0 | 0.11804 | 0 | 0.74485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 36.2466 | 0.1966% | CZ 7 | 2.1087 | 0.44723 | 0.14655 | 0 | 0 | 0.034595 | 0 | 0.2183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.6841 | 0.1966% | CZ 7 | 0 | 0 | 0 | 0.23677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23677 | 0.1966% | CZ 7 | 22.0755 | 4.682 | 1.5342 | 25.8785 | 0 | 0.36218 | 0 | 2.2854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 64.4471 | 0.1966%
CZ 8 | 0.22687 | 0.047813 | 0.016095 | 0.23956 | 0 | 0.0011293 | 0 | 0.020538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.62947 | 0.01103% | CZ 8 | 7.2822 | 1.5347 | 0.5166 | 24.4446 | 0 | 0.03625 | 0 | 0.65923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 36.96 | 0.01103% | CZ 8 | 2.1343 | 0.44979 | 0.15141 | 0 | 0 | 0.010624 | 0 | 0.19321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.6681 | 0.01103% | CZ 8 | 0 | 0 | 0 | 0.24445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24445 | 0.01103% | CZ 8 | 22.3438 | 4.7089 | 1.5851 | 26.7179 | 0 | 0.11122 | 0 | 2.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 65.1188 | 0.01103%
US Weighted | 0.17399 | 0.047513 | 0.014064 | 0.066139 | 0 | 0.023259 | 0 | 0.030214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077465 | 0.43265 | 100% | US Weighted | 5.5848 | 1.5251 | 0.45141 | 6.7489 | 0 | 0.74656 | 0 | 0.96981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4865 | 18.513 | 100% | US Weighted | 1.6368 | 0.44697 | 0.1323 | 0 | 0 | 0.2188 | 0 | 0.28423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72874 | 3.4479 | 100% | US Weighted | 0 | 0 | 0 | 0.067489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067489 | 100% | US Weighted | 17.1359 | 4.6793 | 1.3851 | 7.3766 | 0 | 2.2907 | 0 | 2.9756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6292 | 43.4723 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.16216 | 0.047558 | 0.012536 | 0 | 0 | 0.12016 | 0 | 0.060366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.48056 | 0% | CZ 0A | 5.2048 | 1.5265 | 0.40239 | 0 | 0 | 3.857 | 0 | 1.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.425 | 0% | CZ 0A | 1.5254 | 0.44739 | 0.11793 | 0 | 0 | 1.1304 | 0 | 0.56789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 4.5208 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 15.9699 | 4.6837 | 1.2346 | 0 | 0 | 11.8345 | 0 | 5.9452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 47.3285 | 0%
CZ 0B | 0.16525 | 0.047546 | 0.012491 | 0 | 0 | 0.11692 | 0 | 0.086245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.50624 | 0% | CZ 0B | 5.3043 | 1.5261 | 0.40093 | 0 | 0 | 3.753 | 0 | 2.7683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 16.2493 | 0% | CZ 0B | 1.5546 | 0.44728 | 0.11751 | 0 | 0 | 1.0999 | 0 | 0.81133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 4.7624 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 16.2751 | 4.6826 | 1.2302 | 0 | 0 | 11.5154 | 0 | 8.4939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 49.8576 | 0%
CZ 1A | 0.17461 | 0.047552 | 0.012865 | 0 | 0 | 0.069231 | 0 | 0.043942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.42599 | 2.875% | CZ 1A | 5.6047 | 1.5263 | 0.41295 | 0 | 0 | 2.2222 | 0 | 1.4105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 13.6732 | 2.875% | CZ 1A | 1.6426 | 0.44734 | 0.12103 | 0 | 0 | 0.65128 | 0 | 0.41338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 4.0074 | 2.875% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.875% | CZ 1A | 17.1967 | 4.6832 | 1.2671 | 0 | 0 | 6.8182 | 0 | 4.3277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 41.9534 | 2.875%
CZ 1B | 0.17184 | 0.047484 | 0.01286 | 0.00026414 | 0 | 0.085064 | 0 | 0.057438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.45273 | 0% | CZ 1B | 5.5156 | 1.5241 | 0.41277 | 0.026953 | 0 | 2.7304 | 0 | 1.8436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 14.5501 | 0% | CZ 1B | 1.6165 | 0.4467 | 0.12098 | 0 | 0 | 0.80023 | 0 | 0.54034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 4.2565 | 0% | CZ 1B | 0 | 0 | 0 | 0.00026953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026953 | 0% | CZ 1B | 16.9234 | 4.6765 | 1.2665 | 0.02946 | 0 | 8.3776 | 0 | 5.6568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 44.5908 | 0%
CZ 2A | 0.176 | 0.047461 | 0.013251 | 0.00023737 | 0 | 0.05031 | 0 | 0.039419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.40446 | 19% | CZ 2A | 5.6493 | 1.5234 | 0.42534 | 0.024221 | 0 | 1.6148 | 0 | 1.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 12.999 | 19% | CZ 2A | 1.6557 | 0.44648 | 0.12466 | 0 | 0 | 0.47328 | 0 | 0.37083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.8027 | 19% | CZ 2A | 0 | 0 | 0 | 0.00024221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00024221 | 19% | CZ 2A | 17.3337 | 4.6742 | 1.3051 | 0.026474 | 0 | 4.9548 | 0 | 3.8822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 39.837 | 19%
CZ 2B | 0.1859 | 0.047506 | 0.013263 | 0.00045332 | 0 | 0.051019 | 0 | 0.050781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.42671 | 3.369% | CZ 2B | 5.967 | 1.5249 | 0.42571 | 0.046257 | 0 | 1.6376 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 13.728 | 3.369% | CZ 2B | 1.7488 | 0.44691 | 0.12477 | 0 | 0 | 0.47996 | 0 | 0.47771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 4.0099 | 3.369% | CZ 2B | 0 | 0 | 0 | 0.00046257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00046257 | 3.369% | CZ 2B | 18.3084 | 4.6787 | 1.3062 | 0.050559 | 0 | 5.0247 | 0 | 5.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 42.0302 | 3.369%
CZ 3A | 0.17852 | 0.047495 | 0.013915 | 0.02887 | 0 | 0.026225 | 0 | 0.034681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.40749 | 14.95% | CZ 3A | 5.7302 | 1.5245 | 0.44665 | 2.9459 | 0 | 0.84176 | 0 | 1.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.0988 | 14.95% | CZ 3A | 1.6794 | 0.4468 | 0.13091 | 0 | 0 | 0.2467 | 0 | 0.32625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.5618 | 14.95% | CZ 3A | 0 | 0 | 0 | 0.029459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029459 | 14.95% | CZ 3A | 17.5818 | 4.6776 | 1.3705 | 3.2199 | 0 | 2.5828 | 0 | 3.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 40.5085 | 14.95%
CZ 3B | 0.18117 | 0.047489 | 0.013734 | 0.0037783 | 0 | 0.030566 | 0 | 0.041411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.39593 | 12.03% | CZ 3B | 5.8151 | 1.5243 | 0.44082 | 0.38554 | 0 | 0.98111 | 0 | 1.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 12.9727 | 12.03% | CZ 3B | 1.7043 | 0.44675 | 0.1292 | 0 | 0 | 0.28755 | 0 | 0.38957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.6891 | 12.03% | CZ 3B | 0 | 0 | 0 | 0.0038554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038554 | 12.03% | CZ 3B | 17.8423 | 4.677 | 1.3526 | 0.42139 | 0 | 3.0103 | 0 | 4.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 39.0425 | 12.03%
CZ 3C | 0.18039 | 0.047563 | 0.013978 | 0.00020167 | 0 | 0.0088418 | 0 | 0.026662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.35542 | 0.9851% | CZ 3C | 5.7901 | 1.5267 | 0.44866 | 0.020579 | 0 | 0.2838 | 0 | 0.85578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 11.4223 | 0.9851% | CZ 3C | 1.697 | 0.44744 | 0.13149 | 0 | 0 | 0.083178 | 0 | 0.25082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.3416 | 0.9851% | CZ 3C | 0 | 0 | 0 | 0.00020579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00020579 | 0.9851% | CZ 3C | 17.7657 | 4.6843 | 1.3766 | 0.022493 | 0 | 0.87079 | 0 | 2.6258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 35.0062 | 0.9851%
CZ 4A | 0.17312 | 0.047575 | 0.014438 | 0.1115 | 0 | 0.015419 | 0 | 0.03102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.47085 | 19.91% | CZ 4A | 5.5568 | 1.527 | 0.46341 | 11.3771 | 0 | 0.49493 | 0 | 0.99568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 22.9116 | 19.91% | CZ 4A | 1.6286 | 0.44755 | 0.13582 | 0 | 0 | 0.14505 | 0 | 0.29182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.3806 | 19.91% | CZ 4A | 0 | 0 | 0 | 0.11377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11377 | 19.91% | CZ 4A | 17.0498 | 4.6854 | 1.4219 | 12.4352 | 0 | 1.5186 | 0 | 3.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 47.8263 | 19.91%
CZ 4B | 0.17583 | 0.047472 | 0.014284 | 0.037235 | 0 | 0.018904 | 0 | 0.039136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.41064 | 0.283% | CZ 4B | 5.6437 | 1.5238 | 0.45849 | 3.7995 | 0 | 0.60677 | 0 | 1.2562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.785 | 0.283% | CZ 4B | 1.6541 | 0.44659 | 0.13438 | 0 | 0 | 0.17783 | 0 | 0.36816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.5128 | 0.283% | CZ 4B | 0 | 0 | 0 | 0.037995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.037995 | 0.283% | CZ 4B | 17.3164 | 4.6753 | 1.4068 | 4.1528 | 0 | 1.8618 | 0 | 3.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 40.9278 | 0.283%
CZ 4C | 0.17999 | 0.047563 | 0.014596 | 0.046294 | 0 | 0.0035924 | 0 | 0.025703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.39552 | 2.916% | CZ 4C | 5.7774 | 1.5267 | 0.46851 | 4.7239 | 0 | 0.11531 | 0 | 0.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.9334 | 2.916% | CZ 4C | 1.6932 | 0.44744 | 0.13731 | 0 | 0 | 0.033794 | 0 | 0.24179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.2853 | 2.916% | CZ 4C | 0 | 0 | 0 | 0.047239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047239 | 2.916% | CZ 4C | 17.7266 | 4.6843 | 1.4375 | 5.1632 | 0 | 0.35379 | 0 | 2.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 39.5573 | 2.916%
CZ 5A | 0.17368 | 0.047501 | 0.014874 | 0.19492 | 0 | 0.006691 | 0 | 0.029471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.54491 | 16.91% | CZ 5A | 5.5746 | 1.5247 | 0.47744 | 19.8895 | 0 | 0.21477 | 0 | 0.94595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 31.1236 | 16.91% | CZ 5A | 1.6338 | 0.44686 | 0.13993 | 0 | 0 | 0.062944 | 0 | 0.27724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.2925 | 16.91% | CZ 5A | 0 | 0 | 0 | 0.19889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19889 | 16.91% | CZ 5A | 17.1045 | 4.6781 | 1.4649 | 21.7392 | 0 | 0.65896 | 0 | 2.9025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 56.2087 | 16.91%
CZ 5B | 0.17705 | 0.047552 | 0.01475 | 0.098594 | 0 | 0.011084 | 0 | 0.037161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.46397 | 4.393% | CZ 5B | 5.6828 | 1.5263 | 0.47343 | 10.0606 | 0 | 0.35576 | 0 | 1.1928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 21.7883 | 4.393% | CZ 5B | 1.6655 | 0.44734 | 0.13875 | 0 | 0 | 0.10427 | 0 | 0.34958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.4372 | 4.393% | CZ 5B | 0 | 0 | 0 | 0.10061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10061 | 4.393% | CZ 5B | 17.4365 | 4.6832 | 1.4526 | 10.9962 | 0 | 1.0916 | 0 | 3.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 46.9804 | 4.393%
CZ 5C | 0.17847 | 0.04754 | 0.014846 | 0.042232 | 0 | 0.0014415 | 0 | 0.022678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.38499 | 0.0163% | CZ 5C | 5.7284 | 1.5259 | 0.47653 | 4.3094 | 0 | 0.046268 | 0 | 0.72791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 15.3111 | 0.0163% | CZ 5C | 1.6789 | 0.44723 | 0.13966 | 0 | 0 | 0.01356 | 0 | 0.21334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.2244 | 0.0163% | CZ 5C | 0 | 0 | 0 | 0.043094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043094 | 0.0163% | CZ 5C | 17.5763 | 4.682 | 1.4621 | 4.7102 | 0 | 0.14196 | 0 | 2.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 38.4665 | 0.0163%
CZ 6A | 0.22526 | 0.047529 | 0.015198 | 0.29741 | 0 | 0.0072585 | 0 | 0.031764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.70221 | 1.997% | CZ 6A | 7.2304 | 1.5256 | 0.48782 | 30.3484 | 0 | 0.23298 | 0 | 1.0195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 43.3414 | 1.997% | CZ 6A | 2.1191 | 0.44712 | 0.14297 | 0 | 0 | 0.068283 | 0 | 0.29881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.808 | 1.997% | CZ 6A | 0 | 0 | 0 | 0.30348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30348 | 1.997% | CZ 6A | 22.1851 | 4.6809 | 1.4968 | 33.1708 | 0 | 0.71485 | 0 | 3.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 73.0372 | 1.997%
CZ 6B | 0.22609 | 0.047472 | 0.015119 | 0.17727 | 0 | 0.0052041 | 0 | 0.03253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.58147 | 0.1627% | CZ 6B | 7.257 | 1.5238 | 0.48527 | 18.0884 | 0 | 0.16704 | 0 | 1.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 31.0623 | 0.1627% | CZ 6B | 2.1269 | 0.44659 | 0.14223 | 0 | 0 | 0.048957 | 0 | 0.30602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.8024 | 0.1627% | CZ 6B | 0 | 0 | 0 | 0.18088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18088 | 0.1627% | CZ 6B | 22.2667 | 4.6753 | 1.489 | 19.7706 | 0 | 0.51253 | 0 | 3.2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 59.5783 | 0.1627%
CZ 7 | 0.22581 | 0.04754 | 0.015578 | 0.2976 | 0 | 0.004699 | 0 | 0.028767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.69778 | 0.1966% | CZ 7 | 7.2479 | 1.5259 | 0.50003 | 30.3678 | 0 | 0.15083 | 0 | 0.92336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 43.2126 | 0.1966% | CZ 7 | 2.1242 | 0.44723 | 0.14655 | 0 | 0 | 0.044205 | 0 | 0.27062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.7646 | 0.1966% | CZ 7 | 0 | 0 | 0 | 0.30368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30368 | 0.1966% | CZ 7 | 22.2387 | 4.682 | 1.5342 | 33.1921 | 0 | 0.46278 | 0 | 2.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 72.6035 | 0.1966%
CZ 8 | 0.22846 | 0.047813 | 0.0161 | 0.33681 | 0 | 0.0011293 | 0 | 0.023932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.73202 | 0.01103% | CZ 8 | 7.333 | 1.5347 | 0.51679 | 34.368 | 0 | 0.03625 | 0 | 0.76816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 47.0536 | 0.01103% | CZ 8 | 2.1492 | 0.44979 | 0.15146 | 0 | 0 | 0.010624 | 0 | 0.22514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.7179 | 0.01103% | CZ 8 | 0 | 0 | 0 | 0.34368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34368 | 0.01103% | CZ 8 | 22.4997 | 4.7089 | 1.5856 | 37.5642 | 0 | 0.11122 | 0 | 2.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 76.4872 | 0.01103%
US Weighted | 0.1777 | 0.047513 | 0.014071 | 0.072624 | 0 | 0.025962 | 0 | 0.035294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077783 | 0.45095 | 100% | US Weighted | 5.7038 | 1.5251 | 0.45164 | 7.4106 | 0 | 0.83334 | 0 | 1.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4967 | 19.554 | 100% | US Weighted | 1.6717 | 0.44697 | 0.13237 | 0 | 0 | 0.24424 | 0 | 0.33203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73173 | 3.559 | 100% | US Weighted | 0 | 0 | 0 | 0.074106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074106 | 100% | US Weighted | 17.501 | 4.6793 | 1.3858 | 8.0998 | 0 | 2.5569 | 0 | 3.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6605 | 45.3592 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.27352 | 0.070173 | 0.012956 | 0 | 0 | 0.18183 | 0 | 0.089281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.7068 | 0% | CZ 0A | 8.7793 | 2.2524 | 0.41587 | 0 | 0 | 5.8364 | 0 | 2.8657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 22.6868 | 0% | CZ 0A | 2.5731 | 0.66014 | 0.12188 | 0 | 0 | 1.7105 | 0 | 0.8399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 6.6491 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 26.9375 | 6.911 | 1.276 | 0 | 0 | 17.9077 | 0 | 8.7929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 69.6097 | 0%
CZ 0B | 0.27352 | 0.070184 | 0.012894 | 0 | 0 | 0.17599 | 0 | 0.10512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.71674 | 0% | CZ 0B | 8.7793 | 2.2528 | 0.41387 | 0 | 0 | 5.6488 | 0 | 3.3741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.006 | 0% | CZ 0B | 2.5731 | 0.66025 | 0.1213 | 0 | 0 | 1.6556 | 0 | 0.9889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 6.7427 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 26.9375 | 6.9121 | 1.2699 | 0 | 0 | 17.332 | 0 | 10.3528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 70.5889 | 0%
CZ 1A | 0.27352 | 0.070196 | 0.013285 | 0 | 0 | 0.11215 | 0 | 0.072874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.62106 | 2.875% | CZ 1A | 8.7793 | 2.2531 | 0.42643 | 0 | 0 | 3.5996 | 0 | 2.3391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 19.9348 | 2.875% | CZ 1A | 2.5731 | 0.66035 | 0.12498 | 0 | 0 | 1.055 | 0 | 0.68555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 5.8425 | 2.875% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.875% | CZ 1A | 26.9375 | 6.9132 | 1.3084 | 0 | 0 | 11.0448 | 0 | 7.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 61.1656 | 2.875%
CZ 1B | 0.27352 | 0.070105 | 0.013268 | 0.00088165 | 0 | 0.13119 | 0 | 0.093503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.66151 | 0% | CZ 1B | 8.7793 | 2.2502 | 0.42589 | 0.089965 | 0 | 4.2108 | 0 | 3.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 21.2946 | 0% | CZ 1B | 2.5731 | 0.6595 | 0.12482 | 0 | 0 | 1.2341 | 0 | 0.87962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 6.2147 | 0% | CZ 1B | 0 | 0 | 0 | 0.00089965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00089965 | 0% | CZ 1B | 26.9375 | 6.9043 | 1.3067 | 0.098331 | 0 | 12.9199 | 0 | 9.2087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 65.1601 | 0%
CZ 2A | 0.27352 | 0.070082 | 0.013677 | 0.00053542 | 0 | 0.071365 | 0 | 0.041741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.54996 | 19% | CZ 2A | 8.7793 | 2.2495 | 0.439 | 0.054634 | 0 | 2.2907 | 0 | 1.3398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 17.69 | 19% | CZ 2A | 2.5731 | 0.65929 | 0.12866 | 0 | 0 | 0.67135 | 0 | 0.39267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 5.1686 | 19% | CZ 2A | 0 | 0 | 0 | 0.00054634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00054634 | 19% | CZ 2A | 26.9375 | 6.9021 | 1.347 | 0.059715 | 0 | 7.0284 | 0 | 4.1108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 54.1701 | 19%
CZ 2B | 0.27352 | 0.070133 | 0.013677 | 0.00074959 | 0 | 0.0712 | 0 | 0.075053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.58337 | 3.369% | CZ 2B | 8.7793 | 2.2511 | 0.439 | 0.076488 | 0 | 2.2854 | 0 | 2.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 18.7775 | 3.369% | CZ 2B | 2.5731 | 0.65977 | 0.12866 | 0 | 0 | 0.6698 | 0 | 0.70605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 5.4809 | 3.369% | CZ 2B | 0 | 0 | 0 | 0.00076488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00076488 | 3.369% | CZ 2B | 26.9375 | 6.9071 | 1.347 | 0.083602 | 0 | 7.0122 | 0 | 7.3917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 57.4637 | 3.369%
CZ 3A | 0.27352 | 0.070116 | 0.014364 | 0.039421 | 0 | 0.037694 | 0 | 0.038069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.55222 | 14.95% | CZ 3A | 8.7793 | 2.2506 | 0.46104 | 4.0226 | 0 | 1.2099 | 0 | 1.2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.4824 | 14.95% | CZ 3A | 2.5731 | 0.65961 | 0.13512 | 0 | 0 | 0.3546 | 0 | 0.35813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.8241 | 14.95% | CZ 3A | 0 | 0 | 0 | 0.040226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040226 | 14.95% | CZ 3A | 26.9375 | 6.9054 | 1.4146 | 4.3967 | 0 | 3.7123 | 0 | 3.7492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 54.9004 | 14.95%
CZ 3B | 0.27352 | 0.070116 | 0.014165 | 0.0068498 | 0 | 0.04064 | 0 | 0.045821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.53015 | 12.03% | CZ 3B | 8.7793 | 2.2506 | 0.45467 | 0.69896 | 0 | 1.3044 | 0 | 1.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 17.4958 | 12.03% | CZ 3B | 2.5731 | 0.65961 | 0.13326 | 0 | 0 | 0.38231 | 0 | 0.43105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.9229 | 12.03% | CZ 3B | 0 | 0 | 0 | 0.0069896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0069896 | 12.03% | CZ 3B | 26.9375 | 6.9054 | 1.3951 | 0.76396 | 0 | 4.0024 | 0 | 4.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 52.3017 | 12.03%
CZ 3C | 0.27352 | 0.070105 | 0.014415 | 0.00058182 | 0 | 0.012372 | 0 | 0.027377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.47741 | 0.9851% | CZ 3C | 8.7793 | 2.2502 | 0.46268 | 0.059369 | 0 | 0.39711 | 0 | 0.87874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 15.3646 | 0.9851% | CZ 3C | 2.5731 | 0.6595 | 0.1356 | 0 | 0 | 0.11639 | 0 | 0.25754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.4857 | 0.9851% | CZ 3C | 0 | 0 | 0 | 0.00059369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00059369 | 0.9851% | CZ 3C | 26.9375 | 6.9043 | 1.4196 | 0.064891 | 0 | 1.2184 | 0 | 2.6962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 47.0256 | 0.9851%
CZ 4A | 0.27352 | 0.070008 | 0.014903 | 0.13556 | 0 | 0.021923 | 0 | 0.035015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.62998 | 19.91% | CZ 4A | 8.7793 | 2.2471 | 0.47835 | 13.8331 | 0 | 0.70368 | 0 | 1.1239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 29.7026 | 19.91% | CZ 4A | 2.5731 | 0.65859 | 0.1402 | 0 | 0 | 0.20624 | 0 | 0.3294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.6511 | 19.91% | CZ 4A | 0 | 0 | 0 | 0.13833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13833 | 19.91% | CZ 4A | 26.9375 | 6.8948 | 1.4677 | 15.1196 | 0 | 2.1591 | 0 | 3.4485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 63.8118 | 19.91%
CZ 4B | 0.27352 | 0.070065 | 0.014744 | 0.04399 | 0 | 0.023126 | 0 | 0.042677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.54716 | 0.283% | CZ 4B | 8.7793 | 2.2489 | 0.47325 | 4.4888 | 0 | 0.7423 | 0 | 1.3698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.6395 | 0.283% | CZ 4B | 2.5731 | 0.65913 | 0.1387 | 0 | 0 | 0.21756 | 0 | 0.40148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.7335 | 0.283% | CZ 4B | 0 | 0 | 0 | 0.044888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044888 | 0.283% | CZ 4B | 26.9375 | 6.9004 | 1.4521 | 4.9062 | 0 | 2.2776 | 0 | 4.2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 54.4614 | 0.283%
CZ 4C | 0.27352 | 0.069929 | 0.015067 | 0.054152 | 0 | 0.0038591 | 0 | 0.027099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.52267 | 2.916% | CZ 4C | 8.7793 | 2.2446 | 0.48363 | 5.5257 | 0 | 0.12387 | 0 | 0.86981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 20.5641 | 2.916% | CZ 4C | 2.5731 | 0.65784 | 0.14174 | 0 | 0 | 0.036304 | 0 | 0.25493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.4075 | 2.916% | CZ 4C | 0 | 0 | 0 | 0.055257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055257 | 2.916% | CZ 4C | 26.9375 | 6.887 | 1.4839 | 6.0396 | 0 | 0.38006 | 0 | 2.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 52.1815 | 2.916%
CZ 5A | 0.27352 | 0.070031 | 0.015346 | 0.23554 | 0 | 0.009381 | 0 | 0.033773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.71663 | 16.91% | CZ 5A | 8.7793 | 2.2478 | 0.49256 | 24.0346 | 0 | 0.30111 | 0 | 1.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 39.4766 | 16.91% | CZ 5A | 2.5731 | 0.65881 | 0.14436 | 0 | 0 | 0.08825 | 0 | 0.31771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.5258 | 16.91% | CZ 5A | 0 | 0 | 0 | 0.24035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24035 | 16.91% | CZ 5A | 26.9375 | 6.897 | 1.5113 | 26.2698 | 0 | 0.92389 | 0 | 3.3261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 73.6503 | 16.91%
CZ 5B | 0.27352 | 0.070037 | 0.015215 | 0.1185 | 0 | 0.015754 | 0 | 0.041434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.6135 | 4.393% | CZ 5B | 8.7793 | 2.248 | 0.48837 | 12.0917 | 0 | 0.50567 | 0 | 1.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 27.9802 | 4.393% | CZ 5B | 2.5731 | 0.65886 | 0.14313 | 0 | 0 | 0.1482 | 0 | 0.38978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.6566 | 4.393% | CZ 5B | 0 | 0 | 0 | 0.12092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12092 | 4.393% | CZ 5B | 26.9375 | 6.8976 | 1.4985 | 13.2162 | 0 | 1.5516 | 0 | 4.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 61.9666 | 4.393%
CZ 5C | 0.27352 | 0.069923 | 0.015317 | 0.049151 | 0 | 0.001572 | 0 | 0.024244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.51277 | 0.0163% | CZ 5C | 8.7793 | 2.2444 | 0.49165 | 5.0154 | 0 | 0.050458 | 0 | 0.77818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 19.8966 | 0.0163% | CZ 5C | 2.5731 | 0.65779 | 0.14409 | 0 | 0 | 0.014788 | 0 | 0.22807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.3614 | 0.0163% | CZ 5C | 0 | 0 | 0 | 0.050154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050154 | 0.0163% | CZ 5C | 26.9375 | 6.8864 | 1.5085 | 5.4819 | 0 | 0.15482 | 0 | 2.3877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 51.1415 | 0.0163%
CZ 6A | 0.27352 | 0.070003 | 0.015669 | 0.38386 | 0 | 0.011055 | 0 | 0.040815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.87397 | 1.997% | CZ 6A | 8.7793 | 2.2469 | 0.50294 | 39.1696 | 0 | 0.35485 | 0 | 1.3101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 54.9009 | 1.997% | CZ 6A | 2.5731 | 0.65854 | 0.1474 | 0 | 0 | 0.104 | 0 | 0.38396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.6106 | 1.997% | CZ 6A | 0 | 0 | 0 | 0.3917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3917 | 1.997% | CZ 6A | 26.9375 | 6.8942 | 1.5432 | 42.8124 | 0 | 1.0888 | 0 | 4.0197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 91.0805 | 1.997%
CZ 6B | 0.27352 | 0.069952 | 0.01559 | 0.23392 | 0 | 0.0082119 | 0 | 0.039964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.72019 | 0.1627% | CZ 6B | 8.7793 | 2.2453 | 0.50039 | 23.8689 | 0 | 0.26358 | 0 | 1.2828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 39.4774 | 0.1627% | CZ 6B | 2.5731 | 0.65806 | 0.14666 | 0 | 0 | 0.077252 | 0 | 0.37596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.5746 | 0.1627% | CZ 6B | 0 | 0 | 0 | 0.23869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23869 | 0.1627% | CZ 6B | 26.9375 | 6.8892 | 1.5353 | 26.0887 | 0 | 0.80875 | 0 | 3.9359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 73.98 | 0.1627%
CZ 7 | 0.27352 | 0.069906 | 0.016049 | 0.3876 | 0 | 0.0059532 | 0 | 0.033353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.86542 | 0.1966% | CZ 7 | 8.7793 | 2.2438 | 0.51515 | 39.5512 | 0 | 0.19108 | 0 | 1.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 54.8882 | 0.1966% | CZ 7 | 2.5731 | 0.65763 | 0.15098 | 0 | 0 | 0.056004 | 0 | 0.31376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.495 | 0.1966% | CZ 7 | 0 | 0 | 0 | 0.39551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39551 | 0.1966% | CZ 7 | 26.9375 | 6.8847 | 1.5806 | 43.2294 | 0 | 0.5863 | 0 | 3.2848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 90.288 | 0.1966%
CZ 8 | 0.27352 | 0.06952 | 0.016577 | 0.41058 | 0 | 0.0012485 | 0 | 0.027036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.87752 | 0.01103% | CZ 8 | 8.7793 | 2.2314 | 0.53209 | 41.8961 | 0 | 0.040075 | 0 | 0.86781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 56.884 | 0.01103% | CZ 8 | 2.5731 | 0.654 | 0.15595 | 0 | 0 | 0.011745 | 0 | 0.25434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.3927 | 0.01103% | CZ 8 | 0 | 0 | 0 | 0.41896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41896 | 0.01103% | CZ 8 | 26.9375 | 6.8467 | 1.6326 | 45.7924 | 0 | 0.12296 | 0 | 2.6627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 91.7795 | 0.01103%
US Weighted | 0.27352 | 0.070064 | 0.01452 | 0.089428 | 0 | 0.036896 | 0 | 0.040392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.60386 | 100% | US Weighted | 8.7793 | 2.2489 | 0.46605 | 9.1253 | 0 | 1.1843 | 0 | 1.2965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 25.6375 | 100% | US Weighted | 2.5731 | 0.65912 | 0.13659 | 0 | 0 | 0.34709 | 0 | 0.37999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.8394 | 100% | US Weighted | 0 | 0 | 0 | 0.091253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091253 | 100% | US Weighted | 26.9375 | 6.9003 | 1.43 | 9.9739 | 0 | 3.6337 | 0 | 3.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 60.6381 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 52045 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.27352 | 0.070173 | 0.012956 | 0.0098499 | 0 | 0.18091 | 0 | 0.094338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.72078 | 0% | CZ 0A | 8.7793 | 2.2524 | 0.41587 | 1.0051 | 0 | 5.8067 | 0 | 3.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 23.8245 | 0% | CZ 0A | 2.5731 | 0.66014 | 0.12188 | 0 | 0 | 1.7018 | 0 | 0.88746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 6.688 | 0% | CZ 0A | 0 | 0 | 0 | 0.010051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010051 | 0% | CZ 0A | 26.9375 | 6.911 | 1.276 | 1.0986 | 0 | 17.8166 | 0 | 9.2909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 71.1152 | 0%
CZ 0B | 0.27352 | 0.070184 | 0.012894 | 0.012664 | 0 | 0.17595 | 0 | 0.1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.73585 | 0% | CZ 0B | 8.7793 | 2.2528 | 0.41387 | 1.2923 | 0 | 5.6475 | 0 | 3.5822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 24.505 | 0% | CZ 0B | 2.5731 | 0.66025 | 0.1213 | 0 | 0 | 1.6552 | 0 | 1.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 6.8033 | 0% | CZ 0B | 0 | 0 | 0 | 0.012923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012923 | 0% | CZ 0B | 26.9375 | 6.9121 | 1.2699 | 1.4125 | 0 | 17.3281 | 0 | 10.9911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 72.6358 | 0%
CZ 1A | 0.27352 | 0.070196 | 0.013285 | 0.0098499 | 0 | 0.11274 | 0 | 0.077142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.63578 | 2.875% | CZ 1A | 8.7793 | 2.2531 | 0.42643 | 1.0051 | 0 | 3.6188 | 0 | 2.4761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 21.096 | 2.875% | CZ 1A | 2.5731 | 0.66035 | 0.12498 | 0 | 0 | 1.0606 | 0 | 0.7257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 5.8883 | 2.875% | CZ 1A | 0 | 0 | 0 | 0.010051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010051 | 2.875% | CZ 1A | 26.9375 | 6.9132 | 1.3084 | 1.0986 | 0 | 11.1034 | 0 | 7.5974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 62.7432 | 2.875%
CZ 1B | 0.27352 | 0.070105 | 0.013268 | 0.013543 | 0 | 0.13109 | 0 | 0.099275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.67984 | 0% | CZ 1B | 8.7793 | 2.2502 | 0.42589 | 1.3819 | 0 | 4.2077 | 0 | 3.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 22.7686 | 0% | CZ 1B | 2.5731 | 0.6595 | 0.12482 | 0 | 0 | 1.2332 | 0 | 0.93391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 6.2681 | 0% | CZ 1B | 0 | 0 | 0 | 0.013819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013819 | 0% | CZ 1B | 26.9375 | 6.9043 | 1.3067 | 1.5104 | 0 | 12.9104 | 0 | 9.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 67.1311 | 0%
CZ 2A | 0.27352 | 0.070082 | 0.013677 | 0.017469 | 0 | 0.071041 | 0 | 0.041939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.56677 | 19% | CZ 2A | 8.7793 | 2.2495 | 0.439 | 1.7825 | 0 | 2.2803 | 0 | 1.3462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 19.4139 | 19% | CZ 2A | 2.5731 | 0.65929 | 0.12866 | 0 | 0 | 0.66831 | 0 | 0.39454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 5.1675 | 19% | CZ 2A | 0 | 0 | 0 | 0.017825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017825 | 19% | CZ 2A | 26.9375 | 6.9021 | 1.347 | 1.9483 | 0 | 6.9965 | 0 | 4.1304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 56.0464 | 19%
CZ 2B | 0.27352 | 0.070133 | 0.013683 | 0.010678 | 0 | 0.072063 | 0 | 0.080121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.59924 | 3.369% | CZ 2B | 8.7793 | 2.2511 | 0.43919 | 1.0896 | 0 | 2.3131 | 0 | 2.5717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 19.9811 | 3.369% | CZ 2B | 2.5731 | 0.65977 | 0.12872 | 0 | 0 | 0.67792 | 0 | 0.75373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 5.5368 | 3.369% | CZ 2B | 0 | 0 | 0 | 0.010896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010896 | 3.369% | CZ 2B | 26.9375 | 6.9071 | 1.3475 | 1.1909 | 0 | 7.0971 | 0 | 7.8908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 59.1556 | 3.369%
CZ 3A | 0.27352 | 0.070116 | 0.014364 | 0.061412 | 0 | 0.038137 | 0 | 0.038341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.57493 | 14.95% | CZ 3A | 8.7793 | 2.2506 | 0.46104 | 6.2666 | 0 | 1.2241 | 0 | 1.2307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 22.7494 | 14.95% | CZ 3A | 2.5731 | 0.65961 | 0.13512 | 0 | 0 | 0.35877 | 0 | 0.36069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.8308 | 14.95% | CZ 3A | 0 | 0 | 0 | 0.062666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062666 | 14.95% | CZ 3A | 26.9375 | 6.9054 | 1.4146 | 6.8494 | 0 | 3.7559 | 0 | 3.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 57.4235 | 14.95%
CZ 3B | 0.27352 | 0.070116 | 0.014165 | 0.019636 | 0 | 0.041048 | 0 | 0.046133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.54366 | 12.03% | CZ 3B | 8.7793 | 2.2506 | 0.45467 | 2.0036 | 0 | 1.3176 | 0 | 1.4808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 18.8237 | 12.03% | CZ 3B | 2.5731 | 0.65961 | 0.13326 | 0 | 0 | 0.38615 | 0 | 0.43399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.9297 | 12.03% | CZ 3B | 0 | 0 | 0 | 0.020036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020036 | 12.03% | CZ 3B | 26.9375 | 6.9054 | 1.3951 | 2.19 | 0 | 4.0426 | 0 | 4.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 53.7986 | 12.03%
CZ 3C | 0.27352 | 0.070105 | 0.014415 | 0.011818 | 0 | 0.011078 | 0 | 0.029584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.48956 | 0.9851% | CZ 3C | 8.7793 | 2.2502 | 0.46268 | 1.206 | 0 | 0.35557 | 0 | 0.9496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 16.5405 | 0.9851% | CZ 3C | 2.5731 | 0.6595 | 0.1356 | 0 | 0 | 0.10421 | 0 | 0.27831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.4943 | 0.9851% | CZ 3C | 0 | 0 | 0 | 0.01206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01206 | 0.9851% | CZ 3C | 26.9375 | 6.9043 | 1.4196 | 1.3181 | 0 | 1.091 | 0 | 2.9136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 48.3688 | 0.9851%
CZ 4A | 0.27352 | 0.070008 | 0.014903 | 0.16242 | 0 | 0.021923 | 0 | 0.035033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.65685 | 19.91% | CZ 4A | 8.7793 | 2.2471 | 0.47835 | 16.5736 | 0 | 0.70368 | 0 | 1.1245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 32.4436 | 19.91% | CZ 4A | 2.5731 | 0.65859 | 0.1402 | 0 | 0 | 0.20624 | 0 | 0.32956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.6512 | 19.91% | CZ 4A | 0 | 0 | 0 | 0.16574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16574 | 19.91% | CZ 4A | 26.9375 | 6.8948 | 1.4677 | 18.1149 | 0 | 2.1591 | 0 | 3.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 66.8088 | 19.91%
CZ 4B | 0.27352 | 0.070065 | 0.014744 | 0.065157 | 0 | 0.023081 | 0 | 0.042666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.56827 | 0.283% | CZ 4B | 8.7793 | 2.2489 | 0.47325 | 6.6487 | 0 | 0.74084 | 0 | 1.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 22.7976 | 0.283% | CZ 4B | 2.5731 | 0.65913 | 0.1387 | 0 | 0 | 0.21713 | 0 | 0.40137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.733 | 0.283% | CZ 4B | 0 | 0 | 0 | 0.066487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066487 | 0.283% | CZ 4B | 26.9375 | 6.9004 | 1.4521 | 7.267 | 0 | 2.2731 | 0 | 4.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 56.8166 | 0.283%
CZ 4C | 0.27352 | 0.069929 | 0.015067 | 0.071462 | 0 | 0.0042677 | 0 | 0.027104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.54039 | 2.916% | CZ 4C | 8.7793 | 2.2446 | 0.48363 | 7.2921 | 0 | 0.13698 | 0 | 0.86999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 22.3437 | 2.916% | CZ 4C | 2.5731 | 0.65784 | 0.14174 | 0 | 0 | 0.040148 | 0 | 0.25498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.4114 | 2.916% | CZ 4C | 0 | 0 | 0 | 0.072921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072921 | 2.916% | CZ 4C | 26.9375 | 6.887 | 1.4839 | 7.9702 | 0 | 0.42031 | 0 | 2.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 54.1529 | 2.916%
CZ 5A | 0.27352 | 0.070031 | 0.015346 | 0.26159 | 0 | 0.010051 | 0 | 0.034204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.74378 | 16.91% | CZ 5A | 8.7793 | 2.2478 | 0.49256 | 26.6924 | 0 | 0.3226 | 0 | 1.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 42.1697 | 16.91% | CZ 5A | 2.5731 | 0.65881 | 0.14436 | 0 | 0 | 0.09455 | 0 | 0.32177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.5361 | 16.91% | CZ 5A | 0 | 0 | 0 | 0.26692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26692 | 16.91% | CZ 5A | 26.9375 | 6.897 | 1.5113 | 29.1748 | 0 | 0.98984 | 0 | 3.3686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 76.6637 | 16.91%
CZ 5B | 0.27352 | 0.070037 | 0.015215 | 0.14389 | 0 | 0.01601 | 0 | 0.041899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.63961 | 4.393% | CZ 5B | 8.7793 | 2.248 | 0.48837 | 14.6828 | 0 | 0.51387 | 0 | 1.3449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 30.5944 | 4.393% | CZ 5B | 2.5731 | 0.65886 | 0.14313 | 0 | 0 | 0.15061 | 0 | 0.39416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.6634 | 4.393% | CZ 5B | 0 | 0 | 0 | 0.14683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14683 | 4.393% | CZ 5B | 26.9375 | 6.8976 | 1.4985 | 16.0483 | 0 | 1.5767 | 0 | 4.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 64.8697 | 4.393%
CZ 5C | 0.27352 | 0.069923 | 0.015317 | 0.067498 | 0 | 0.0018444 | 0 | 0.024539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.53168 | 0.0163% | CZ 5C | 8.7793 | 2.2444 | 0.49165 | 6.8876 | 0 | 0.059202 | 0 | 0.78766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 21.7869 | 0.0163% | CZ 5C | 2.5731 | 0.65779 | 0.14409 | 0 | 0 | 0.017351 | 0 | 0.23085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.3667 | 0.0163% | CZ 5C | 0 | 0 | 0 | 0.068876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068876 | 0.0163% | CZ 5C | 26.9375 | 6.8864 | 1.5085 | 7.5281 | 0 | 0.18165 | 0 | 2.4168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 53.2436 | 0.0163%
CZ 6A | 0.27352 | 0.070003 | 0.015669 | 0.40793 | 0 | 0.011288 | 0 | 0.041264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.89871 | 1.997% | CZ 6A | 8.7793 | 2.2469 | 0.50294 | 41.6251 | 0 | 0.36231 | 0 | 1.3245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 57.3782 | 1.997% | CZ 6A | 2.5731 | 0.65854 | 0.1474 | 0 | 0 | 0.10619 | 0 | 0.38818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.617 | 1.997% | CZ 6A | 0 | 0 | 0 | 0.41625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41625 | 1.997% | CZ 6A | 26.9375 | 6.8942 | 1.5432 | 45.4962 | 0 | 1.1117 | 0 | 4.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 93.8313 | 1.997%
CZ 6B | 0.27352 | 0.069952 | 0.01559 | 0.26733 | 0 | 0.0083878 | 0 | 0.040475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.7543 | 0.1627% | CZ 6B | 8.7793 | 2.2453 | 0.50039 | 27.2788 | 0 | 0.26923 | 0 | 1.2992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 42.9093 | 0.1627% | CZ 6B | 2.5731 | 0.65806 | 0.14666 | 0 | 0 | 0.078907 | 0 | 0.38076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.581 | 0.1627% | CZ 6B | 0 | 0 | 0 | 0.27279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27279 | 0.1627% | CZ 6B | 26.9375 | 6.8892 | 1.5353 | 29.8157 | 0 | 0.82608 | 0 | 3.9862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 77.7747 | 0.1627%
CZ 7 | 0.27352 | 0.069906 | 0.016055 | 0.41164 | 0 | 0.0066853 | 0 | 0.033767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.89061 | 0.1966% | CZ 7 | 8.7793 | 2.2438 | 0.51533 | 42.0041 | 0 | 0.21458 | 0 | 1.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 57.3781 | 0.1966% | CZ 7 | 2.5731 | 0.65763 | 0.15103 | 0 | 0 | 0.062891 | 0 | 0.31766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.5059 | 0.1966% | CZ 7 | 0 | 0 | 0 | 0.42004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42004 | 0.1966% | CZ 7 | 26.9375 | 6.8847 | 1.5812 | 45.9105 | 0 | 0.6584 | 0 | 3.3256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 93.0825 | 0.1966%
CZ 8 | 0.27352 | 0.06952 | 0.016577 | 0.4319 | 0 | 0.0014301 | 0 | 0.027212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.8992 | 0.01103% | CZ 8 | 8.7793 | 2.2314 | 0.53209 | 44.0713 | 0 | 0.045904 | 0 | 0.87345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 59.0706 | 0.01103% | CZ 8 | 2.5731 | 0.654 | 0.15595 | 0 | 0 | 0.013454 | 0 | 0.25599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.3961 | 0.01103% | CZ 8 | 0 | 0 | 0 | 0.44071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44071 | 0.01103% | CZ 8 | 26.9375 | 6.8467 | 1.6326 | 48.1699 | 0 | 0.14085 | 0 | 2.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 94.1922 | 0.01103%
US Weighted | 0.27352 | 0.070064 | 0.01452 | 0.11022 | 0 | 0.037126 | 0 | 0.040931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079043 | 0.62542 | 100% | US Weighted | 8.7793 | 2.2489 | 0.46606 | 11.2466 | 0 | 1.1916 | 0 | 1.3138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5371 | 27.7835 | 100% | US Weighted | 2.5731 | 0.65912 | 0.13659 | 0 | 0 | 0.34925 | 0 | 0.38505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74358 | 4.8467 | 100% | US Weighted | 0 | 0 | 0 | 0.11247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11247 | 100% | US Weighted | 26.9375 | 6.9003 | 1.43 | 12.2926 | 0 | 3.6563 | 0 | 4.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7846 | 63.0325 | 100%
Building Type: | Warehouse |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Warehouse |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 52045 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 52045 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 52045 | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.18468 | 0.037938 | 0.00044266 | 0.0098499 | 0 | 0.086858 | 0 | 0.04892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.37027 | 0% | CZ 0A | 5.9278 | 1.2177 | 0.014208 | 1.0051 | 0 | 2.7879 | 0 | 1.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 12.5737 | 0% | CZ 0A | 1.7373 | 0.3569 | 0.0041642 | 0 | 0 | 0.8171 | 0 | 0.4602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 3.3906 | 0% | CZ 0A | 0 | 0 | 0 | 0.010051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010051 | 0% | CZ 0A | 18.1883 | 3.7364 | 0.043595 | 1.0986 | 0 | 8.5542 | 0 | 4.8179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 36.5942 | 0%
CZ 0B | 0.18254 | 0.037967 | 0.00039726 | 0.012661 | 0 | 0.077545 | 0 | 0.055843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.36853 | 0% | CZ 0B | 5.8591 | 1.2186 | 0.012751 | 1.2919 | 0 | 2.489 | 0 | 1.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 12.7146 | 0% | CZ 0B | 1.7172 | 0.35716 | 0.0037371 | 0 | 0 | 0.72949 | 0 | 0.52534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 3.3478 | 0% | CZ 0B | 0 | 0 | 0 | 0.012919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012919 | 0% | CZ 0B | 17.9776 | 3.7392 | 0.039124 | 1.4121 | 0 | 7.637 | 0 | 5.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 36.4601 | 0%
CZ 1A | 0.18074 | 0.037967 | 0.00043698 | 0.0098499 | 0 | 0.059453 | 0 | 0.042864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.33289 | 2.875% | CZ 1A | 5.8014 | 1.2186 | 0.014026 | 1.0051 | 0 | 1.9083 | 0 | 1.3758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 11.374 | 2.875% | CZ 1A | 1.7003 | 0.35716 | 0.0041109 | 0 | 0 | 0.55929 | 0 | 0.40324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 3.0389 | 2.875% | CZ 1A | 0 | 0 | 0 | 0.010051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010051 | 2.875% | CZ 1A | 17.8004 | 3.7392 | 0.043037 | 1.0986 | 0 | 5.8552 | 0 | 4.2215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 32.9132 | 2.875%
CZ 1B | 0.18173 | 0.037927 | 0.00040861 | 0.013191 | 0 | 0.062631 | 0 | 0.051286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.34876 | 0% | CZ 1B | 5.8333 | 1.2174 | 0.013115 | 1.346 | 0 | 2.0103 | 0 | 1.6462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 12.1169 | 0% | CZ 1B | 1.7096 | 0.35679 | 0.0038439 | 0 | 0 | 0.58919 | 0 | 0.48247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 3.1568 | 0% | CZ 1B | 0 | 0 | 0 | 0.01346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01346 | 0% | CZ 1B | 17.8982 | 3.7352 | 0.040242 | 1.4712 | 0 | 6.1682 | 0 | 5.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 34.5194 | 0%
CZ 2A | 0.18033 | 0.03791 | 0.00043698 | 0.017158 | 0 | 0.032325 | 0 | 0.010113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.27985 | 19% | CZ 2A | 5.7883 | 1.2168 | 0.014026 | 1.7509 | 0 | 1.0376 | 0 | 0.32461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.1828 | 19% | CZ 2A | 1.6964 | 0.35663 | 0.0041109 | 0 | 0 | 0.3041 | 0 | 0.095137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.4713 | 19% | CZ 2A | 0 | 0 | 0 | 0.017509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017509 | 19% | CZ 2A | 17.7601 | 3.7336 | 0.043037 | 1.9137 | 0 | 3.1836 | 0 | 0.99599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 27.7854 | 19%
CZ 2B | 0.17597 | 0.037927 | 0.00041428 | 0.0099731 | 0 | 0.033375 | 0 | 0.04031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.29955 | 3.369% | CZ 2B | 5.6484 | 1.2174 | 0.013298 | 1.0177 | 0 | 1.0713 | 0 | 1.2939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.3125 | 3.369% | CZ 2B | 1.6554 | 0.35679 | 0.0038973 | 0 | 0 | 0.31397 | 0 | 0.37921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.7242 | 3.369% | CZ 2B | 0 | 0 | 0 | 0.010177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010177 | 3.369% | CZ 2B | 17.3309 | 3.7352 | 0.040801 | 1.1123 | 0 | 3.287 | 0 | 3.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 29.6316 | 3.369%
CZ 3A | 0.17831 | 0.037881 | 0.00045401 | 0.030235 | 0 | 0.018682 | 0 | 0.0097158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.27685 | 14.95% | CZ 3A | 5.7233 | 1.2159 | 0.014573 | 3.0852 | 0 | 0.59967 | 0 | 0.31186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 11.0011 | 14.95% | CZ 3A | 1.6774 | 0.35636 | 0.004271 | 0 | 0 | 0.17575 | 0 | 0.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.32 | 14.95% | CZ 3A | 0 | 0 | 0 | 0.030852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030852 | 14.95% | CZ 3A | 17.5606 | 3.7308 | 0.044713 | 3.3721 | 0 | 1.84 | 0 | 0.95687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 27.6604 | 14.95%
CZ 3B | 0.17741 | 0.037944 | 0.00042563 | 0.014139 | 0 | 0.017695 | 0 | 0.010664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.25985 | 12.03% | CZ 3B | 5.6945 | 1.2179 | 0.013662 | 1.4427 | 0 | 0.56797 | 0 | 0.34228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 9.3297 | 12.03% | CZ 3B | 1.669 | 0.35695 | 0.0040041 | 0 | 0 | 0.16646 | 0 | 0.10032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.3115 | 12.03% | CZ 3B | 0 | 0 | 0 | 0.014427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014427 | 12.03% | CZ 3B | 17.4723 | 3.7369 | 0.041919 | 1.5769 | 0 | 1.7427 | 0 | 1.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 25.7763 | 12.03%
CZ 3C | 0.17825 | 0.03783 | 0.00043698 | 0.011187 | 0 | 0.0046252 | 0 | 0.0093129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.24322 | 0.9851% | CZ 3C | 5.7214 | 1.2143 | 0.014026 | 1.1415 | 0 | 0.14846 | 0 | 0.29892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 8.5893 | 0.9851% | CZ 3C | 1.6769 | 0.35588 | 0.0041109 | 0 | 0 | 0.043511 | 0 | 0.087609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.1828 | 0.9851% | CZ 3C | 0 | 0 | 0 | 0.011415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011415 | 0.9851% | CZ 3C | 17.555 | 3.7257 | 0.043037 | 1.2477 | 0 | 0.45552 | 0 | 0.91718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 24.0995 | 0.9851%
CZ 4A | 0.1796 | 0.037666 | 0.00046536 | 0.057536 | 0 | 0.011577 | 0 | 0.011543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.29997 | 19.91% | CZ 4A | 5.7648 | 1.209 | 0.014937 | 5.871 | 0 | 0.3716 | 0 | 0.37051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 13.6525 | 19.91% | CZ 4A | 1.6896 | 0.35433 | 0.0043778 | 0 | 0 | 0.10891 | 0 | 0.10859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.2806 | 19.91% | CZ 4A | 0 | 0 | 0 | 0.05871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05871 | 19.91% | CZ 4A | 17.688 | 3.7095 | 0.045831 | 6.417 | 0 | 1.1402 | 0 | 1.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 30.2928 | 19.91%
CZ 4B | 0.17839 | 0.037887 | 0.00045968 | 0.029755 | 0 | 0.010578 | 0 | 0.013172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.27182 | 0.283% | CZ 4B | 5.7258 | 1.2161 | 0.014755 | 3.0362 | 0 | 0.33954 | 0 | 0.42279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 10.8059 | 0.283% | CZ 4B | 1.6781 | 0.35642 | 0.0043244 | 0 | 0 | 0.099515 | 0 | 0.12391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.2771 | 0.283% | CZ 4B | 0 | 0 | 0 | 0.030362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030362 | 0.283% | CZ 4B | 17.5684 | 3.7313 | 0.045272 | 3.3186 | 0 | 1.0418 | 0 | 1.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 27.1581 | 0.283%
CZ 4C | 0.17591 | 0.037507 | 0.00046536 | 0.024861 | 0 | 0.00248 | 0 | 0.0081608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.25096 | 2.916% | CZ 4C | 5.6464 | 1.2039 | 0.014937 | 2.5369 | 0 | 0.079604 | 0 | 0.26194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 9.7943 | 2.916% | CZ 4C | 1.6549 | 0.35284 | 0.0043778 | 0 | 0 | 0.02333 | 0 | 0.076772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.127 | 2.916% | CZ 4C | 0 | 0 | 0 | 0.025369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025369 | 2.916% | CZ 4C | 17.3247 | 3.6939 | 0.045831 | 2.7728 | 0 | 0.24425 | 0 | 0.80372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 25.0406 | 2.916%
CZ 5A | 0.17919 | 0.037751 | 0.00047103 | 0.083998 | 0 | 0.0058454 | 0 | 0.012247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.32108 | 16.91% | CZ 5A | 5.7515 | 1.2117 | 0.015119 | 8.5712 | 0 | 0.18762 | 0 | 0.3931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 16.1809 | 16.91% | CZ 5A | 1.6857 | 0.35514 | 0.0044312 | 0 | 0 | 0.054989 | 0 | 0.11521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.2303 | 16.91% | CZ 5A | 0 | 0 | 0 | 0.085712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085712 | 16.91% | CZ 5A | 17.6472 | 3.7179 | 0.04639 | 9.3684 | 0 | 0.57568 | 0 | 1.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 32.7171 | 16.91%
CZ 5B | 0.17765 | 0.037734 | 0.00046536 | 0.054043 | 0 | 0.0092334 | 0 | 0.014403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.29511 | 4.393% | CZ 5B | 5.7021 | 1.2112 | 0.014937 | 5.5146 | 0 | 0.29637 | 0 | 0.46232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 13.2522 | 4.393% | CZ 5B | 1.6712 | 0.35498 | 0.0043778 | 0 | 0 | 0.086862 | 0 | 0.1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.2678 | 4.393% | CZ 5B | 0 | 0 | 0 | 0.055146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055146 | 4.393% | CZ 5B | 17.4958 | 3.7162 | 0.045831 | 6.0275 | 0 | 0.90936 | 0 | 1.4185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 29.7686 | 4.393%
CZ 5C | 0.17643 | 0.037518 | 0.00046536 | 0.025713 | 0 | 0.0011861 | 0 | 0.0075763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.25046 | 0.0163% | CZ 5C | 5.663 | 1.2043 | 0.014937 | 2.6237 | 0 | 0.038071 | 0 | 0.24318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 9.8378 | 0.0163% | CZ 5C | 1.6597 | 0.35295 | 0.0043778 | 0 | 0 | 0.011158 | 0 | 0.071273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.1143 | 0.0163% | CZ 5C | 0 | 0 | 0 | 0.026237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026237 | 0.0163% | CZ 5C | 17.3756 | 3.695 | 0.045831 | 2.8677 | 0 | 0.11681 | 0 | 0.74615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 25.0025 | 0.0163%
CZ 6A | 0.14507 | 0.037683 | 0.00047103 | 0.13936 | 0 | 0.0070882 | 0 | 0.017627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.34887 | 1.997% | CZ 6A | 4.6564 | 1.2095 | 0.015119 | 14.2204 | 0 | 0.22752 | 0 | 0.56579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 20.9454 | 1.997% | CZ 6A | 1.3647 | 0.35449 | 0.0044312 | 0 | 0 | 0.066681 | 0 | 0.16582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 1.971 | 1.997% | CZ 6A | 0 | 0 | 0 | 0.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1422 | 1.997% | CZ 6A | 14.287 | 3.7112 | 0.04639 | 15.5429 | 0 | 0.69809 | 0 | 1.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 36.177 | 1.997%
CZ 6B | 0.14464 | 0.037626 | 0.00047103 | 0.10581 | 0 | 0.0052665 | 0 | 0.016356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.31174 | 0.1627% | CZ 6B | 4.6427 | 1.2077 | 0.015119 | 10.7965 | 0 | 0.16904 | 0 | 0.52498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 17.4067 | 0.1627% | CZ 6B | 1.3607 | 0.35396 | 0.0044312 | 0 | 0 | 0.049544 | 0 | 0.15386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 1.9373 | 0.1627% | CZ 6B | 0 | 0 | 0 | 0.10797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10797 | 0.1627% | CZ 6B | 14.2451 | 3.7056 | 0.04639 | 11.8006 | 0 | 0.51867 | 0 | 1.6108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 32.0825 | 0.1627%
CZ 7 | 0.14478 | 0.03749 | 0.00047103 | 0.16518 | 0 | 0.0043925 | 0 | 0.013081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.36698 | 0.1966% | CZ 7 | 4.6472 | 1.2033 | 0.015119 | 16.8555 | 0 | 0.14099 | 0 | 0.41988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 23.3327 | 0.1966% | CZ 7 | 1.362 | 0.35268 | 0.0044312 | 0 | 0 | 0.041322 | 0 | 0.12306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 1.8984 | 0.1966% | CZ 7 | 0 | 0 | 0 | 0.16855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16855 | 0.1966% | CZ 7 | 14.2591 | 3.6922 | 0.04639 | 18.423 | 0 | 0.4326 | 0 | 1.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 38.297 | 0.1966%
CZ 8 | 0.1431 | 0.036247 | 0.00047671 | 0.17721 | 0 | 0.00082857 | 0 | 0.0092221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.36867 | 0.01103% | CZ 8 | 4.5933 | 1.1635 | 0.015301 | 18.0827 | 0 | 0.026595 | 0 | 0.29601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 24.2281 | 0.01103% | CZ 8 | 1.3462 | 0.34099 | 0.0044846 | 0 | 0 | 0.0077946 | 0 | 0.086755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 1.8011 | 0.01103% | CZ 8 | 0 | 0 | 0 | 0.18083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18083 | 0.01103% | CZ 8 | 14.0936 | 3.5698 | 0.046949 | 19.7644 | 0 | 0.081602 | 0 | 0.90824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 38.62 | 0.01103%
US Weighted | 0.17809 | 0.03781 | 0.00045175 | 0.042352 | 0 | 0.017903 | 0 | 0.013022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015777 | 0.29121 | 100% | US Weighted | 5.7164 | 1.2136 | 0.0145 | 4.3217 | 0 | 0.57465 | 0 | 0.41798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05064 | 12.3095 | 100% | US Weighted | 1.6754 | 0.35569 | 0.0042498 | 0 | 0 | 0.16842 | 0 | 0.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014842 | 2.3411 | 100% | US Weighted | 0 | 0 | 0 | 0.043217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043217 | 100% | US Weighted | 17.5396 | 3.7237 | 0.044491 | 4.7236 | 0 | 1.7632 | 0 | 1.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15538 | 29.2324 | 100%
Building Type: | Warehouse |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Warehouse |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Warehouse |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Warehouse |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 52045 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 52045 | [17 empty] | Prototype Floor Area: | 52045 | Building Type: | Warehouse | [15 empty] | Prototype Floor Area: | 52045 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 67.52% | 54.06% | 3.417% | 100% |  | 48.01% |  | 51.86% | [7 empty] | 1.996% | 51.37% | 0% | CZ 0A | 67.52% | 54.06% | 3.417% | 100% |  | 48.01% |  | 51.86% | [7 empty] | 1.996% | 52.78% | 0% | CZ 0A | 67.52% | 54.06% | 3.417% |  |  | 48.01% |  | 51.86% | [7 empty] | 1.996% | 50.7% | 0% | CZ 0A |  |  |  | 100% | [12 empty] | 100% | 0% | CZ 0A | 67.52% | 54.06% | 3.417% | 100% |  | 48.01% |  | 51.86% | [7 empty] | 1.996% | 51.46% | 0%
CZ 0B | 66.74% | 54.1% | 3.081% | 99.97% |  | 44.07% |  | 50.04% | [7 empty] | 1.996% | 50.08% | 0% | CZ 0B | 66.74% | 54.1% | 3.081% | 99.97% |  | 44.07% |  | 50.04% | [7 empty] | 1.996% | 51.89% | 0% | CZ 0B | 66.74% | 54.1% | 3.081% |  |  | 44.07% |  | 50.04% | [7 empty] | 1.996% | 49.21% | 0% | CZ 0B |  |  |  | 99.97% | [12 empty] | 99.97% | 0% | CZ 0B | 66.74% | 54.1% | 3.081% | 99.97% |  | 44.07% |  | 50.04% | [7 empty] | 1.996% | 50.2% | 0%
CZ 1A | 66.08% | 54.09% | 3.289% | 100% |  | 52.73% |  | 55.57% | [7 empty] | 1.996% | 52.36% | 2.875% | CZ 1A | 66.08% | 54.09% | 3.289% | 100% |  | 52.73% |  | 55.57% | [7 empty] | 1.996% | 53.92% | 2.875% | CZ 1A | 66.08% | 54.09% | 3.289% |  |  | 52.73% |  | 55.57% | [7 empty] | 1.996% | 51.61% | 2.875% | CZ 1A |  |  |  | 100% | [12 empty] | 100% | 2.875% | CZ 1A | 66.08% | 54.09% | 3.289% | 100% |  | 52.73% |  | 55.57% | [7 empty] | 1.996% | 52.46% | 2.875%
CZ 1B | 66.44% | 54.1% | 3.08% | 97.4% |  | 47.78% |  | 51.66% | [7 empty] | 1.996% | 51.3% | 0% | CZ 1B | 66.44% | 54.1% | 3.08% | 97.4% |  | 47.78% |  | 51.66% | [7 empty] | 1.996% | 53.22% | 0% | CZ 1B | 66.44% | 54.1% | 3.08% |  |  | 47.78% |  | 51.66% | [7 empty] | 1.996% | 50.36% | 0% | CZ 1B |  |  |  | 97.4% | [12 empty] | 97.4% | 0% | CZ 1B | 66.44% | 54.1% | 3.08% | 97.4% |  | 47.78% |  | 51.66% | [7 empty] | 1.996% | 51.42% | 0%
CZ 2A | 65.93% | 54.09% | 3.195% | 98.22% |  | 45.5% |  | 24.11% | [7 empty] | 1.996% | 49.38% | 19% | CZ 2A | 65.93% | 54.09% | 3.195% | 98.22% |  | 45.5% |  | 24.11% | [7 empty] | 1.996% | 52.45% | 19% | CZ 2A | 65.93% | 54.09% | 3.195% |  |  | 45.5% |  | 24.11% | [7 empty] | 1.996% | 47.82% | 19% | CZ 2A |  |  |  | 98.22% | [12 empty] | 98.22% | 19% | CZ 2A | 65.93% | 54.09% | 3.195% | 98.22% |  | 45.5% |  | 24.11% | [7 empty] | 1.996% | 49.58% | 19%
CZ 2B | 64.34% | 54.08% | 3.028% | 93.4% |  | 46.31% |  | 50.31% | [7 empty] | 1.996% | 49.99% | 3.369% | CZ 2B | 64.34% | 54.08% | 3.028% | 93.4% |  | 46.31% |  | 50.31% | [7 empty] | 1.996% | 51.61% | 3.369% | CZ 2B | 64.34% | 54.08% | 3.028% |  |  | 46.31% |  | 50.31% | [7 empty] | 1.996% | 49.2% | 3.369% | CZ 2B |  |  |  | 93.4% | [12 empty] | 93.4% | 3.369% | CZ 2B | 64.34% | 54.08% | 3.028% | 93.4% |  | 46.31% |  | 50.31% | [7 empty] | 1.996% | 50.09% | 3.369%
CZ 3A | 65.19% | 54.03% | 3.161% | 49.23% |  | 48.99% |  | 25.34% | [7 empty] | 1.996% | 48.15% | 14.95% | CZ 3A | 65.19% | 54.03% | 3.161% | 49.23% |  | 48.99% |  | 25.34% | [7 empty] | 1.996% | 48.36% | 14.95% | CZ 3A | 65.19% | 54.03% | 3.161% |  |  | 48.99% |  | 25.34% | [7 empty] | 1.996% | 48.03% | 14.95% | CZ 3A |  |  |  | 49.23% | [12 empty] | 49.23% | 14.95% | CZ 3A | 65.19% | 54.03% | 3.161% | 49.23% |  | 48.99% |  | 25.34% | [7 empty] | 1.996% | 48.17% | 14.95%
CZ 3B | 64.86% | 54.12% | 3.005% | 72.01% |  | 43.11% |  | 23.11% | [7 empty] | 1.996% | 47.8% | 12.03% | CZ 3B | 64.86% | 54.12% | 3.005% | 72.01% |  | 43.11% |  | 23.11% | [7 empty] | 1.996% | 49.56% | 12.03% | CZ 3B | 64.86% | 54.12% | 3.005% |  |  | 43.11% |  | 23.11% | [7 empty] | 1.996% | 46.89% | 12.03% | CZ 3B |  |  |  | 72.01% | [12 empty] | 72.01% | 12.03% | CZ 3B | 64.86% | 54.12% | 3.005% | 72.01% |  | 43.11% |  | 23.11% | [7 empty] | 1.996% | 47.91% | 12.03%
CZ 3C | 65.17% | 53.96% | 3.031% | 94.65% |  | 41.75% |  | 31.48% | [7 empty] | 1.996% | 49.68% | 0.9851% | CZ 3C | 65.17% | 53.96% | 3.031% | 94.65% |  | 41.75% |  | 31.48% | [7 empty] | 1.996% | 51.93% | 0.9851% | CZ 3C | 65.17% | 53.96% | 3.031% |  |  | 41.75% |  | 31.48% | [7 empty] | 1.996% | 48.57% | 0.9851% | CZ 3C |  |  |  | 94.65% | [12 empty] | 94.65% | 0.9851% | CZ 3C | 65.17% | 53.96% | 3.031% | 94.65% |  | 41.75% |  | 31.48% | [7 empty] | 1.996% | 49.82% | 0.9851%
CZ 4A | 65.66% | 53.8% | 3.123% | 35.42% |  | 52.81% |  | 32.95% | [7 empty] | 1.996% | 45.67% | 19.91% | CZ 4A | 65.66% | 53.8% | 3.123% | 35.42% |  | 52.81% |  | 32.95% | [7 empty] | 1.996% | 42.08% | 19.91% | CZ 4A | 65.66% | 53.8% | 3.123% |  |  | 52.81% |  | 32.95% | [7 empty] | 1.996% | 49.03% | 19.91% | CZ 4A |  |  |  | 35.42% | [12 empty] | 35.42% | 19.91% | CZ 4A | 65.66% | 53.8% | 3.123% | 35.42% |  | 52.81% |  | 32.95% | [7 empty] | 1.996% | 45.34% | 19.91%
CZ 4B | 65.22% | 54.07% | 3.118% | 45.67% |  | 45.83% |  | 30.87% | [7 empty] | 1.996% | 47.83% | 0.283% | CZ 4B | 65.22% | 54.07% | 3.118% | 45.67% |  | 45.83% |  | 30.87% | [7 empty] | 1.996% | 47.4% | 0.283% | CZ 4B | 65.22% | 54.07% | 3.118% |  |  | 45.83% |  | 30.87% | [7 empty] | 1.996% | 48.11% | 0.283% | CZ 4B |  |  |  | 45.67% | [12 empty] | 45.67% | 0.283% | CZ 4B | 65.22% | 54.07% | 3.118% | 45.67% |  | 45.83% |  | 30.87% | [7 empty] | 1.996% | 47.8% | 0.283%
CZ 4C | 64.31% | 53.64% | 3.089% | 34.79% |  | 58.11% |  | 30.11% | [7 empty] | 1.996% | 46.44% | 2.916% | CZ 4C | 64.31% | 53.64% | 3.089% | 34.79% |  | 58.11% |  | 30.11% | [7 empty] | 1.996% | 43.83% | 2.916% | CZ 4C | 64.31% | 53.64% | 3.089% |  |  | 58.11% |  | 30.11% | [7 empty] | 1.996% | 48.22% | 2.916% | CZ 4C |  |  |  | 34.79% | [12 empty] | 34.79% | 2.916% | CZ 4C | 64.31% | 53.64% | 3.089% | 34.79% |  | 58.11% |  | 30.11% | [7 empty] | 1.996% | 46.24% | 2.916%
CZ 5A | 65.51% | 53.91% | 3.07% | 32.11% |  | 58.16% |  | 35.81% | [7 empty] | 1.996% | 43.17% | 16.91% | CZ 5A | 65.51% | 53.91% | 3.07% | 32.11% |  | 58.16% |  | 35.81% | [7 empty] | 1.996% | 38.37% | 16.91% | CZ 5A | 65.51% | 53.91% | 3.07% |  |  | 58.16% |  | 35.81% | [7 empty] | 1.996% | 49.17% | 16.91% | CZ 5A |  |  |  | 32.11% | [12 empty] | 32.11% | 16.91% | CZ 5A | 65.51% | 53.91% | 3.07% | 32.11% |  | 58.16% |  | 35.81% | [7 empty] | 1.996% | 42.68% | 16.91%
CZ 5B | 64.95% | 53.88% | 3.059% | 37.56% |  | 57.67% |  | 34.38% | [7 empty] | 1.996% | 46.14% | 4.393% | CZ 5B | 64.95% | 53.88% | 3.059% | 37.56% |  | 57.67% |  | 34.38% | [7 empty] | 1.996% | 43.32% | 4.393% | CZ 5B | 64.95% | 53.88% | 3.059% |  |  | 57.67% |  | 34.38% | [7 empty] | 1.996% | 48.63% | 4.393% | CZ 5B |  |  |  | 37.56% | [12 empty] | 37.56% | 4.393% | CZ 5B | 64.95% | 53.88% | 3.059% | 37.56% |  | 57.67% |  | 34.38% | [7 empty] | 1.996% | 45.89% | 4.393%
CZ 5C | 64.5% | 53.66% | 3.038% | 38.09% |  | 64.31% |  | 30.87% | [7 empty] | 1.996% | 47.11% | 0.0163% | CZ 5C | 64.5% | 53.66% | 3.038% | 38.09% |  | 64.31% |  | 30.87% | [7 empty] | 1.996% | 45.15% | 0.0163% | CZ 5C | 64.5% | 53.66% | 3.038% |  |  | 64.31% |  | 30.87% | [7 empty] | 1.996% | 48.42% | 0.0163% | CZ 5C |  |  |  | 38.09% | [12 empty] | 38.09% | 0.0163% | CZ 5C | 64.5% | 53.66% | 3.038% | 38.09% |  | 64.31% |  | 30.87% | [7 empty] | 1.996% | 46.96% | 0.0163%
CZ 6A | 53.04% | 53.83% | 3.006% | 34.16% |  | 62.8% |  | 42.72% | [7 empty] | 1.996% | 38.82% | 1.997% | CZ 6A | 53.04% | 53.83% | 3.006% | 34.16% |  | 62.8% |  | 42.72% | [7 empty] | 1.996% | 36.5% | 1.997% | CZ 6A | 53.04% | 53.83% | 3.006% |  |  | 62.8% |  | 42.72% | [7 empty] | 1.996% | 42.69% | 1.997% | CZ 6A |  |  |  | 34.16% | [12 empty] | 34.16% | 1.997% | CZ 6A | 53.04% | 53.83% | 3.006% | 34.16% |  | 62.8% |  | 42.72% | [7 empty] | 1.996% | 38.56% | 1.997%
CZ 6B | 52.88% | 53.79% | 3.021% | 39.58% |  | 62.79% |  | 40.41% | [7 empty] | 1.996% | 41.33% | 0.1627% | CZ 6B | 52.88% | 53.79% | 3.021% | 39.58% |  | 62.79% |  | 40.41% | [7 empty] | 1.996% | 40.57% | 0.1627% | CZ 6B | 52.88% | 53.79% | 3.021% |  |  | 62.79% |  | 40.41% | [7 empty] | 1.996% | 42.29% | 0.1627% | CZ 6B |  |  |  | 39.58% | [12 empty] | 39.58% | 0.1627% | CZ 6B | 52.88% | 53.79% | 3.021% | 39.58% |  | 62.79% |  | 40.41% | [7 empty] | 1.996% | 41.25% | 0.1627%
CZ 7 | 52.93% | 53.63% | 2.934% | 40.13% |  | 65.7% |  | 38.74% | [7 empty] | 1.996% | 41.21% | 0.1966% | CZ 7 | 52.93% | 53.63% | 2.934% | 40.13% |  | 65.7% |  | 38.74% | [7 empty] | 1.996% | 40.66% | 0.1966% | CZ 7 | 52.93% | 53.63% | 2.934% |  |  | 65.7% |  | 38.74% | [7 empty] | 1.996% | 42.13% | 0.1966% | CZ 7 |  |  |  | 40.13% | [12 empty] | 40.13% | 0.1966% | CZ 7 | 52.93% | 53.63% | 2.934% | 40.13% |  | 65.7% |  | 38.74% | [7 empty] | 1.996% | 41.14% | 0.1966%
CZ 8 | 52.32% | 52.14% | 2.876% | 41.03% |  | 57.94% |  | 33.89% | [7 empty] | 1.996% | 41% | 0.01103% | CZ 8 | 52.32% | 52.14% | 2.876% | 41.03% |  | 57.94% |  | 33.89% | [7 empty] | 1.996% | 41.02% | 0.01103% | CZ 8 | 52.32% | 52.14% | 2.876% |  |  | 57.94% |  | 33.89% | [7 empty] | 1.996% | 40.97% | 0.01103% | CZ 8 |  |  |  | 41.03% | [12 empty] | 41.03% | 0.01103% | CZ 8 | 52.32% | 52.14% | 2.876% | 41.03% |  | 57.94% |  | 33.89% | [7 empty] | 1.996% | 41% | 0.01103%
US Weighted | 65.11% | 53.96% | 3.113% | 57.75% | 0% | 50.85% | 0% | 30.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.85% | 100% | US Weighted | 65.11% | 53.96% | 3.113% | 57.75% | 0% | 50.85% | 0% | 30.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.03% | 100% | US Weighted | 65.11% | 53.96% | 3.113% | 0% | 0% | 50.85% | 0% | 30.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 48.3% | 100% | US Weighted | 0% | 0% | 0% | 57.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 57.75% | 100% | US Weighted | 65.11% | 53.96% | 3.113% | 57.75% | 0% | 50.85% | 0% | 30.85% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.996% | 46.74% | 100%

## RestQS
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 2501 |  | Building Type: | Quick-service Restaurant |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 |  | Building Type: | Quick-service Restaurant |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Quick-service Restaurant |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Quick-service Restaurant | [14 empty] | Prototype Floor Area: | 2501 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.29915 | 0.10383 | 0.65808 | 0.6553 | 0 | 1.0467 | 0 | 0.65509 | 0 | 0 | 0.67217 | 0 | 0 | 4.5293 | 0 | 0 | 8.6195 |  | STD2019 | 9.6022 | 3.3328 | 67.1511 | 66.8672 | 0 | 33.5954 | 0 | 21.0269 | 0 | 0 | 21.5751 | 0 | 0 | 269.3289 | 0 | 0 | 492.4796 |  | STD2019 | 2.8142 | 0.97679 | 0 | 0 | 0 | 9.8463 | 0 | 6.1626 | 0 | 0 | 6.3233 | 0 | 0 | 25.937 | 0 | 0 | 52.0602 |  | STD2019 | 0 | 0 | 0.67151 | 0.66867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1485 |  | STD2019 | 29.4623 | 10.2261 | 73.3961 | 73.0858 | 0 | 103.0805 | 0 | 64.5165 | 0 | 0 | 66.1988 | 0 | 0 | 469.1836 | 0 | 0 | 889.1496
STD2016 | 0.32126 | 0.10383 | 0.65797 | 0.66889 | 0 | 1.1161 | 0 | 0.67554 | 0 | 0 | 1.013 | 0 | 0 | 4.5293 | 0 | 0 | 9.0859 |  | STD2016 | 10.3118 | 3.3328 | 67.1396 | 68.2538 | 0 | 35.825 | 0 | 21.6833 | 0 | 0 | 32.5152 | 0 | 0 | 269.3289 | 0 | 0 | 508.3904 |  | STD2016 | 3.0222 | 0.97679 | 0 | 0 | 0 | 10.4997 | 0 | 6.355 | 0 | 0 | 9.5297 | 0 | 0 | 25.937 | 0 | 0 | 56.3204 |  | STD2016 | 0 | 0 | 0.6714 | 0.68254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1623 |  | STD2016 | 31.6396 | 10.2261 | 73.3835 | 74.6014 | 0 | 109.9216 | 0 | 66.5306 | 0 | 0 | 99.766 | 0 | 0 | 469.1836 | 0 | 0 | 935.2523
STD2013 | 0.37798 | 0.18137 | 0.65797 | 0.67401 | 0 | 1.1271 | 0 | 0.68035 | 0 | 0 | 1.013 | 0 | 0 | 4.5293 | 0 | 0 | 9.241 |  | STD2013 | 12.1325 | 5.8216 | 67.1395 | 68.7766 | 0 | 36.1769 | 0 | 21.8378 | 0 | 0 | 32.5159 | 0 | 0 | 269.3289 | 0 | 0 | 513.7297 |  | STD2013 | 3.5558 | 1.7062 | 0 | 0 | 0 | 10.6028 | 0 | 6.4003 | 0 | 0 | 9.5299 | 0 | 0 | 25.937 | 0 | 0 | 57.732 |  | STD2013 | 0 | 0 | 0.6714 | 0.68777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1675 |  | STD2013 | 37.2259 | 17.8624 | 73.3835 | 75.1728 | 0 | 111.0012 | 0 | 67.0048 | 0 | 0 | 99.7682 | 0 | 0 | 469.1836 | 0 | 0 | 950.6023
STD2010 | 0.40349 | 0.18137 | 0.65835 | 0.78952 | 0 | 1.1505 | 0 | 1.1054 | 0 | 0 | 1.2784 | 0 | 0 | 4.5293 | 0 | 0 | 10.0962 |  | STD2010 | 12.951 | 5.8216 | 67.1786 | 80.5632 | 0 | 36.9277 | 0 | 35.4812 | 0 | 0 | 41.0331 | 0 | 0 | 269.3289 | 0 | 0 | 549.2854 |  | STD2010 | 3.7957 | 1.7062 | 0 | 0 | 0 | 10.8229 | 0 | 10.399 | 0 | 0 | 12.0261 | 0 | 0 | 25.937 | 0 | 0 | 64.6869 |  | STD2010 | 0 | 0 | 0.67179 | 0.80563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2857 |  | STD2010 | 39.7375 | 17.8624 | 73.4262 | 88.0556 | 0 | 113.3048 | 0 | 108.8666 | 0 | 0 | 125.9015 | 0 | 0 | 469.1836 | 0 | 0 | 1036.3382
STD2007 | 0.88668 | 0.32337 | 0.65841 | 0.74246 | 0 | 1.6254 | 0 | 1.6392 | 0 | 0 | 1.2772 | 0 | 0 | 4.5327 | 0 | 0 | 11.6854 |  | STD2007 | 28.4604 | 10.3794 | 67.1851 | 75.7613 | 0 | 52.1728 | 0 | 52.6137 | 0 | 0 | 40.9958 | 0 | 0 | 269.4388 | 0 | 0 | 597.0073 |  | STD2007 | 8.3413 | 3.042 | 0 | 0 | 0 | 15.291 | 0 | 15.4202 | 0 | 0 | 12.0152 | 0 | 0 | 25.9692 | 0 | 0 | 80.0789 |  | STD2007 | 0 | 0 | 0.67185 | 0.75761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2378 |  | STD2007 | 87.3246 | 31.8469 | 73.4333 | 82.8071 | 0 | 160.0813 | 0 | 161.4341 | 0 | 0 | 125.7869 | 0 | 0 | 469.5209 | 0 | 0 | 1192.2351
STD2004 | 0.88668 | 0.32337 | 0.65768 | 0.94706 | 0 | 1.7413 | 0 | 1.6713 | 0 | 0 | 1.2866 | 0 | 0 | 4.5327 | 0 | 0 | 12.0466 |  | STD2004 | 28.4604 | 10.3794 | 67.11 | 96.6386 | 0 | 55.8912 | 0 | 53.6441 | 0 | 0 | 41.298 | 0 | 0 | 269.4388 | 0 | 0 | 622.8604 |  | STD2004 | 8.3413 | 3.042 | 0 | 0 | 0 | 16.3808 | 0 | 15.7222 | 0 | 0 | 12.1037 | 0 | 0 | 25.9692 | 0 | 0 | 81.5592 |  | STD2004 | 0 | 0 | 0.6711 | 0.96639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.4458 |  | STD2004 | 87.3246 | 31.8469 | 73.3512 | 105.626 | 0 | 171.4904 | 0 | 164.5955 | 0 | 0 | 126.7142 | 0 | 0 | 469.5209 | 0 | 0 | 1230.4696
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | -0.00073616 | 0.2046 | 0 | 0.11585 | 0 | 0.032101 | 0 | 0 | 0.0094148 | 0 | 0 | 0 | 0 | 0 | 0.36122 |  | 2004-2007 | 0 | 0 | -0.075118 | 20.8772 | 0 | 3.7184 | 0 | 1.0304 | 0 | 0 | 0.3022 | 0 | 0 | 0 | 0 | 0 | 25.8531 |  | 2004-2007 | 0 | 0 | 0 | 0 | 0 | 1.0898 | 0 | 0.30198 | 0 | 0 | 0.088568 | 0 | 0 | 0 | 0 | 0 | 1.4803 |  | 2004-2007 | 0 | 0 | -0.00075118 | 0.20877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20802 |  | 2004-2007 | 0 | 0 | -0.082104 | 22.8188 | 0 | 11.4091 | 0 | 3.1614 | 0 | 0 | 0.92722 | 0 | 0 | 0 | 0 | 0 | 38.2345
2007-2010 | 0.48319 | 0.14199 | 6.3489e-05 | -0.047058 | 0 | 0.47496 | 0 | 0.53376 | 0 | 0 | -0.0011629 | 0 | 0 | 0.0034248 | 0 | 0 | 1.5892 |  | 2007-2010 | 15.5093 | 4.5577 | 0.0064785 | -4.8019 | 0 | 15.2452 | 0 | 17.1325 | 0 | 0 | -0.037326 | 0 | 0 | 0.10993 | 0 | 0 | 47.7219 |  | 2007-2010 | 4.5455 | 1.3358 | 0 | 0 | 0 | 4.4681 | 0 | 5.0212 | 0 | 0 | -0.01094 | 0 | 0 | 0.032218 | 0 | 0 | 15.3919 |  | 2007-2010 | 0 | 0 | 6.4785e-05 | -0.048019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.047954 |  | 2007-2010 | 47.5871 | 13.9844 | 0.007081 | -5.2484 | 0 | 46.7765 | 0 | 52.5674 | 0 | 0 | -0.11453 | 0 | 0 | 0.3373 | 0 | 0 | 155.8969
2010-2013 | 0.025503 | 0 | 0.000383 | 0.11551 | 0 | 0.023391 | 0 | 0.42506 | 0 | 0 | 0.26535 | 0 | 0 | 0 | 0 | 0 | 0.85519 |  | 2010-2013 | 0.81859 | 0 | 0.039082 | 11.7866 | 0 | 0.75079 | 0 | 13.6434 | 0 | 0 | 8.5172 | 0 | 0 | 0 | 0 | 0 | 35.5557 |  | 2010-2013 | 0.23991 | 0 | 0 | 0 | 0 | 0.22004 | 0 | 3.9986 | 0 | 0 | 2.4963 | 0 | 0 | 0 | 0 | 0 | 6.9549 |  | 2010-2013 | 0 | 0 | 0.00039082 | 0.11787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11826 |  | 2010-2013 | 2.5117 | 0 | 0.042717 | 12.8828 | 0 | 2.3036 | 0 | 41.8619 | 0 | 0 | 26.1333 | 0 | 0 | 0 | 0 | 0 | 85.736
2013-2016 | 0.056722 | 0.077538 | -2.4997e-07 | 0.005123 | 0 | 0.010962 | 0 | 0.0048144 | 0 | 0 | 2.2248e-05 | 0 | 0 | 0 | 0 | 0 | 0.15518 |  | 2013-2016 | 1.8207 | 2.4888 | -2.5507e-05 | 0.52275 | 0 | 0.35186 | 0 | 0.15453 | 0 | 0 | 0.0007141 | 0 | 0 | 0 | 0 | 0 | 5.3393 |  | 2013-2016 | 0.5336 | 0.72943 | 0 | 0 | 0 | 0.10312 | 0 | 0.045291 | 0 | 0 | 0.00020929 | 0 | 0 | 0 | 0 | 0 | 1.4117 |  | 2013-2016 | 0 | 0 | -2.5507e-07 | 0.0052275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052273 |  | 2013-2016 | 5.5863 | 7.6364 | -2.7879e-05 | 0.57137 | 0 | 1.0796 | 0 | 0.47415 | 0 | 0 | 0.0021911 | 0 | 0 | 0 | 0 | 0 | 15.35
2016-2019 | 0.022107 | 0 | -0.00011277 | 0.013589 | 0 | 0.069463 | 0 | 0.020451 | 0 | 0 | 0.34083 | 0 | 0 | 0 | 0 | 0 | 0.46633 |  | 2016-2019 | 0.7096 | 0 | -0.011507 | 1.3866 | 0 | 2.2296 | 0 | 0.65643 | 0 | 0 | 10.94 | 0 | 0 | 0 | 0 | 0 | 15.9108 |  | 2016-2019 | 0.20797 | 0 | 0 | 0 | 0 | 0.65346 | 0 | 0.19239 | 0 | 0 | 3.2063 | 0 | 0 | 0 | 0 | 0 | 4.2602 |  | 2016-2019 | 0 | 0 | -0.00011507 | 0.013866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013751 |  | 2016-2019 | 2.1773 | 0 | -0.012577 | 1.5156 | 0 | 6.8411 | 0 | 2.0141 | 0 | 0 | 33.5672 | 0 | 0 | 0 | 0 | 0 | 46.1027
2004-2019 | 0.58752 | 0.21953 | -0.00040268 | 0.29176 | 0 | 0.69462 | 0 | 1.0162 | 0 | 0 | 0.61446 | 0 | 0 | 0.0034248 | 0 | 0 | 3.4271 |  | 2004-2019 | 18.8582 | 7.0465 | -0.04109 | 29.7714 | 0 | 22.2958 | 0 | 32.6172 | 0 | 0 | 19.7228 | 0 | 0 | 0.10993 | 0 | 0 | 130.3808 |  | 2004-2019 | 5.527 | 2.0652 | 0 | 0 | 0 | 6.5345 | 0 | 9.5596 | 0 | 0 | 5.7804 | 0 | 0 | 0.032218 | 0 | 0 | 29.499 |  | 2004-2019 | 0 | 0 | -0.0004109 | 0.29771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2973 |  | 2004-2019 | 57.8623 | 21.6208 | -0.044911 | 32.5401 | 0 | 68.4099 | 0 | 100.079 | 0 | 0 | 60.5154 | 0 | 0 | 0.3373 | 0 | 0 | 341.3199
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.1119% | 21.6% |  | 6.653% |  | 1.921% |  |  | 0.7317% |  |  | 0% |  |  | 2.999% |  | 2004-2007 | 0% | 0% | -0.1119% | 21.6% |  | 6.653% |  | 1.921% |  |  | 0.7317% |  |  | 0% |  |  | 4.151% |  | 2004-2007 | 0% | 0% |  |  |  | 6.653% |  | 1.921% |  |  | 0.7317% |  |  | 0% |  |  | 1.815% |  | 2004-2007 |  |  | -0.1119% | 21.6% | [9 empty] | 0% |  |  | 6.037% |  | 2004-2007 | 0% | 0% | -0.1119% | 21.6% |  | 6.653% |  | 1.921% |  |  | 0.7317% |  |  | 0% |  |  | 3.107%
2007-2010 | 54.49% | 43.91% | 0.009643% | -6.338% |  | 29.22% |  | 32.56% |  |  | -0.09105% |  |  | 0.07556% |  |  | 13.6% |  | 2007-2010 | 54.49% | 43.91% | 0.009643% | -6.338% |  | 29.22% |  | 32.56% |  |  | -0.09105% |  |  | 0.0408% |  |  | 7.994% |  | 2007-2010 | 54.49% | 43.91% |  |  |  | 29.22% |  | 32.56% |  |  | -0.09105% |  |  | 0.1241% |  |  | 19.22% |  | 2007-2010 |  |  | 0.009643% | -6.338% | [9 empty] | 0% |  |  | -1.481% |  | 2007-2010 | 54.49% | 43.91% | 0.009643% | -6.338% |  | 29.22% |  | 32.56% |  |  | -0.09105% |  |  | 0.07184% |  |  | 13.08%
2010-2013 | 6.321% | 0% | 0.05818% | 14.63% |  | 2.033% |  | 38.45% |  |  | 20.76% |  |  | 0% |  |  | 8.47% |  | 2010-2013 | 6.321% | 0% | 0.05818% | 14.63% |  | 2.033% |  | 38.45% |  |  | 20.76% |  |  | 0% |  |  | 6.473% |  | 2010-2013 | 6.321% | 0% |  |  |  | 2.033% |  | 38.45% |  |  | 20.76% |  |  | 0% |  |  | 10.75% |  | 2010-2013 |  |  | 0.05818% | 14.63% | [9 empty] | 0% |  |  | 3.599% |  | 2010-2013 | 6.321% | 0% | 0.05818% | 14.63% |  | 2.033% |  | 38.45% |  |  | 20.76% |  |  | 0% |  |  | 8.273%
2013-2016 | 15.01% | 42.75% | -3.799e-05% | 0.7601% |  | 0.9726% |  | 0.7076% |  |  | 0.002196% |  |  | 0% |  |  | 1.679% |  | 2013-2016 | 15.01% | 42.75% | -3.799e-05% | 0.7601% |  | 0.9726% |  | 0.7076% |  |  | 0.002196% |  |  | 0% |  |  | 1.039% |  | 2013-2016 | 15.01% | 42.75% |  |  |  | 0.9726% |  | 0.7076% |  |  | 0.002196% |  |  | 0% |  |  | 2.445% |  | 2013-2016 |  |  | -3.799e-05% | 0.7601% | [9 empty] | 0% |  |  | 0.165% |  | 2013-2016 | 15.01% | 42.75% | -3.799e-05% | 0.7601% |  | 0.9726% |  | 0.7076% |  |  | 0.002196% |  |  | 0% |  |  | 1.615%
2016-2019 | 6.881% | 0% | -0.01714% | 2.032% |  | 6.224% |  | 3.027% |  |  | 33.65% |  |  | 0% |  |  | 5.132% |  | 2016-2019 | 6.881% | 0% | -0.01714% | 2.032% |  | 6.224% |  | 3.027% |  |  | 33.65% |  |  | 0% |  |  | 3.13% |  | 2016-2019 | 6.881% | 0% |  |  |  | 6.224% |  | 3.027% |  |  | 33.65% |  |  | 0% |  |  | 7.564% |  | 2016-2019 |  |  | -0.01714% | 2.032% | [9 empty] | 0% |  |  | 0.4349% |  | 2016-2019 | 6.881% | 0% | -0.01714% | 2.032% |  | 6.224% |  | 3.027% |  |  | 33.65% |  |  | 0% |  |  | 4.929%
2004-2019 | 66.26% | 67.89% | -0.06123% | 30.81% |  | 39.89% |  | 60.8% |  |  | 47.76% |  |  | 0.07556% |  |  | 28.45% |  | 2004-2019 | 66.26% | 67.89% | -0.06123% | 30.81% |  | 39.89% |  | 60.8% |  |  | 47.76% |  |  | 0.0408% |  |  | 20.93% |  | 2004-2019 | 66.26% | 67.89% |  |  |  | 39.89% |  | 60.8% |  |  | 47.76% |  |  | 0.1241% |  |  | 36.17% |  | 2004-2019 |  |  | -0.06123% | 30.81% | [9 empty] | 0% |  |  | 8.628% |  | 2004-2019 | 66.26% | 67.89% | -0.06123% | 30.81% |  | 39.89% |  | 60.8% |  |  | 47.76% |  |  | 0.07184% |  |  | 27.74%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.29961 | 0.10381 | 0.4622 | 0 | 0 | 4.0715 | 0 | 0.90226 | 0 | 0 | 0.70705 | 0 | 0 | 4.5293 | 0 | 0 | 11.0757 | 0% | CZ 0A | 9.6169 | 3.332 | 47.1635 | 0 | 0 | 130.6872 | 0 | 28.9607 | 0 | 0 | 22.6948 | 0 | 0 | 269.3289 | 0 | 0 | 511.7839 | 0% | CZ 0A | 2.8186 | 0.97655 | 0 | 0 | 0 | 38.3022 | 0 | 8.4879 | 0 | 0 | 6.6515 | 0 | 0 | 25.937 | 0 | 0 | 83.1737 | 0% | CZ 0A | 0 | 0 | 0.47163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.28 | 0% | CZ 0A | 29.5075 | 10.2235 | 51.5497 | 0 | 0 | 400.986 | 0 | 88.8599 | 0 | 0 | 69.634 | 0 | 0 | 469.1836 | 0 | 0 | 1119.9442 | 0%
CZ 0B | 0.29902 | 0.10381 | 0.46038 | 0.0003714 | 0 | 3.6439 | 0 | 0.90604 | 0 | 0 | 0.70233 | 0 | 0 | 4.5293 | 0 | 0 | 10.6451 | 0% | CZ 0B | 9.598 | 3.332 | 46.9778 | 0.037898 | 0 | 116.9612 | 0 | 29.082 | 0 | 0 | 22.5431 | 0 | 0 | 269.3289 | 0 | 0 | 497.8608 | 0% | CZ 0B | 2.813 | 0.97655 | 0 | 0 | 0 | 34.2794 | 0 | 8.5235 | 0 | 0 | 6.607 | 0 | 0 | 25.937 | 0 | 0 | 79.1364 | 0% | CZ 0B | 0 | 0 | 0.46978 | 0.00037898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2785 | 0% | CZ 0B | 29.4494 | 10.2235 | 51.3467 | 0.041422 | 0 | 358.8706 | 0 | 89.2321 | 0 | 0 | 69.1688 | 0 | 0 | 469.1836 | 0 | 0 | 1077.5161 | 0%
CZ 1A | 0.29961 | 0.10381 | 0.50432 | 0 | 0 | 2.4979 | 0 | 0.68201 | 0 | 0 | 0.69595 | 0 | 0 | 4.5293 | 0 | 0 | 9.3128 | 2.382% | CZ 1A | 9.6169 | 3.332 | 51.4611 | 0 | 0 | 80.1765 | 0 | 21.8911 | 0 | 0 | 22.3384 | 0 | 0 | 269.3289 | 0 | 0 | 458.1449 | 2.382% | CZ 1A | 2.8186 | 0.97655 | 0 | 0 | 0 | 23.4984 | 0 | 6.4159 | 0 | 0 | 6.547 | 0 | 0 | 25.937 | 0 | 0 | 66.1934 | 2.382% | CZ 1A | 0 | 0 | 0.51461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3229 | 2.382% | CZ 1A | 29.5075 | 10.2235 | 56.2469 | 0 | 0 | 246.0046 | 0 | 67.1683 | 0 | 0 | 68.5407 | 0 | 0 | 469.1836 | 0 | 0 | 946.8752 | 2.382%
CZ 1B | 0.29985 | 0.10357 | 0.50536 | 0.034503 | 0 | 2.7617 | 0 | 0.86117 | 0 | 0 | 0.69571 | 0 | 0 | 4.5293 | 0 | 0 | 9.7911 | 0% | CZ 1B | 9.6245 | 3.3244 | 51.5672 | 3.5207 | 0 | 88.6449 | 0 | 27.6416 | 0 | 0 | 22.3308 | 0 | 0 | 269.3289 | 0 | 0 | 475.9829 | 0% | CZ 1B | 2.8208 | 0.97433 | 0 | 0 | 0 | 25.9803 | 0 | 8.1013 | 0 | 0 | 6.5448 | 0 | 0 | 25.937 | 0 | 0 | 70.3585 | 0% | CZ 1B | 0 | 0 | 0.51567 | 0.035207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3592 | 0% | CZ 1B | 29.5308 | 10.2003 | 56.3629 | 3.8481 | 0 | 271.988 | 0 | 84.8123 | 0 | 0 | 68.5175 | 0 | 0 | 469.1836 | 0 | 0 | 994.4434 | 0%
CZ 2A | 0.29855 | 0.10357 | 0.55152 | 0.09218 | 0 | 2.1282 | 0 | 0.73031 | 0 | 0 | 0.69134 | 0 | 0 | 4.5293 | 0 | 0 | 9.125 | 20.26% | CZ 2A | 9.5828 | 3.3244 | 56.2778 | 9.4062 | 0 | 68.3117 | 0 | 23.4415 | 0 | 0 | 22.1906 | 0 | 0 | 269.3289 | 0 | 0 | 461.8639 | 20.26% | CZ 2A | 2.8086 | 0.97433 | 0 | 0 | 0 | 20.021 | 0 | 6.8703 | 0 | 0 | 6.5037 | 0 | 0 | 25.937 | 0 | 0 | 63.1149 | 20.26% | CZ 2A | 0 | 0 | 0.56278 | 0.094062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4652 | 20.26% | CZ 2A | 29.4028 | 10.2003 | 61.5117 | 10.2809 | 0 | 209.6 | 0 | 71.9253 | 0 | 0 | 68.0871 | 0 | 0 | 469.1836 | 0 | 0 | 930.1917 | 20.26%
CZ 2B | 0.29855 | 0.10369 | 0.55509 | 0.078253 | 0 | 1.4581 | 0 | 0.77307 | 0 | 0 | 0.68095 | 0 | 0 | 4.5293 | 0 | 0 | 8.477 | 2.859% | CZ 2B | 9.5828 | 3.3282 | 56.6416 | 7.985 | 0 | 46.8034 | 0 | 24.8137 | 0 | 0 | 21.857 | 0 | 0 | 269.3289 | 0 | 0 | 440.3407 | 2.859% | CZ 2B | 2.8086 | 0.97544 | 0 | 0 | 0 | 13.7173 | 0 | 7.2725 | 0 | 0 | 6.4059 | 0 | 0 | 25.937 | 0 | 0 | 57.1167 | 2.859% | CZ 2B | 0 | 0 | 0.56642 | 0.07985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4546 | 2.859% | CZ 2B | 29.4028 | 10.2119 | 61.9093 | 8.7276 | 0 | 143.6064 | 0 | 76.1357 | 0 | 0 | 67.0636 | 0 | 0 | 469.1836 | 0 | 0 | 866.241 | 2.859%
CZ 3A | 0.29867 | 0.10369 | 0.63308 | 0.48252 | 0 | 1.1161 | 0 | 0.68201 | 0 | 0 | 0.67587 | 0 | 0 | 4.5293 | 0 | 0 | 8.5212 | 19.57% | CZ 3A | 9.5866 | 3.3282 | 64.6001 | 49.2365 | 0 | 35.8256 | 0 | 21.8911 | 0 | 0 | 21.694 | 0 | 0 | 269.3289 | 0 | 0 | 475.491 | 19.57% | CZ 3A | 2.8097 | 0.97544 | 0 | 0 | 0 | 10.4999 | 0 | 6.4159 | 0 | 0 | 6.3582 | 0 | 0 | 25.937 | 0 | 0 | 52.9961 | 19.57% | CZ 3A | 0 | 0 | 0.646 | 0.49236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.9467 | 19.57% | CZ 3A | 29.4145 | 10.2119 | 70.6079 | 53.8155 | 0 | 109.9234 | 0 | 67.1683 | 0 | 0 | 66.5635 | 0 | 0 | 469.1836 | 0 | 0 | 876.8885 | 19.57%
CZ 3B | 0.29938 | 0.10369 | 0.61251 | 0.26577 | 0 | 1.0051 | 0 | 0.7374 | 0 | 0 | 0.6741 | 0 | 0 | 4.5293 | 0 | 0 | 8.2272 | 6.098% | CZ 3B | 9.6094 | 3.3282 | 62.5006 | 27.1195 | 0 | 32.2624 | 0 | 23.669 | 0 | 0 | 21.6372 | 0 | 0 | 269.3289 | 0 | 0 | 449.455 | 6.098% | CZ 3B | 2.8163 | 0.97544 | 0 | 0 | 0 | 9.4556 | 0 | 6.937 | 0 | 0 | 6.3415 | 0 | 0 | 25.937 | 0 | 0 | 52.4628 | 6.098% | CZ 3B | 0 | 0 | 0.62501 | 0.27119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.7045 | 6.098% | CZ 3B | 29.4843 | 10.2119 | 68.3132 | 29.6416 | 0 | 98.9904 | 0 | 72.6232 | 0 | 0 | 66.389 | 0 | 0 | 469.1836 | 0 | 0 | 844.837 | 6.098%
CZ 3C | 0.30044 | 0.10404 | 0.64151 | 0.11866 | 0 | 0.38641 | 0 | 0.57809 | 0 | 0 | 0.68142 | 0 | 0 | 4.5293 | 0 | 0 | 7.3398 | 0.5719% | CZ 3C | 9.6435 | 3.3396 | 65.4604 | 12.1083 | 0 | 12.4031 | 0 | 18.5553 | 0 | 0 | 21.8722 | 0 | 0 | 269.3289 | 0 | 0 | 412.7111 | 0.5719% | CZ 3C | 2.8263 | 0.97878 | 0 | 0 | 0 | 3.6351 | 0 | 5.4383 | 0 | 0 | 6.4104 | 0 | 0 | 25.937 | 0 | 0 | 45.2259 | 0.5719% | CZ 3C | 0 | 0 | 0.6546 | 0.12108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.584 | 0.5719% | CZ 3C | 29.5889 | 10.2468 | 71.5482 | 13.2343 | 0 | 38.0562 | 0 | 56.9331 | 0 | 0 | 67.1101 | 0 | 0 | 469.1836 | 0 | 0 | 755.9013 | 0.5719%
CZ 4A | 0.3002 | 0.10428 | 0.6973 | 0.80559 | 0 | 0.68556 | 0 | 0.59604 | 0 | 0 | 0.66477 | 0 | 0 | 4.5293 | 0 | 0 | 8.383 | 16.6% | CZ 4A | 9.6359 | 3.3472 | 71.1526 | 82.2035 | 0 | 22.0048 | 0 | 19.1315 | 0 | 0 | 21.3377 | 0 | 0 | 269.3289 | 0 | 0 | 498.1421 | 16.6% | CZ 4A | 2.8241 | 0.981 | 0 | 0 | 0 | 6.4493 | 0 | 5.6071 | 0 | 0 | 6.2537 | 0 | 0 | 25.937 | 0 | 0 | 48.0522 | 16.6% | CZ 4A | 0 | 0 | 0.71153 | 0.82204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.3419 | 16.6% | CZ 4A | 29.5657 | 10.2701 | 77.7698 | 89.8485 | 0 | 67.5172 | 0 | 58.701 | 0 | 0 | 65.4702 | 0 | 0 | 469.1836 | 0 | 0 | 868.326 | 16.6%
CZ 4B | 0.29879 | 0.10369 | 0.6791 | 0.46558 | 0 | 0.5834 | 0 | 0.66276 | 0 | 0 | 0.66489 | 0 | 0 | 4.5293 | 0 | 0 | 7.9875 | 0.604% | CZ 4B | 9.5904 | 3.3282 | 69.2956 | 47.5083 | 0 | 18.7259 | 0 | 21.2732 | 0 | 0 | 21.3415 | 0 | 0 | 269.3289 | 0 | 0 | 460.3921 | 0.604% | CZ 4B | 2.8108 | 0.97544 | 0 | 0 | 0 | 5.4883 | 0 | 6.2348 | 0 | 0 | 6.2548 | 0 | 0 | 25.937 | 0 | 0 | 47.7011 | 0.604% | CZ 4B | 0 | 0 | 0.69296 | 0.47508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.9764 | 0.604% | CZ 4B | 29.4261 | 10.2119 | 75.7401 | 51.9266 | 0 | 57.4565 | 0 | 65.2725 | 0 | 0 | 65.4818 | 0 | 0 | 469.1836 | 0 | 0 | 824.6991 | 0.604%
CZ 4C | 0.30032 | 0.10428 | 0.71672 | 0.54231 | 0 | 0.17006 | 0 | 0.5423 | 0 | 0 | 0.6617 | 0 | 0 | 4.5293 | 0 | 0 | 7.567 | 1.378% | CZ 4C | 9.6397 | 3.3472 | 73.1346 | 55.338 | 0 | 5.4586 | 0 | 17.4068 | 0 | 0 | 21.2391 | 0 | 0 | 269.3289 | 0 | 0 | 454.8928 | 1.378% | CZ 4C | 2.8252 | 0.981 | 0 | 0 | 0 | 1.5998 | 0 | 5.1016 | 0 | 0 | 6.2248 | 0 | 0 | 25.937 | 0 | 0 | 42.6695 | 1.378% | CZ 4C | 0 | 0 | 0.73135 | 0.55338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.093 | 1.378% | CZ 4C | 29.5773 | 10.2701 | 79.9362 | 60.4844 | 0 | 16.7485 | 0 | 53.409 | 0 | 0 | 65.1678 | 0 | 0 | 469.1836 | 0 | 0 | 784.7767 | 1.378%
CZ 5A | 0.29914 | 0.10381 | 0.75122 | 1.2589 | 0 | 0.37496 | 0 | 0.57407 | 0 | 0 | 0.65851 | 0 | 0 | 4.5293 | 0 | 0 | 8.5499 | 20.38% | CZ 5A | 9.6018 | 3.332 | 76.6553 | 128.4612 | 0 | 12.0354 | 0 | 18.4265 | 0 | 0 | 21.1368 | 0 | 0 | 269.3289 | 0 | 0 | 538.9778 | 20.38% | CZ 5A | 2.8141 | 0.97655 | 0 | 0 | 0 | 3.5274 | 0 | 5.4005 | 0 | 0 | 6.1948 | 0 | 0 | 25.937 | 0 | 0 | 44.8504 | 20.38% | CZ 5A | 0 | 0 | 0.76655 | 1.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8595 | 20.38% | CZ 5A | 29.461 | 10.2235 | 83.7843 | 140.4081 | 0 | 36.928 | 0 | 56.5377 | 0 | 0 | 64.8538 | 0 | 0 | 469.1836 | 0 | 0 | 891.38 | 20.38%
CZ 5B | 0.29938 | 0.10404 | 0.73596 | 0.93094 | 0 | 0.39905 | 0 | 0.66359 | 0 | 0 | 0.65851 | 0 | 0 | 4.5293 | 0 | 0 | 8.3207 | 5.254% | CZ 5B | 9.6094 | 3.3396 | 75.0977 | 94.9939 | 0 | 12.8087 | 0 | 21.2998 | 0 | 0 | 21.1368 | 0 | 0 | 269.3289 | 0 | 0 | 507.6147 | 5.254% | CZ 5B | 2.8163 | 0.97878 | 0 | 0 | 0 | 3.754 | 0 | 6.2426 | 0 | 0 | 6.1948 | 0 | 0 | 25.937 | 0 | 0 | 45.9236 | 5.254% | CZ 5B | 0 | 0 | 0.75098 | 0.94994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5092 | 5.254% | CZ 5B | 29.4843 | 10.2468 | 82.0818 | 103.8284 | 0 | 39.3007 | 0 | 65.3539 | 0 | 0 | 64.8538 | 0 | 0 | 469.1836 | 0 | 0 | 864.3332 | 5.254%
CZ 5C | 0.3002 | 0.10416 | 0.74773 | 0.71423 | 0 | 0.064954 | 0 | 0.52364 | 0 | 0 | 0.65579 | 0 | 0 | 4.5293 | 0 | 0 | 7.64 | 0.02535% | CZ 5C | 9.6359 | 3.3434 | 76.2991 | 72.8807 | 0 | 2.0849 | 0 | 16.8078 | 0 | 0 | 21.0496 | 0 | 0 | 269.3289 | 0 | 0 | 471.4302 | 0.02535% | CZ 5C | 2.8241 | 0.97989 | 0 | 0 | 0 | 0.61104 | 0 | 4.9261 | 0 | 0 | 6.1693 | 0 | 0 | 25.937 | 0 | 0 | 41.4474 | 0.02535% | CZ 5C | 0 | 0 | 0.76299 | 0.72881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.3001 | 0.02535% | CZ 5C | 29.5657 | 10.2584 | 83.3949 | 79.6586 | 0 | 6.397 | 0 | 51.5713 | 0 | 0 | 64.5862 | 0 | 0 | 469.1836 | 0 | 0 | 794.6157 | 0.02535%
CZ 6A | 0.29938 | 0.10404 | 0.79096 | 1.8503 | 0 | 0.4111 | 0 | 0.60986 | 0 | 0 | 0.65603 | 0 | 0 | 4.5293 | 0 | 0 | 9.251 | 3.192% | CZ 6A | 9.6094 | 3.3396 | 80.7104 | 188.8093 | 0 | 13.1953 | 0 | 19.575 | 0 | 0 | 21.0572 | 0 | 0 | 269.3289 | 0 | 0 | 605.6249 | 3.192% | CZ 6A | 2.8163 | 0.97878 | 0 | 0 | 0 | 3.8673 | 0 | 5.7371 | 0 | 0 | 6.1715 | 0 | 0 | 25.937 | 0 | 0 | 45.5081 | 3.192% | CZ 6A | 0 | 0 | 0.8071 | 1.8881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.5035 | 3.192% | CZ 6A | 29.4843 | 10.2468 | 88.2164 | 206.3685 | 0 | 40.4871 | 0 | 60.0618 | 0 | 0 | 64.6095 | 0 | 0 | 469.1836 | 0 | 0 | 968.658 | 3.192%
CZ 6B | 0.29879 | 0.10381 | 0.78108 | 1.4089 | 0 | 0.25533 | 0 | 0.63666 | 0 | 0 | 0.65296 | 0 | 0 | 4.5293 | 0 | 0 | 8.6668 | 0.5438% | CZ 6B | 9.5904 | 3.332 | 79.7023 | 143.7643 | 0 | 8.1954 | 0 | 20.4355 | 0 | 0 | 20.9586 | 0 | 0 | 269.3289 | 0 | 0 | 555.3074 | 0.5438% | CZ 6B | 2.8108 | 0.97655 | 0 | 0 | 0 | 2.4019 | 0 | 5.9893 | 0 | 0 | 6.1426 | 0 | 0 | 25.937 | 0 | 0 | 44.2582 | 0.5438% | CZ 6B | 0 | 0 | 0.79702 | 1.4376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.043 | 0.5438% | CZ 6B | 29.4261 | 10.2235 | 87.1146 | 157.1343 | 0 | 25.1459 | 0 | 62.702 | 0 | 0 | 64.3071 | 0 | 0 | 469.1836 | 0 | 0 | 905.2372 | 0.5438%
CZ 7 | 0.29914 | 0.10428 | 0.83828 | 2.3516 | 0 | 0.28154 | 0 | 0.60112 | 0 | 0 | 0.65213 | 0 | 0 | 4.5293 | 0 | 0 | 9.6574 | 0.271% | CZ 7 | 9.6018 | 3.3472 | 85.5385 | 239.9633 | 0 | 9.037 | 0 | 19.2945 | 0 | 0 | 20.9321 | 0 | 0 | 269.3289 | 0 | 0 | 657.0432 | 0.271% | CZ 7 | 2.8141 | 0.981 | 0 | 0 | 0 | 2.6486 | 0 | 5.6549 | 0 | 0 | 6.1348 | 0 | 0 | 25.937 | 0 | 0 | 44.1704 | 0.271% | CZ 7 | 0 | 0 | 0.85539 | 2.3996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.0633 | 0.271% | CZ 7 | 29.461 | 10.2701 | 93.4936 | 262.2799 | 0 | 27.728 | 0 | 59.2011 | 0 | 0 | 64.2257 | 0 | 0 | 469.1836 | 0 | 0 | 1015.843 | 0.271%
CZ 8 | 0.30363 | 0.10617 | 0.90208 | 3.33 | 0 | 0.087156 | 0 | 0.601 | 0 | 0 | 0.64576 | 0 | 0 | 4.5293 | 0 | 0 | 10.5051 | 0.008189% | CZ 8 | 9.7458 | 3.4078 | 92.0493 | 339.8006 | 0 | 2.7975 | 0 | 19.2907 | 0 | 0 | 20.7274 | 0 | 0 | 269.3289 | 0 | 0 | 757.148 | 0.008189% | CZ 8 | 2.8563 | 0.99877 | 0 | 0 | 0 | 0.8199 | 0 | 5.6538 | 0 | 0 | 6.0749 | 0 | 0 | 25.937 | 0 | 0 | 42.3406 | 0.008189% | CZ 8 | 0 | 0 | 0.92049 | 3.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.1268 | 0.008189% | CZ 8 | 29.903 | 10.4562 | 100.6099 | 371.402 | 0 | 8.5836 | 0 | 59.1895 | 0 | 0 | 63.5976 | 0 | 0 | 469.1836 | 0 | 0 | 1112.9253 | 0.008189%
US Weighted | 0.29915 | 0.10383 | 0.65808 | 0.6553 | 0 | 1.0467 | 0 | 0.65509 | 0 | 0 | 0.67217 | 0 | 0 | 4.5293 | 0 | 0 | 8.6195 | 100% | US Weighted | 9.6022 | 3.3328 | 67.1511 | 66.8672 | 0 | 33.5954 | 0 | 21.0269 | 0 | 0 | 21.5751 | 0 | 0 | 269.3289 | 0 | 0 | 492.4796 | 100% | US Weighted | 2.8142 | 0.97679 | 0 | 0 | 0 | 9.8463 | 0 | 6.1626 | 0 | 0 | 6.3233 | 0 | 0 | 25.937 | 0 | 0 | 52.0602 | 100% | US Weighted | 0 | 0 | 0.67151 | 0.66867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1485 | 100% | US Weighted | 29.4623 | 10.2261 | 73.3961 | 73.0858 | 0 | 103.0805 | 0 | 64.5165 | 0 | 0 | 66.1988 | 0 | 0 | 469.1836 | 0 | 0 | 889.1496 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.32193 | 0.10381 | 0.46224 | 0 | 0 | 4.2666 | 0 | 0.93616 | 0 | 0 | 1.0743 | 0 | 0 | 4.5293 | 0 | 0 | 11.6943 | 0% | CZ 0A | 10.3334 | 3.332 | 47.1673 | 0 | 0 | 136.9494 | 0 | 30.0487 | 0 | 0 | 34.4837 | 0 | 0 | 269.3289 | 0 | 0 | 531.6433 | 0% | CZ 0A | 3.0285 | 0.97655 | 0 | 0 | 0 | 40.1376 | 0 | 8.8068 | 0 | 0 | 10.1066 | 0 | 0 | 25.937 | 0 | 0 | 88.993 | 0% | CZ 0A | 0 | 0 | 0.47167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.28 | 0% | CZ 0A | 31.7058 | 10.2235 | 51.5538 | 0 | 0 | 420.2002 | 0 | 92.1979 | 0 | 0 | 105.8061 | 0 | 0 | 469.1836 | 0 | 0 | 1180.8709 | 0%
CZ 0B | 0.32122 | 0.10381 | 0.46035 | 0.00033426 | 0 | 3.7968 | 0 | 0.93179 | 0 | 0 | 1.0658 | 0 | 0 | 4.5293 | 0 | 0 | 11.2094 | 0% | CZ 0B | 10.3106 | 3.332 | 46.974 | 0.034108 | 0 | 121.8701 | 0 | 29.9084 | 0 | 0 | 34.2108 | 0 | 0 | 269.3289 | 0 | 0 | 515.9689 | 0% | CZ 0B | 3.0219 | 0.97655 | 0 | 0 | 0 | 35.7181 | 0 | 8.7657 | 0 | 0 | 10.0266 | 0 | 0 | 25.937 | 0 | 0 | 84.4458 | 0% | CZ 0B | 0 | 0 | 0.46974 | 0.00034108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2784 | 0% | CZ 0B | 31.636 | 10.2235 | 51.3426 | 0.03728 | 0 | 373.9326 | 0 | 91.7676 | 0 | 0 | 104.9686 | 0 | 0 | 469.1836 | 0 | 0 | 1133.0917 | 0%
CZ 1A | 0.32146 | 0.10381 | 0.50428 | 0 | 0 | 2.6518 | 0 | 0.7074 | 0 | 0 | 1.0548 | 0 | 0 | 4.5293 | 0 | 0 | 9.8728 | 2.382% | CZ 1A | 10.3182 | 3.332 | 51.4573 | 0 | 0 | 85.1157 | 0 | 22.7061 | 0 | 0 | 33.8583 | 0 | 0 | 269.3289 | 0 | 0 | 476.1165 | 2.382% | CZ 1A | 3.0241 | 0.97655 | 0 | 0 | 0 | 24.946 | 0 | 6.6548 | 0 | 0 | 9.9233 | 0 | 0 | 25.937 | 0 | 0 | 71.4617 | 2.382% | CZ 1A | 0 | 0 | 0.51457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3229 | 2.382% | CZ 1A | 31.6592 | 10.2235 | 56.2428 | 0 | 0 | 261.1596 | 0 | 69.6689 | 0 | 0 | 103.887 | 0 | 0 | 469.1836 | 0 | 0 | 1002.0247 | 2.382%
CZ 1B | 0.32217 | 0.10357 | 0.50532 | 0.033314 | 0 | 2.9013 | 0 | 0.88916 | 0 | 0 | 1.054 | 0 | 0 | 4.5293 | 0 | 0 | 10.3381 | 0% | CZ 1B | 10.341 | 3.3244 | 51.5634 | 3.3994 | 0 | 93.1254 | 0 | 28.54 | 0 | 0 | 33.8317 | 0 | 0 | 269.3289 | 0 | 0 | 493.4541 | 0% | CZ 1B | 3.0308 | 0.97433 | 0 | 0 | 0 | 27.2935 | 0 | 8.3646 | 0 | 0 | 9.9155 | 0 | 0 | 25.937 | 0 | 0 | 75.5157 | 0% | CZ 1B | 0 | 0 | 0.51563 | 0.033994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3579 | 0% | CZ 1B | 31.729 | 10.2003 | 56.3588 | 3.7156 | 0 | 285.7357 | 0 | 87.5688 | 0 | 0 | 103.8055 | 0 | 0 | 469.1836 | 0 | 0 | 1048.2972 | 0%
CZ 2A | 0.32028 | 0.10357 | 0.55145 | 0.093443 | 0 | 2.2563 | 0 | 0.75712 | 0 | 0 | 1.0472 | 0 | 0 | 4.5293 | 0 | 0 | 9.6585 | 20.26% | CZ 2A | 10.2803 | 3.3244 | 56.2702 | 9.535 | 0 | 72.4208 | 0 | 24.302 | 0 | 0 | 33.6119 | 0 | 0 | 269.3289 | 0 | 0 | 479.0735 | 20.26% | CZ 2A | 3.013 | 0.97433 | 0 | 0 | 0 | 21.2253 | 0 | 7.1225 | 0 | 0 | 9.8511 | 0 | 0 | 25.937 | 0 | 0 | 68.1232 | 20.26% | CZ 2A | 0 | 0 | 0.5627 | 0.09535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4664 | 20.26% | CZ 2A | 31.5429 | 10.2003 | 61.5034 | 10.4218 | 0 | 222.2078 | 0 | 74.5655 | 0 | 0 | 103.131 | 0 | 0 | 469.1836 | 0 | 0 | 982.7562 | 20.26%
CZ 2B | 0.31993 | 0.10369 | 0.55498 | 0.078253 | 0 | 1.5389 | 0 | 0.79385 | 0 | 0 | 1.0264 | 0 | 0 | 4.5293 | 0 | 0 | 8.9453 | 2.859% | CZ 2B | 10.2689 | 3.3282 | 56.6303 | 7.985 | 0 | 49.3962 | 0 | 25.4809 | 0 | 0 | 32.9447 | 0 | 0 | 269.3289 | 0 | 0 | 455.3631 | 2.859% | CZ 2B | 3.0097 | 0.97544 | 0 | 0 | 0 | 14.4772 | 0 | 7.468 | 0 | 0 | 9.6555 | 0 | 0 | 25.937 | 0 | 0 | 61.5229 | 2.859% | CZ 2B | 0 | 0 | 0.5663 | 0.07985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4545 | 2.859% | CZ 2B | 31.508 | 10.2119 | 61.8969 | 8.7276 | 0 | 151.5619 | 0 | 78.1827 | 0 | 0 | 101.0839 | 0 | 0 | 469.1836 | 0 | 0 | 912.3566 | 2.859%
CZ 3A | 0.32075 | 0.10369 | 0.63297 | 0.49084 | 0 | 1.1903 | 0 | 0.70339 | 0 | 0 | 1.0195 | 0 | 0 | 4.5293 | 0 | 0 | 8.9907 | 19.57% | CZ 3A | 10.2955 | 3.3282 | 64.5888 | 50.0854 | 0 | 38.2062 | 0 | 22.5772 | 0 | 0 | 32.7249 | 0 | 0 | 269.3289 | 0 | 0 | 491.1349 | 19.57% | CZ 3A | 3.0174 | 0.97544 | 0 | 0 | 0 | 11.1976 | 0 | 6.617 | 0 | 0 | 9.5911 | 0 | 0 | 25.937 | 0 | 0 | 57.3356 | 19.57% | CZ 3A | 0 | 0 | 0.64589 | 0.50085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.9551 | 19.57% | CZ 3A | 31.5895 | 10.2119 | 70.5955 | 54.7433 | 0 | 117.2276 | 0 | 69.2735 | 0 | 0 | 100.4093 | 0 | 0 | 469.1836 | 0 | 0 | 923.2341 | 19.57%
CZ 3B | 0.32122 | 0.10369 | 0.61239 | 0.26785 | 0 | 1.0691 | 0 | 0.75027 | 0 | 0 | 1.0147 | 0 | 0 | 4.5293 | 0 | 0 | 8.6685 | 6.098% | CZ 3B | 10.3106 | 3.3282 | 62.4892 | 27.3317 | 0 | 34.3169 | 0 | 24.0821 | 0 | 0 | 32.5694 | 0 | 0 | 269.3289 | 0 | 0 | 463.7571 | 6.098% | CZ 3B | 3.0219 | 0.97544 | 0 | 0 | 0 | 10.0577 | 0 | 7.0581 | 0 | 0 | 9.5456 | 0 | 0 | 25.937 | 0 | 0 | 56.5957 | 6.098% | CZ 3B | 0 | 0 | 0.62489 | 0.27332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.7065 | 6.098% | CZ 3B | 31.636 | 10.2119 | 68.3007 | 29.8735 | 0 | 105.2943 | 0 | 73.8909 | 0 | 0 | 99.9325 | 0 | 0 | 469.1836 | 0 | 0 | 888.3234 | 6.098%
CZ 3C | 0.323 | 0.10404 | 0.64136 | 0.11621 | 0 | 0.42515 | 0 | 0.59757 | 0 | 0 | 1.03 | 0 | 0 | 4.5293 | 0 | 0 | 7.7666 | 0.5719% | CZ 3C | 10.3675 | 3.3396 | 65.4452 | 11.8581 | 0 | 13.6464 | 0 | 19.1808 | 0 | 0 | 33.0622 | 0 | 0 | 269.3289 | 0 | 0 | 426.2287 | 0.5719% | CZ 3C | 3.0385 | 0.97878 | 0 | 0 | 0 | 3.9995 | 0 | 5.6216 | 0 | 0 | 9.69 | 0 | 0 | 25.937 | 0 | 0 | 49.2654 | 0.5719% | CZ 3C | 0 | 0 | 0.65445 | 0.11858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.5814 | 0.5719% | CZ 3C | 31.8104 | 10.2468 | 71.5316 | 12.9609 | 0 | 41.8711 | 0 | 58.8522 | 0 | 0 | 101.4445 | 0 | 0 | 469.1836 | 0 | 0 | 797.9012 | 0.5719%
CZ 4A | 0.323 | 0.10428 | 0.69715 | 0.8131 | 0 | 0.73835 | 0 | 0.61411 | 0 | 0 | 1.0005 | 0 | 0 | 4.5293 | 0 | 0 | 8.8197 | 16.6% | CZ 4A | 10.3675 | 3.3472 | 71.1374 | 82.9691 | 0 | 23.6993 | 0 | 19.7115 | 0 | 0 | 32.1146 | 0 | 0 | 269.3289 | 0 | 0 | 512.6753 | 16.6% | CZ 4A | 3.0385 | 0.981 | 0 | 0 | 0 | 6.9459 | 0 | 5.7771 | 0 | 0 | 9.4122 | 0 | 0 | 25.937 | 0 | 0 | 52.0917 | 16.6% | CZ 4A | 0 | 0 | 0.71137 | 0.82969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.3494 | 16.6% | CZ 4A | 31.8104 | 10.2701 | 77.7532 | 90.6852 | 0 | 72.7162 | 0 | 60.4805 | 0 | 0 | 98.5368 | 0 | 0 | 469.1836 | 0 | 0 | 911.436 | 16.6%
CZ 4B | 0.32028 | 0.10369 | 0.67899 | 0.48553 | 0 | 0.62237 | 0 | 0.67882 | 0 | 0 | 0.99851 | 0 | 0 | 4.5293 | 0 | 0 | 8.4174 | 0.604% | CZ 4B | 10.2803 | 3.3282 | 69.2843 | 49.5434 | 0 | 19.9768 | 0 | 21.7888 | 0 | 0 | 32.0501 | 0 | 0 | 269.3289 | 0 | 0 | 475.5808 | 0.604% | CZ 4B | 3.013 | 0.97544 | 0 | 0 | 0 | 5.8549 | 0 | 6.3859 | 0 | 0 | 9.3934 | 0 | 0 | 25.937 | 0 | 0 | 51.5596 | 0.604% | CZ 4B | 0 | 0 | 0.69284 | 0.49543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.9966 | 0.604% | CZ 4B | 31.5429 | 10.2119 | 75.7277 | 54.151 | 0 | 61.2947 | 0 | 66.8543 | 0 | 0 | 98.339 | 0 | 0 | 469.1836 | 0 | 0 | 867.3051 | 0.604%
CZ 4C | 0.32347 | 0.10428 | 0.7165 | 0.53942 | 0 | 0.19014 | 0 | 0.55836 | 0 | 0 | 0.99603 | 0 | 0 | 4.5293 | 0 | 0 | 7.9575 | 1.378% | CZ 4C | 10.3826 | 3.3472 | 73.1119 | 55.0424 | 0 | 6.103 | 0 | 17.9223 | 0 | 0 | 31.9705 | 0 | 0 | 269.3289 | 0 | 0 | 467.2087 | 1.378% | CZ 4C | 3.043 | 0.981 | 0 | 0 | 0 | 1.7887 | 0 | 5.2527 | 0 | 0 | 9.37 | 0 | 0 | 25.937 | 0 | 0 | 46.3724 | 1.378% | CZ 4C | 0 | 0 | 0.73112 | 0.55042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.0899 | 1.378% | CZ 4C | 31.857 | 10.2701 | 79.9113 | 60.1613 | 0 | 18.7257 | 0 | 54.9908 | 0 | 0 | 98.0948 | 0 | 0 | 469.1836 | 0 | 0 | 823.1945 | 1.378%
CZ 5A | 0.32134 | 0.10381 | 0.75111 | 1.2913 | 0 | 0.4085 | 0 | 0.59273 | 0 | 0 | 0.98918 | 0 | 0 | 4.5293 | 0 | 0 | 8.9872 | 20.38% | CZ 5A | 10.3144 | 3.332 | 76.644 | 131.7659 | 0 | 13.1119 | 0 | 19.0254 | 0 | 0 | 31.7507 | 0 | 0 | 269.3289 | 0 | 0 | 555.2731 | 20.38% | CZ 5A | 3.023 | 0.97655 | 0 | 0 | 0 | 3.8429 | 0 | 5.576 | 0 | 0 | 9.3056 | 0 | 0 | 25.937 | 0 | 0 | 48.661 | 20.38% | CZ 5A | 0 | 0 | 0.76644 | 1.3177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8924 | 20.38% | CZ 5A | 31.6476 | 10.2235 | 83.7718 | 144.0201 | 0 | 40.2312 | 0 | 58.3754 | 0 | 0 | 97.4202 | 0 | 0 | 469.1836 | 0 | 0 | 934.8734 | 20.38%
CZ 5B | 0.32122 | 0.10404 | 0.73585 | 0.95638 | 0 | 0.42716 | 0 | 0.67788 | 0 | 0 | 0.98765 | 0 | 0 | 4.5293 | 0 | 0 | 8.7394 | 5.254% | CZ 5B | 10.3106 | 3.3396 | 75.0864 | 97.5899 | 0 | 13.7109 | 0 | 21.7585 | 0 | 0 | 31.7014 | 0 | 0 | 269.3289 | 0 | 0 | 522.826 | 5.254% | CZ 5B | 3.0219 | 0.97878 | 0 | 0 | 0 | 4.0184 | 0 | 6.377 | 0 | 0 | 9.2911 | 0 | 0 | 25.937 | 0 | 0 | 49.6242 | 5.254% | CZ 5B | 0 | 0 | 0.75086 | 0.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5351 | 5.254% | CZ 5B | 31.636 | 10.2468 | 82.0694 | 106.6658 | 0 | 42.0689 | 0 | 66.7612 | 0 | 0 | 97.269 | 0 | 0 | 469.1836 | 0 | 0 | 905.9006 | 5.254%
CZ 5C | 0.32311 | 0.10416 | 0.74743 | 0.70294 | 0 | 0.078417 | 0 | 0.53699 | 0 | 0 | 0.9867 | 0 | 0 | 4.5293 | 0 | 0 | 8.009 | 0.02535% | CZ 5C | 10.3713 | 3.3434 | 76.2688 | 71.7286 | 0 | 2.517 | 0 | 17.2362 | 0 | 0 | 31.6711 | 0 | 0 | 269.3289 | 0 | 0 | 482.4652 | 0.02535% | CZ 5C | 3.0396 | 0.97989 | 0 | 0 | 0 | 0.73769 | 0 | 5.0516 | 0 | 0 | 9.2823 | 0 | 0 | 25.937 | 0 | 0 | 45.0281 | 0.02535% | CZ 5C | 0 | 0 | 0.76269 | 0.71729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2883 | 0.02535% | CZ 5C | 31.8221 | 10.2584 | 83.3618 | 78.3994 | 0 | 7.7229 | 0 | 52.8856 | 0 | 0 | 97.1759 | 0 | 0 | 469.1836 | 0 | 0 | 830.8097 | 0.02535%
CZ 6A | 0.32134 | 0.10404 | 0.79078 | 1.9095 | 0 | 0.447 | 0 | 0.63099 | 0 | 0 | 0.9847 | 0 | 0 | 4.5293 | 0 | 0 | 9.7176 | 3.192% | CZ 6A | 10.3144 | 3.3396 | 80.6914 | 194.8463 | 0 | 14.3477 | 0 | 20.2536 | 0 | 0 | 31.6066 | 0 | 0 | 269.3289 | 0 | 0 | 624.7285 | 3.192% | CZ 6A | 3.023 | 0.97878 | 0 | 0 | 0 | 4.2051 | 0 | 5.936 | 0 | 0 | 9.2634 | 0 | 0 | 25.937 | 0 | 0 | 49.3432 | 3.192% | CZ 6A | 0 | 0 | 0.80691 | 1.9485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.5637 | 3.192% | CZ 6A | 31.6476 | 10.2468 | 88.1957 | 212.967 | 0 | 44.0229 | 0 | 62.1438 | 0 | 0 | 96.9782 | 0 | 0 | 469.1836 | 0 | 0 | 1015.3856 | 3.192%
CZ 6B | 0.32028 | 0.10381 | 0.78093 | 1.4471 | 0 | 0.27257 | 0 | 0.65922 | 0 | 0 | 0.97808 | 0 | 0 | 4.5293 | 0 | 0 | 9.0912 | 0.5438% | CZ 6B | 10.2803 | 3.332 | 79.6871 | 147.6601 | 0 | 8.7489 | 0 | 21.1595 | 0 | 0 | 31.3943 | 0 | 0 | 269.3289 | 0 | 0 | 571.5912 | 0.5438% | CZ 6B | 3.013 | 0.97655 | 0 | 0 | 0 | 2.5641 | 0 | 6.2015 | 0 | 0 | 9.2012 | 0 | 0 | 25.937 | 0 | 0 | 47.8933 | 0.5438% | CZ 6B | 0 | 0 | 0.79687 | 1.4766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.0818 | 0.5438% | CZ 6B | 31.5429 | 10.2235 | 87.098 | 161.3925 | 0 | 26.8441 | 0 | 64.9235 | 0 | 0 | 96.3269 | 0 | 0 | 469.1836 | 0 | 0 | 947.5351 | 0.5438%
CZ 7 | 0.32075 | 0.10428 | 0.83813 | 2.4368 | 0 | 0.31107 | 0 | 0.6258 | 0 | 0 | 0.97737 | 0 | 0 | 4.5293 | 0 | 0 | 10.1435 | 0.271% | CZ 7 | 10.2955 | 3.3472 | 85.5233 | 248.6532 | 0 | 9.9846 | 0 | 20.0868 | 0 | 0 | 31.3716 | 0 | 0 | 269.3289 | 0 | 0 | 678.5911 | 0.271% | CZ 7 | 3.0174 | 0.981 | 0 | 0 | 0 | 2.9263 | 0 | 5.8871 | 0 | 0 | 9.1945 | 0 | 0 | 25.937 | 0 | 0 | 47.9433 | 0.271% | CZ 7 | 0 | 0 | 0.85523 | 2.4865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.1501 | 0.271% | CZ 7 | 31.5895 | 10.2701 | 93.477 | 271.778 | 0 | 30.6357 | 0 | 61.632 | 0 | 0 | 96.2571 | 0 | 0 | 469.1836 | 0 | 0 | 1064.8229 | 0.271%
CZ 8 | 0.32819 | 0.10617 | 0.9019 | 3.394 | 0 | 0.10133 | 0 | 0.61978 | 0 | 0 | 0.96639 | 0 | 0 | 4.5293 | 0 | 0 | 10.947 | 0.008189% | CZ 8 | 10.5343 | 3.4078 | 92.0304 | 346.3303 | 0 | 3.2524 | 0 | 19.8934 | 0 | 0 | 31.0191 | 0 | 0 | 269.3289 | 0 | 0 | 775.7965 | 0.008189% | CZ 8 | 3.0874 | 0.99877 | 0 | 0 | 0 | 0.95322 | 0 | 5.8304 | 0 | 0 | 9.0912 | 0 | 0 | 25.937 | 0 | 0 | 45.898 | 0.008189% | CZ 8 | 0 | 0 | 0.9203 | 3.4633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.1919 | 0.008189% | CZ 8 | 32.3222 | 10.4562 | 100.5892 | 378.539 | 0 | 9.9793 | 0 | 61.0388 | 0 | 0 | 95.1754 | 0 | 0 | 469.1836 | 0 | 0 | 1157.2837 | 0.008189%
US Weighted | 0.32126 | 0.10383 | 0.65797 | 0.66889 | 0 | 1.1161 | 0 | 0.67554 | 0 | 0 | 1.013 | 0 | 0 | 4.5293 | 0 | 0 | 9.0859 | 100% | US Weighted | 10.3118 | 3.3328 | 67.1396 | 68.2538 | 0 | 35.825 | 0 | 21.6833 | 0 | 0 | 32.5152 | 0 | 0 | 269.3289 | 0 | 0 | 508.3904 | 100% | US Weighted | 3.0222 | 0.97679 | 0 | 0 | 0 | 10.4997 | 0 | 6.355 | 0 | 0 | 9.5297 | 0 | 0 | 25.937 | 0 | 0 | 56.3204 | 100% | US Weighted | 0 | 0 | 0.6714 | 0.68254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1623 | 100% | US Weighted | 31.6396 | 10.2261 | 73.3835 | 74.6014 | 0 | 109.9216 | 0 | 66.5306 | 0 | 0 | 99.766 | 0 | 0 | 469.1836 | 0 | 0 | 935.2523 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.37827 | 0.18152 | 0.46224 | 0 | 0 | 4.3072 | 0 | 0.94372 | 0 | 0 | 1.0742 | 0 | 0 | 4.5293 | 0 | 0 | 11.8765 | 0% | CZ 0A | 12.1415 | 5.8263 | 47.1673 | 0 | 0 | 138.2534 | 0 | 30.2913 | 0 | 0 | 34.4799 | 0 | 0 | 269.3289 | 0 | 0 | 537.4885 | 0% | CZ 0A | 3.5585 | 1.7076 | 0 | 0 | 0 | 40.5197 | 0 | 8.8779 | 0 | 0 | 10.1055 | 0 | 0 | 25.937 | 0 | 0 | 90.7061 | 0% | CZ 0A | 0 | 0 | 0.47167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.28 | 0% | CZ 0A | 37.2537 | 17.8767 | 51.5538 | 0 | 0 | 424.2012 | 0 | 92.9423 | 0 | 0 | 105.7944 | 0 | 0 | 469.1836 | 0 | 0 | 1198.8057 | 0%
CZ 0B | 0.37756 | 0.1814 | 0.46035 | 0.00033426 | 0 | 3.8332 | 0 | 0.93864 | 0 | 0 | 1.0656 | 0 | 0 | 4.5293 | 0 | 0 | 11.3863 | 0% | CZ 0B | 12.1188 | 5.8225 | 46.974 | 0.034108 | 0 | 123.0376 | 0 | 30.1283 | 0 | 0 | 34.2032 | 0 | 0 | 269.3289 | 0 | 0 | 521.6473 | 0% | CZ 0B | 3.5518 | 1.7065 | 0 | 0 | 0 | 36.0603 | 0 | 8.8301 | 0 | 0 | 10.0244 | 0 | 0 | 25.937 | 0 | 0 | 86.11 | 0% | CZ 0B | 0 | 0 | 0.46974 | 0.00034108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2784 | 0% | CZ 0B | 37.1839 | 17.865 | 51.3426 | 0.03728 | 0 | 377.5149 | 0 | 92.4422 | 0 | 0 | 104.9454 | 0 | 0 | 469.1836 | 0 | 0 | 1150.5148 | 0%
CZ 1A | 0.37838 | 0.18152 | 0.50428 | 0 | 0 | 2.6727 | 0 | 0.71024 | 0 | 0 | 1.0548 | 0 | 0 | 4.5293 | 0 | 0 | 10.0312 | 2.382% | CZ 1A | 12.1453 | 5.8263 | 51.4573 | 0 | 0 | 85.7867 | 0 | 22.7971 | 0 | 0 | 33.8583 | 0 | 0 | 269.3289 | 0 | 0 | 481.1998 | 2.382% | CZ 1A | 3.5596 | 1.7076 | 0 | 0 | 0 | 25.1426 | 0 | 6.6814 | 0 | 0 | 9.9233 | 0 | 0 | 25.937 | 0 | 0 | 72.9515 | 2.382% | CZ 1A | 0 | 0 | 0.51457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3229 | 2.382% | CZ 1A | 37.2653 | 17.8767 | 56.2428 | 0 | 0 | 263.2183 | 0 | 69.9481 | 0 | 0 | 103.887 | 0 | 0 | 469.1836 | 0 | 0 | 1017.6217 | 2.382%
CZ 1B | 0.37909 | 0.18116 | 0.50532 | 0.032943 | 0 | 2.9209 | 0 | 0.89317 | 0 | 0 | 1.0538 | 0 | 0 | 4.5293 | 0 | 0 | 10.4956 | 0% | CZ 1B | 12.1681 | 5.8149 | 51.5634 | 3.3615 | 0 | 93.7547 | 0 | 28.6688 | 0 | 0 | 33.8242 | 0 | 0 | 269.3289 | 0 | 0 | 498.4844 | 0% | CZ 1B | 3.5663 | 1.7042 | 0 | 0 | 0 | 27.4779 | 0 | 8.4024 | 0 | 0 | 9.9133 | 0 | 0 | 25.937 | 0 | 0 | 77.0011 | 0% | CZ 1B | 0 | 0 | 0.51563 | 0.033615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3576 | 0% | CZ 1B | 37.3351 | 17.8418 | 56.3588 | 3.6741 | 0 | 287.6664 | 0 | 87.9643 | 0 | 0 | 103.7823 | 0 | 0 | 469.1836 | 0 | 0 | 1063.8063 | 0%
CZ 2A | 0.37709 | 0.18116 | 0.55149 | 0.093629 | 0 | 2.2731 | 0 | 0.76102 | 0 | 0 | 1.0471 | 0 | 0 | 4.5293 | 0 | 0 | 9.8138 | 20.26% | CZ 2A | 12.1036 | 5.8149 | 56.274 | 9.554 | 0 | 72.9628 | 0 | 24.4271 | 0 | 0 | 33.6081 | 0 | 0 | 269.3289 | 0 | 0 | 484.0734 | 20.26% | CZ 2A | 3.5474 | 1.7042 | 0 | 0 | 0 | 21.3842 | 0 | 7.1592 | 0 | 0 | 9.85 | 0 | 0 | 25.937 | 0 | 0 | 69.5819 | 20.26% | CZ 2A | 0 | 0 | 0.56274 | 0.09554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4666 | 20.26% | CZ 2A | 37.1374 | 17.8418 | 61.5075 | 10.4425 | 0 | 223.8711 | 0 | 74.9493 | 0 | 0 | 103.1193 | 0 | 0 | 469.1836 | 0 | 0 | 998.0524 | 20.26%
CZ 2B | 0.37673 | 0.18128 | 0.55498 | 0.078476 | 0 | 1.5501 | 0 | 0.79728 | 0 | 0 | 1.0263 | 0 | 0 | 4.5293 | 0 | 0 | 9.0944 | 2.859% | CZ 2B | 12.0922 | 5.8187 | 56.6303 | 8.0077 | 0 | 49.7564 | 0 | 25.5908 | 0 | 0 | 32.9409 | 0 | 0 | 269.3289 | 0 | 0 | 460.1659 | 2.859% | CZ 2B | 3.544 | 1.7054 | 0 | 0 | 0 | 14.5828 | 0 | 7.5002 | 0 | 0 | 9.6544 | 0 | 0 | 25.937 | 0 | 0 | 62.9238 | 2.859% | CZ 2B | 0 | 0 | 0.5663 | 0.080077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4547 | 2.859% | CZ 2B | 37.1025 | 17.8534 | 61.8969 | 8.7525 | 0 | 152.6668 | 0 | 78.52 | 0 | 0 | 101.0723 | 0 | 0 | 469.1836 | 0 | 0 | 927.048 | 2.859%
CZ 3A | 0.37768 | 0.18128 | 0.63297 | 0.49474 | 0 | 1.1995 | 0 | 0.70705 | 0 | 0 | 1.0195 | 0 | 0 | 4.5293 | 0 | 0 | 9.142 | 19.57% | CZ 3A | 12.1226 | 5.8187 | 64.5888 | 50.4833 | 0 | 38.5019 | 0 | 22.6948 | 0 | 0 | 32.7249 | 0 | 0 | 269.3289 | 0 | 0 | 496.2636 | 19.57% | CZ 3A | 3.5529 | 1.7054 | 0 | 0 | 0 | 11.2842 | 0 | 6.6515 | 0 | 0 | 9.5911 | 0 | 0 | 25.937 | 0 | 0 | 58.7221 | 19.57% | CZ 3A | 0 | 0 | 0.64589 | 0.50483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.959 | 19.57% | CZ 3A | 37.1955 | 17.8534 | 70.5955 | 55.1782 | 0 | 118.1348 | 0 | 69.634 | 0 | 0 | 100.4093 | 0 | 0 | 469.1836 | 0 | 0 | 938.1844 | 19.57%
CZ 3B | 0.37815 | 0.18128 | 0.61239 | 0.27075 | 0 | 1.0775 | 0 | 0.75405 | 0 | 0 | 1.0147 | 0 | 0 | 4.5293 | 0 | 0 | 8.8181 | 6.098% | CZ 3B | 12.1377 | 5.8187 | 62.4892 | 27.6273 | 0 | 34.5861 | 0 | 24.2034 | 0 | 0 | 32.5694 | 0 | 0 | 269.3289 | 0 | 0 | 468.7608 | 6.098% | CZ 3B | 3.5574 | 1.7054 | 0 | 0 | 0 | 10.1366 | 0 | 7.0936 | 0 | 0 | 9.5456 | 0 | 0 | 25.937 | 0 | 0 | 57.9755 | 6.098% | CZ 3B | 0 | 0 | 0.62489 | 0.27627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.7095 | 6.098% | CZ 3B | 37.2421 | 17.8534 | 68.3007 | 30.1966 | 0 | 106.1201 | 0 | 74.2631 | 0 | 0 | 99.9325 | 0 | 0 | 469.1836 | 0 | 0 | 903.0921 | 6.098%
CZ 3C | 0.37992 | 0.18163 | 0.64136 | 0.11695 | 0 | 0.42881 | 0 | 0.60041 | 0 | 0 | 1.0302 | 0 | 0 | 4.5293 | 0 | 0 | 7.9085 | 0.5719% | CZ 3C | 12.1946 | 5.8301 | 65.4452 | 11.9339 | 0 | 13.7639 | 0 | 19.2718 | 0 | 0 | 33.066 | 0 | 0 | 269.3289 | 0 | 0 | 430.8344 | 0.5719% | CZ 3C | 3.574 | 1.7087 | 0 | 0 | 0 | 4.034 | 0 | 5.6482 | 0 | 0 | 9.6911 | 0 | 0 | 25.937 | 0 | 0 | 50.593 | 0.5719% | CZ 3C | 0 | 0 | 0.65445 | 0.11934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.5821 | 0.5719% | CZ 3C | 37.4165 | 17.8883 | 71.5316 | 13.0438 | 0 | 42.2317 | 0 | 59.1314 | 0 | 0 | 101.4561 | 0 | 0 | 469.1836 | 0 | 0 | 811.883 | 0.5719%
CZ 4A | 0.37945 | 0.18163 | 0.69715 | 0.81328 | 0 | 0.75523 | 0 | 0.61918 | 0 | 0 | 1.0006 | 0 | 0 | 4.5293 | 0 | 0 | 8.9758 | 16.6% | CZ 4A | 12.1794 | 5.8301 | 71.1374 | 82.988 | 0 | 24.2413 | 0 | 19.8745 | 0 | 0 | 32.1184 | 0 | 0 | 269.3289 | 0 | 0 | 517.698 | 16.6% | CZ 4A | 3.5696 | 1.7087 | 0 | 0 | 0 | 7.1047 | 0 | 5.8249 | 0 | 0 | 9.4134 | 0 | 0 | 25.937 | 0 | 0 | 53.5582 | 16.6% | CZ 4A | 0 | 0 | 0.71137 | 0.82988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.3496 | 16.6% | CZ 4A | 37.37 | 17.8883 | 77.7532 | 90.7059 | 0 | 74.3794 | 0 | 60.9807 | 0 | 0 | 98.5484 | 0 | 0 | 469.1836 | 0 | 0 | 926.8095 | 16.6%
CZ 4B | 0.37685 | 0.18116 | 0.67899 | 0.47164 | 0 | 0.63218 | 0 | 0.6826 | 0 | 0 | 0.99851 | 0 | 0 | 4.5293 | 0 | 0 | 8.5512 | 0.604% | CZ 4B | 12.096 | 5.8149 | 69.2843 | 48.1261 | 0 | 20.2915 | 0 | 21.9101 | 0 | 0 | 32.0501 | 0 | 0 | 269.3289 | 0 | 0 | 478.9018 | 0.604% | CZ 4B | 3.5451 | 1.7042 | 0 | 0 | 0 | 5.9471 | 0 | 6.4215 | 0 | 0 | 9.3934 | 0 | 0 | 25.937 | 0 | 0 | 52.9483 | 0.604% | CZ 4B | 0 | 0 | 0.69284 | 0.48126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.9824 | 0.604% | CZ 4B | 37.1141 | 17.8418 | 75.7277 | 52.6018 | 0 | 62.2601 | 0 | 67.2264 | 0 | 0 | 98.339 | 0 | 0 | 469.1836 | 0 | 0 | 880.2945 | 0.604%
CZ 4C | 0.3798 | 0.18163 | 0.7165 | 0.53756 | 0 | 0.19226 | 0 | 0.56451 | 0 | 0 | 0.99627 | 0 | 0 | 4.5293 | 0 | 0 | 8.0978 | 1.378% | CZ 4C | 12.1908 | 5.8301 | 73.1119 | 54.8529 | 0 | 6.1712 | 0 | 18.1194 | 0 | 0 | 31.9781 | 0 | 0 | 269.3289 | 0 | 0 | 471.5832 | 1.378% | CZ 4C | 3.5729 | 1.7087 | 0 | 0 | 0 | 1.8087 | 0 | 5.3105 | 0 | 0 | 9.3722 | 0 | 0 | 25.937 | 0 | 0 | 47.71 | 1.378% | CZ 4C | 0 | 0 | 0.73112 | 0.54853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.088 | 1.378% | CZ 4C | 37.4049 | 17.8883 | 79.9113 | 59.9542 | 0 | 18.9351 | 0 | 55.5956 | 0 | 0 | 98.118 | 0 | 0 | 469.1836 | 0 | 0 | 836.9909 | 1.378%
CZ 5A | 0.37791 | 0.1814 | 0.75107 | 1.3069 | 0 | 0.41393 | 0 | 0.60029 | 0 | 0 | 0.9893 | 0 | 0 | 4.5293 | 0 | 0 | 9.1501 | 20.38% | CZ 5A | 12.1301 | 5.8225 | 76.6402 | 133.3576 | 0 | 13.2863 | 0 | 19.268 | 0 | 0 | 31.7545 | 0 | 0 | 269.3289 | 0 | 0 | 561.588 | 20.38% | CZ 5A | 3.5551 | 1.7065 | 0 | 0 | 0 | 3.894 | 0 | 5.6471 | 0 | 0 | 9.3067 | 0 | 0 | 25.937 | 0 | 0 | 50.0464 | 20.38% | CZ 5A | 0 | 0 | 0.7664 | 1.3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.9083 | 20.38% | CZ 5A | 37.2188 | 17.865 | 83.7677 | 145.7599 | 0 | 40.7662 | 0 | 59.1197 | 0 | 0 | 97.4318 | 0 | 0 | 469.1836 | 0 | 0 | 951.1127 | 20.38%
CZ 5B | 0.37791 | 0.18152 | 0.73585 | 0.96058 | 0 | 0.43212 | 0 | 0.68284 | 0 | 0 | 0.98765 | 0 | 0 | 4.5293 | 0 | 0 | 8.8877 | 5.254% | CZ 5B | 12.1301 | 5.8263 | 75.0864 | 98.0182 | 0 | 13.8701 | 0 | 21.9177 | 0 | 0 | 31.7014 | 0 | 0 | 269.3289 | 0 | 0 | 527.8789 | 5.254% | CZ 5B | 3.5551 | 1.7076 | 0 | 0 | 0 | 4.0651 | 0 | 6.4237 | 0 | 0 | 9.2911 | 0 | 0 | 25.937 | 0 | 0 | 50.9796 | 5.254% | CZ 5B | 0 | 0 | 0.75086 | 0.98018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5394 | 5.254% | CZ 5B | 37.2188 | 17.8767 | 82.0694 | 107.1338 | 0 | 42.5574 | 0 | 67.2497 | 0 | 0 | 97.269 | 0 | 0 | 469.1836 | 0 | 0 | 920.5583 | 5.254%
CZ 5C | 0.3798 | 0.18152 | 0.74743 | 0.70372 | 0 | 0.078889 | 0 | 0.54148 | 0 | 0 | 0.9867 | 0 | 0 | 4.5293 | 0 | 0 | 8.1488 | 0.02535% | CZ 5C | 12.1908 | 5.8263 | 76.2688 | 71.8082 | 0 | 2.5322 | 0 | 17.3802 | 0 | 0 | 31.6711 | 0 | 0 | 269.3289 | 0 | 0 | 487.0064 | 0.02535% | CZ 5C | 3.5729 | 1.7076 | 0 | 0 | 0 | 0.74214 | 0 | 5.0939 | 0 | 0 | 9.2823 | 0 | 0 | 25.937 | 0 | 0 | 46.3357 | 0.02535% | CZ 5C | 0 | 0 | 0.76269 | 0.71808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2891 | 0.02535% | CZ 5C | 37.4049 | 17.8767 | 83.3618 | 78.4864 | 0 | 7.7694 | 0 | 53.3276 | 0 | 0 | 97.1759 | 0 | 0 | 469.1836 | 0 | 0 | 844.5862 | 0.02535%
CZ 6A | 0.37827 | 0.18152 | 0.79078 | 1.9301 | 0 | 0.45042 | 0 | 0.63454 | 0 | 0 | 0.9847 | 0 | 0 | 4.5293 | 0 | 0 | 9.8795 | 3.192% | CZ 6A | 12.1415 | 5.8263 | 80.6914 | 196.9459 | 0 | 14.4576 | 0 | 20.3673 | 0 | 0 | 31.6066 | 0 | 0 | 269.3289 | 0 | 0 | 631.3654 | 3.192% | CZ 6A | 3.5585 | 1.7076 | 0 | 0 | 0 | 4.2373 | 0 | 5.9693 | 0 | 0 | 9.2634 | 0 | 0 | 25.937 | 0 | 0 | 50.673 | 3.192% | CZ 6A | 0 | 0 | 0.80691 | 1.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.5847 | 3.192% | CZ 6A | 37.2537 | 17.8767 | 88.1957 | 215.2618 | 0 | 44.3602 | 0 | 62.4927 | 0 | 0 | 96.9782 | 0 | 0 | 469.1836 | 0 | 0 | 1031.6025 | 3.192%
CZ 6B | 0.3772 | 0.18128 | 0.7809 | 1.4638 | 0 | 0.27446 | 0 | 0.663 | 0 | 0 | 0.97832 | 0 | 0 | 4.5293 | 0 | 0 | 9.2482 | 0.5438% | CZ 6B | 12.1074 | 5.8187 | 79.6833 | 149.3693 | 0 | 8.8095 | 0 | 21.2808 | 0 | 0 | 31.4019 | 0 | 0 | 269.3289 | 0 | 0 | 577.7999 | 0.5438% | CZ 6B | 3.5485 | 1.7054 | 0 | 0 | 0 | 2.5819 | 0 | 6.2371 | 0 | 0 | 9.2034 | 0 | 0 | 25.937 | 0 | 0 | 49.2132 | 0.5438% | CZ 6B | 0 | 0 | 0.79683 | 1.4937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.0988 | 0.5438% | CZ 6B | 37.149 | 17.8534 | 87.0939 | 163.2607 | 0 | 27.0301 | 0 | 65.2957 | 0 | 0 | 96.3502 | 0 | 0 | 469.1836 | 0 | 0 | 963.2165 | 0.5438%
CZ 7 | 0.37756 | 0.18163 | 0.83813 | 2.4598 | 0 | 0.31367 | 0 | 0.62934 | 0 | 0 | 0.97761 | 0 | 0 | 4.5293 | 0 | 0 | 10.307 | 0.271% | CZ 7 | 12.1188 | 5.8301 | 85.5233 | 251.0029 | 0 | 10.068 | 0 | 20.2005 | 0 | 0 | 31.3792 | 0 | 0 | 269.3289 | 0 | 0 | 685.4516 | 0.271% | CZ 7 | 3.5518 | 1.7087 | 0 | 0 | 0 | 2.9508 | 0 | 5.9204 | 0 | 0 | 9.1967 | 0 | 0 | 25.937 | 0 | 0 | 49.2654 | 0.271% | CZ 7 | 0 | 0 | 0.85523 | 2.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.1736 | 0.271% | CZ 7 | 37.1839 | 17.8883 | 93.477 | 274.3462 | 0 | 30.8916 | 0 | 61.9809 | 0 | 0 | 96.2804 | 0 | 0 | 469.1836 | 0 | 0 | 1081.2318 | 0.271%
CZ 8 | 0.385 | 0.18293 | 0.90186 | 3.4386 | 0 | 0.10204 | 0 | 0.62438 | 0 | 0 | 0.96663 | 0 | 0 | 4.5293 | 0 | 0 | 11.1307 | 0.008189% | CZ 8 | 12.3576 | 5.8718 | 92.0266 | 350.8742 | 0 | 3.2751 | 0 | 20.0413 | 0 | 0 | 31.0266 | 0 | 0 | 269.3289 | 0 | 0 | 784.8021 | 0.008189% | CZ 8 | 3.6218 | 1.7209 | 0 | 0 | 0 | 0.95989 | 0 | 5.8738 | 0 | 0 | 9.0934 | 0 | 0 | 25.937 | 0 | 0 | 47.2067 | 0.008189% | CZ 8 | 0 | 0 | 0.92027 | 3.5087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.2373 | 0.008189% | CZ 8 | 37.9166 | 18.0162 | 100.585 | 383.5055 | 0 | 10.0491 | 0 | 61.4924 | 0 | 0 | 95.1987 | 0 | 0 | 469.1836 | 0 | 0 | 1175.9472 | 0.008189%
US Weighted | 0.37798 | 0.18137 | 0.65797 | 0.67401 | 0 | 1.1271 | 0 | 0.68035 | 0 | 0 | 1.013 | 0 | 0 | 4.5293 | 0 | 0 | 9.241 | 100% | US Weighted | 12.1325 | 5.8216 | 67.1395 | 68.7766 | 0 | 36.1769 | 0 | 21.8378 | 0 | 0 | 32.5159 | 0 | 0 | 269.3289 | 0 | 0 | 513.7297 | 100% | US Weighted | 3.5558 | 1.7062 | 0 | 0 | 0 | 10.6028 | 0 | 6.4003 | 0 | 0 | 9.5299 | 0 | 0 | 25.937 | 0 | 0 | 57.732 | 100% | US Weighted | 0 | 0 | 0.6714 | 0.68777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1675 | 100% | US Weighted | 37.2259 | 17.8624 | 73.3835 | 75.1728 | 0 | 111.0012 | 0 | 67.0048 | 0 | 0 | 99.7682 | 0 | 0 | 469.1836 | 0 | 0 | 950.6023 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.40389 | 0.18152 | 0.46261 | 0 | 0 | 4.6367 | 0 | 1.2403 | 0 | 0 | 1.3392 | 0 | 0 | 4.5293 | 0 | 0 | 12.7935 | 0% | CZ 0A | 12.9641 | 5.8263 | 47.2052 | 0 | 0 | 148.8293 | 0 | 39.8096 | 0 | 0 | 42.9862 | 0 | 0 | 269.3289 | 0 | 0 | 566.9496 | 0% | CZ 0A | 3.7996 | 1.7076 | 0 | 0 | 0 | 43.6194 | 0 | 11.6675 | 0 | 0 | 12.5985 | 0 | 0 | 25.937 | 0 | 0 | 99.3296 | 0% | CZ 0A | 0 | 0 | 0.47205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2804 | 0% | CZ 0A | 39.7776 | 17.8767 | 51.5952 | 0 | 0 | 456.6514 | 0 | 122.1474 | 0 | 0 | 131.8941 | 0 | 0 | 469.1836 | 0 | 0 | 1289.1259 | 0%
CZ 0B | 0.4033 | 0.1814 | 0.46027 | 0.00040854 | 0 | 3.9818 | 0 | 1.2203 | 0 | 0 | 1.3345 | 0 | 0 | 4.5293 | 0 | 0 | 12.1112 | 0% | CZ 0B | 12.9451 | 5.8225 | 46.9664 | 0.041687 | 0 | 127.8063 | 0 | 39.169 | 0 | 0 | 42.8346 | 0 | 0 | 269.3289 | 0 | 0 | 544.9144 | 0% | CZ 0B | 3.794 | 1.7065 | 0 | 0 | 0 | 37.4579 | 0 | 11.4798 | 0 | 0 | 12.5541 | 0 | 0 | 25.937 | 0 | 0 | 92.9292 | 0% | CZ 0B | 0 | 0 | 0.46966 | 0.00041687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2784 | 0% | CZ 0B | 39.7194 | 17.865 | 51.3343 | 0.045564 | 0 | 392.1465 | 0 | 120.1818 | 0 | 0 | 131.4289 | 0 | 0 | 469.1836 | 0 | 0 | 1221.9051 | 0%
CZ 1A | 0.40401 | 0.18152 | 0.50462 | 0 | 0 | 2.8092 | 0 | 1.1837 | 0 | 0 | 1.3199 | 0 | 0 | 4.5293 | 0 | 0 | 10.9321 | 2.382% | CZ 1A | 12.9679 | 5.8263 | 51.4914 | 0 | 0 | 90.1687 | 0 | 37.9939 | 0 | 0 | 42.3645 | 0 | 0 | 269.3289 | 0 | 0 | 510.1415 | 2.382% | CZ 1A | 3.8007 | 1.7076 | 0 | 0 | 0 | 26.4269 | 0 | 11.1354 | 0 | 0 | 12.4163 | 0 | 0 | 25.937 | 0 | 0 | 81.4239 | 2.382% | CZ 1A | 0 | 0 | 0.51491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3232 | 2.382% | CZ 1A | 39.7892 | 17.8767 | 56.2801 | 0 | 0 | 276.6636 | 0 | 116.5762 | 0 | 0 | 129.9866 | 0 | 0 | 469.1836 | 0 | 0 | 1106.356 | 2.382%
CZ 1B | 0.40425 | 0.18116 | 0.50525 | 0.034466 | 0 | 3.0384 | 0 | 1.1716 | 0 | 0 | 1.3234 | 0 | 0 | 4.5293 | 0 | 0 | 11.1878 | 0% | CZ 1B | 12.9755 | 5.8149 | 51.5558 | 3.5169 | 0 | 97.5264 | 0 | 37.6073 | 0 | 0 | 42.4783 | 0 | 0 | 269.3289 | 0 | 0 | 520.8038 | 0% | CZ 1B | 3.8029 | 1.7042 | 0 | 0 | 0 | 28.5834 | 0 | 11.0221 | 0 | 0 | 12.4497 | 0 | 0 | 25.937 | 0 | 0 | 83.4992 | 0% | CZ 1B | 0 | 0 | 0.51556 | 0.035169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.359 | 0% | CZ 1B | 39.8125 | 17.8418 | 56.3505 | 3.844 | 0 | 299.2391 | 0 | 115.3899 | 0 | 0 | 130.3356 | 0 | 0 | 469.1836 | 0 | 0 | 1131.9968 | 0%
CZ 2A | 0.40271 | 0.18116 | 0.55201 | 0.10897 | 0 | 2.3566 | 0 | 1.2191 | 0 | 0 | 1.3099 | 0 | 0 | 4.5293 | 0 | 0 | 10.6598 | 20.26% | CZ 2A | 12.9262 | 5.8149 | 56.3271 | 11.1191 | 0 | 75.6429 | 0 | 39.1311 | 0 | 0 | 42.0461 | 0 | 0 | 269.3289 | 0 | 0 | 512.3362 | 20.26% | CZ 2A | 3.7884 | 1.7042 | 0 | 0 | 0 | 22.1697 | 0 | 11.4687 | 0 | 0 | 12.323 | 0 | 0 | 25.937 | 0 | 0 | 77.391 | 20.26% | CZ 2A | 0 | 0 | 0.56327 | 0.11119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4828 | 20.26% | CZ 2A | 39.6613 | 17.8418 | 61.5655 | 12.1532 | 0 | 232.0941 | 0 | 120.0655 | 0 | 0 | 129.0096 | 0 | 0 | 469.1836 | 0 | 0 | 1081.5746 | 20.26%
CZ 2B | 0.40283 | 0.18128 | 0.55487 | 0.074836 | 0 | 1.617 | 0 | 1.052 | 0 | 0 | 1.2971 | 0 | 0 | 4.5293 | 0 | 0 | 9.7091 | 2.859% | CZ 2B | 12.93 | 5.8187 | 56.6189 | 7.6364 | 0 | 51.9019 | 0 | 33.7673 | 0 | 0 | 41.6329 | 0 | 0 | 269.3289 | 0 | 0 | 479.6349 | 2.859% | CZ 2B | 3.7896 | 1.7054 | 0 | 0 | 0 | 15.2116 | 0 | 9.8966 | 0 | 0 | 12.2019 | 0 | 0 | 25.937 | 0 | 0 | 68.742 | 2.859% | CZ 2B | 0 | 0 | 0.56619 | 0.076364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4509 | 2.859% | CZ 2B | 39.6729 | 17.8534 | 61.8845 | 8.3465 | 0 | 159.2499 | 0 | 103.6078 | 0 | 0 | 127.7419 | 0 | 0 | 469.1836 | 0 | 0 | 987.5405 | 2.859%
CZ 3A | 0.40307 | 0.18128 | 0.63308 | 0.4856 | 0 | 1.2775 | 0 | 0.97241 | 0 | 0 | 1.2877 | 0 | 0 | 4.5293 | 0 | 0 | 9.7699 | 19.57% | CZ 3A | 12.9376 | 5.8187 | 64.6001 | 49.551 | 0 | 41.0037 | 0 | 31.2124 | 0 | 0 | 41.3335 | 0 | 0 | 269.3289 | 0 | 0 | 515.7858 | 19.57% | CZ 3A | 3.7918 | 1.7054 | 0 | 0 | 0 | 12.0175 | 0 | 9.1478 | 0 | 0 | 12.1142 | 0 | 0 | 25.937 | 0 | 0 | 64.7136 | 19.57% | CZ 3A | 0 | 0 | 0.646 | 0.49551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.9498 | 19.57% | CZ 3A | 39.6962 | 17.8534 | 70.6079 | 54.1593 | 0 | 125.8112 | 0 | 95.7686 | 0 | 0 | 126.823 | 0 | 0 | 469.1836 | 0 | 0 | 999.9031 | 19.57%
CZ 3B | 0.40389 | 0.18128 | 0.61228 | 0.26235 | 0 | 1.1302 | 0 | 1.0128 | 0 | 0 | 1.2861 | 0 | 0 | 4.5293 | 0 | 0 | 9.4181 | 6.098% | CZ 3B | 12.9641 | 5.8187 | 62.4779 | 26.7708 | 0 | 36.2767 | 0 | 32.5088 | 0 | 0 | 41.2804 | 0 | 0 | 269.3289 | 0 | 0 | 487.4262 | 6.098% | CZ 3B | 3.7996 | 1.7054 | 0 | 0 | 0 | 10.6321 | 0 | 9.5278 | 0 | 0 | 12.0986 | 0 | 0 | 25.937 | 0 | 0 | 63.7004 | 6.098% | CZ 3B | 0 | 0 | 0.62478 | 0.26771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.7008 | 6.098% | CZ 3B | 39.7776 | 17.8534 | 68.2883 | 29.2605 | 0 | 111.3075 | 0 | 99.7464 | 0 | 0 | 126.6602 | 0 | 0 | 469.1836 | 0 | 0 | 962.0774 | 6.098%
CZ 3C | 0.40543 | 0.18163 | 0.64225 | 0.13003 | 0 | 0.3341 | 0 | 1.1296 | 0 | 0 | 1.2887 | 0 | 0 | 4.5293 | 0 | 0 | 8.641 | 0.5719% | CZ 3C | 13.0134 | 5.8301 | 65.5362 | 13.2679 | 0 | 10.7238 | 0 | 36.2578 | 0 | 0 | 41.3638 | 0 | 0 | 269.3289 | 0 | 0 | 455.3218 | 0.5719% | CZ 3C | 3.814 | 1.7087 | 0 | 0 | 0 | 3.143 | 0 | 10.6265 | 0 | 0 | 12.123 | 0 | 0 | 25.937 | 0 | 0 | 57.3522 | 0.5719% | CZ 3C | 0 | 0 | 0.65536 | 0.13268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.5964 | 0.5719% | CZ 3C | 39.9288 | 17.8883 | 71.6311 | 14.5018 | 0 | 32.9037 | 0 | 111.2493 | 0 | 0 | 126.9161 | 0 | 0 | 469.1836 | 0 | 0 | 884.2027 | 0.5719%
CZ 4A | 0.4046 | 0.18163 | 0.69774 | 1.0504 | 0 | 0.72701 | 0 | 1.106 | 0 | 0 | 1.2639 | 0 | 0 | 4.5293 | 0 | 0 | 9.9605 | 16.6% | CZ 4A | 12.9868 | 5.8301 | 71.1981 | 107.1818 | 0 | 23.3354 | 0 | 35.4996 | 0 | 0 | 40.5678 | 0 | 0 | 269.3289 | 0 | 0 | 565.9284 | 16.6% | CZ 4A | 3.8062 | 1.7087 | 0 | 0 | 0 | 6.8392 | 0 | 10.4043 | 0 | 0 | 11.8897 | 0 | 0 | 25.937 | 0 | 0 | 60.5852 | 16.6% | CZ 4A | 0 | 0 | 0.71198 | 1.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5921 | 16.6% | CZ 4A | 39.8474 | 17.8883 | 77.8195 | 117.1497 | 0 | 71.5997 | 0 | 108.9231 | 0 | 0 | 124.4736 | 0 | 0 | 469.1836 | 0 | 0 | 1026.8848 | 16.6%
CZ 4B | 0.40295 | 0.18116 | 0.67925 | 0.52471 | 0 | 0.62202 | 0 | 1.2412 | 0 | 0 | 1.2655 | 0 | 0 | 4.5293 | 0 | 0 | 9.4461 | 0.604% | CZ 4B | 12.9338 | 5.8149 | 69.3108 | 53.5416 | 0 | 19.9655 | 0 | 39.84 | 0 | 0 | 40.6208 | 0 | 0 | 269.3289 | 0 | 0 | 511.3562 | 0.604% | CZ 4B | 3.7907 | 1.7042 | 0 | 0 | 0 | 5.8515 | 0 | 11.6764 | 0 | 0 | 11.9053 | 0 | 0 | 25.937 | 0 | 0 | 60.8652 | 0.604% | CZ 4B | 0 | 0 | 0.69311 | 0.53542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.0368 | 0.604% | CZ 4B | 39.6845 | 17.8418 | 75.7567 | 58.521 | 0 | 61.2598 | 0 | 122.2405 | 0 | 0 | 124.6364 | 0 | 0 | 469.1836 | 0 | 0 | 969.1243 | 0.604%
CZ 4C | 0.40484 | 0.18163 | 0.71746 | 0.66406 | 0 | 0.14502 | 0 | 1.346 | 0 | 0 | 1.2549 | 0 | 0 | 4.5293 | 0 | 0 | 9.2431 | 1.378% | CZ 4C | 12.9944 | 5.8301 | 73.2104 | 67.7608 | 0 | 4.6549 | 0 | 43.2023 | 0 | 0 | 40.2797 | 0 | 0 | 269.3289 | 0 | 0 | 517.2614 | 1.378% | CZ 4C | 3.8084 | 1.7087 | 0 | 0 | 0 | 1.3643 | 0 | 12.6619 | 0 | 0 | 11.8053 | 0 | 0 | 25.937 | 0 | 0 | 57.2856 | 1.378% | CZ 4C | 0 | 0 | 0.7321 | 0.67761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.218 | 1.378% | CZ 4C | 39.8706 | 17.8883 | 80.019 | 74.0625 | 0 | 14.2827 | 0 | 132.5571 | 0 | 0 | 123.5897 | 0 | 0 | 469.1836 | 0 | 0 | 951.4535 | 1.378%
CZ 5A | 0.40342 | 0.1814 | 0.75163 | 1.6018 | 0 | 0.36846 | 0 | 1.0891 | 0 | 0 | 1.2532 | 0 | 0 | 4.5293 | 0 | 0 | 10.1783 | 20.38% | CZ 5A | 12.9489 | 5.8225 | 76.697 | 163.4444 | 0 | 11.8269 | 0 | 34.9576 | 0 | 0 | 40.2266 | 0 | 0 | 269.3289 | 0 | 0 | 615.2528 | 20.38% | CZ 5A | 3.7951 | 1.7065 | 0 | 0 | 0 | 3.4663 | 0 | 10.2455 | 0 | 0 | 11.7897 | 0 | 0 | 25.937 | 0 | 0 | 56.9401 | 20.38% | CZ 5A | 0 | 0 | 0.76697 | 1.6344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2097 | 20.38% | CZ 5A | 39.7311 | 17.865 | 83.8298 | 178.6448 | 0 | 36.2883 | 0 | 107.2599 | 0 | 0 | 123.4268 | 0 | 0 | 469.1836 | 0 | 0 | 1056.2293 | 20.38%
CZ 5B | 0.40378 | 0.18152 | 0.73603 | 1.0116 | 0 | 0.41381 | 0 | 1.2197 | 0 | 0 | 1.2557 | 0 | 0 | 4.5293 | 0 | 0 | 9.7514 | 5.254% | CZ 5B | 12.9603 | 5.8263 | 75.1053 | 103.2215 | 0 | 13.2825 | 0 | 39.1501 | 0 | 0 | 40.3062 | 0 | 0 | 269.3289 | 0 | 0 | 559.181 | 5.254% | CZ 5B | 3.7984 | 1.7076 | 0 | 0 | 0 | 3.8929 | 0 | 11.4742 | 0 | 0 | 11.8131 | 0 | 0 | 25.937 | 0 | 0 | 58.6232 | 5.254% | CZ 5B | 0 | 0 | 0.75105 | 1.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5916 | 5.254% | CZ 5B | 39.766 | 17.8767 | 82.0901 | 112.8211 | 0 | 40.7546 | 0 | 120.1237 | 0 | 0 | 123.6711 | 0 | 0 | 469.1836 | 0 | 0 | 1006.2867 | 5.254%
CZ 5C | 0.40484 | 0.18152 | 0.74844 | 0.88726 | 0 | 0.04098 | 0 | 1.2677 | 0 | 0 | 1.2455 | 0 | 0 | 4.5293 | 0 | 0 | 9.3054 | 0.02535% | CZ 5C | 12.9944 | 5.8263 | 76.3711 | 90.5372 | 0 | 1.3154 | 0 | 40.6891 | 0 | 0 | 39.9764 | 0 | 0 | 269.3289 | 0 | 0 | 537.0387 | 0.02535% | CZ 5C | 3.8084 | 1.7076 | 0 | 0 | 0 | 0.38551 | 0 | 11.9253 | 0 | 0 | 11.7164 | 0 | 0 | 25.937 | 0 | 0 | 55.4802 | 0.02535% | CZ 5C | 0 | 0 | 0.76371 | 0.90537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.4774 | 0.02535% | CZ 5C | 39.8706 | 17.8767 | 83.4736 | 98.9571 | 0 | 4.0359 | 0 | 124.8458 | 0 | 0 | 122.6592 | 0 | 0 | 469.1836 | 0 | 0 | 960.9025 | 0.02535%
CZ 6A | 0.40378 | 0.18152 | 0.79118 | 2.2049 | 0 | 0.42515 | 0 | 1.1272 | 0 | 0 | 1.251 | 0 | 0 | 4.5293 | 0 | 0 | 10.9141 | 3.192% | CZ 6A | 12.9603 | 5.8263 | 80.7331 | 224.9938 | 0 | 13.6464 | 0 | 36.182 | 0 | 0 | 40.1546 | 0 | 0 | 269.3289 | 0 | 0 | 683.8253 | 3.192% | CZ 6A | 3.7984 | 1.7076 | 0 | 0 | 0 | 3.9995 | 0 | 10.6043 | 0 | 0 | 11.7686 | 0 | 0 | 25.937 | 0 | 0 | 57.8155 | 3.192% | CZ 6A | 0 | 0 | 0.80733 | 2.2499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.8656 | 3.192% | CZ 6A | 39.766 | 17.8767 | 88.2413 | 245.9182 | 0 | 41.8711 | 0 | 111.0167 | 0 | 0 | 123.2058 | 0 | 0 | 469.1836 | 0 | 0 | 1137.0794 | 3.192%
CZ 6B | 0.40307 | 0.18128 | 0.78119 | 1.5849 | 0 | 0.26064 | 0 | 1.1907 | 0 | 0 | 1.2456 | 0 | 0 | 4.5293 | 0 | 0 | 10.1765 | 0.5438% | CZ 6B | 12.9376 | 5.8187 | 79.7137 | 161.7201 | 0 | 8.366 | 0 | 38.2176 | 0 | 0 | 39.9802 | 0 | 0 | 269.3289 | 0 | 0 | 616.0826 | 0.5438% | CZ 6B | 3.7918 | 1.7054 | 0 | 0 | 0 | 2.4519 | 0 | 11.2009 | 0 | 0 | 11.7175 | 0 | 0 | 25.937 | 0 | 0 | 56.8045 | 0.5438% | CZ 6B | 0 | 0 | 0.79714 | 1.6172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.2227 | 0.5438% | CZ 6B | 39.6962 | 17.8534 | 87.127 | 176.7601 | 0 | 25.6693 | 0 | 117.2625 | 0 | 0 | 122.6708 | 0 | 0 | 469.1836 | 0 | 0 | 1056.2229 | 0.5438%
CZ 7 | 0.40318 | 0.18163 | 0.8385 | 2.8321 | 0 | 0.27977 | 0 | 1.1174 | 0 | 0 | 1.244 | 0 | 0 | 4.5293 | 0 | 0 | 11.4259 | 0.271% | CZ 7 | 12.9414 | 5.8301 | 85.5612 | 288.9914 | 0 | 8.9801 | 0 | 35.8673 | 0 | 0 | 39.9309 | 0 | 0 | 269.3289 | 0 | 0 | 747.4312 | 0.271% | CZ 7 | 3.7929 | 1.7087 | 0 | 0 | 0 | 2.6319 | 0 | 10.5121 | 0 | 0 | 11.7031 | 0 | 0 | 25.937 | 0 | 0 | 56.2857 | 0.271% | CZ 7 | 0 | 0 | 0.85561 | 2.8899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.5538 | 0.271% | CZ 7 | 39.7078 | 17.8883 | 93.5184 | 315.8676 | 0 | 27.5535 | 0 | 110.0513 | 0 | 0 | 122.5196 | 0 | 0 | 469.1836 | 0 | 0 | 1196.2901 | 0.271%
CZ 8 | 0.40909 | 0.18293 | 0.90234 | 3.9842 | 0 | 0.072866 | 0 | 1.3199 | 0 | 0 | 1.2321 | 0 | 0 | 4.5293 | 0 | 0 | 12.6326 | 0.008189% | CZ 8 | 13.1309 | 5.8718 | 92.0758 | 406.5495 | 0 | 2.3388 | 0 | 42.3645 | 0 | 0 | 39.5481 | 0 | 0 | 269.3289 | 0 | 0 | 871.2083 | 0.008189% | CZ 8 | 3.8484 | 1.7209 | 0 | 0 | 0 | 0.68548 | 0 | 12.4163 | 0 | 0 | 11.5909 | 0 | 0 | 25.937 | 0 | 0 | 56.199 | 0.008189% | CZ 8 | 0 | 0 | 0.92076 | 4.0655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.7946 | 0.008189% | CZ 8 | 40.2893 | 18.0162 | 100.6389 | 444.3586 | 0 | 7.1762 | 0 | 129.9866 | 0 | 0 | 121.3449 | 0 | 0 | 469.1836 | 0 | 0 | 1330.9944 | 0.008189%
US Weighted | 0.40349 | 0.18137 | 0.65835 | 0.78952 | 0 | 1.1505 | 0 | 1.1054 | 0 | 0 | 1.2784 | 0 | 0 | 4.5293 | 0 | 0 | 10.0962 | 100% | US Weighted | 12.951 | 5.8216 | 67.1786 | 80.5632 | 0 | 36.9277 | 0 | 35.4812 | 0 | 0 | 41.0331 | 0 | 0 | 269.3289 | 0 | 0 | 549.2854 | 100% | US Weighted | 3.7957 | 1.7062 | 0 | 0 | 0 | 10.8229 | 0 | 10.399 | 0 | 0 | 12.0261 | 0 | 0 | 25.937 | 0 | 0 | 64.6869 | 100% | US Weighted | 0 | 0 | 0.67179 | 0.80563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2857 | 100% | US Weighted | 39.7375 | 17.8624 | 73.4262 | 88.0556 | 0 | 113.3048 | 0 | 108.8666 | 0 | 0 | 125.9015 | 0 | 0 | 469.1836 | 0 | 0 | 1036.3382 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.88668 | 0.32382 | 0.46265 | 0 | 0 | 5.84 | 0 | 1.8067 | 0 | 0 | 1.3391 | 0 | 0 | 4.5327 | 0 | 0 | 15.1916 | 0% | CZ 0A | 28.4604 | 10.394 | 47.2089 | 0 | 0 | 187.4525 | 0 | 57.9897 | 0 | 0 | 42.9824 | 0 | 0 | 269.4388 | 0 | 0 | 643.9267 | 0% | CZ 0A | 8.3413 | 3.0463 | 0 | 0 | 0 | 54.9392 | 0 | 16.9958 | 0 | 0 | 12.5974 | 0 | 0 | 25.9692 | 0 | 0 | 121.8892 | 0% | CZ 0A | 0 | 0 | 0.47209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2804 | 0% | CZ 0A | 87.3246 | 31.8919 | 51.5994 | 0 | 0 | 575.1583 | 0 | 177.9291 | 0 | 0 | 131.8825 | 0 | 0 | 469.5209 | 0 | 0 | 1525.3066 | 0%
CZ 0B | 0.88668 | 0.32394 | 0.46035 | 0 | 0 | 4.9978 | 0 | 2.068 | 0 | 0 | 1.3338 | 0 | 0 | 4.5327 | 0 | 0 | 14.6032 | 0% | CZ 0B | 28.4604 | 10.3978 | 46.974 | 0 | 0 | 160.4174 | 0 | 66.3784 | 0 | 0 | 42.8118 | 0 | 0 | 269.4388 | 0 | 0 | 624.8787 | 0% | CZ 0B | 8.3413 | 3.0474 | 0 | 0 | 0 | 47.0157 | 0 | 19.4544 | 0 | 0 | 12.5474 | 0 | 0 | 25.9692 | 0 | 0 | 116.3754 | 0% | CZ 0B | 0 | 0 | 0.46974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2781 | 0% | CZ 0B | 87.3246 | 31.9035 | 51.3426 | 0 | 0 | 492.2069 | 0 | 203.6682 | 0 | 0 | 131.3591 | 0 | 0 | 469.5209 | 0 | 0 | 1467.3258 | 0%
CZ 1A | 0.88668 | 0.32394 | 0.50465 | 0 | 0 | 3.7951 | 0 | 1.6523 | 0 | 0 | 1.3188 | 0 | 0 | 4.5327 | 0 | 0 | 13.0141 | 2.382% | CZ 1A | 28.4604 | 10.3978 | 51.4952 | 0 | 0 | 121.8132 | 0 | 53.0353 | 0 | 0 | 42.3304 | 0 | 0 | 269.4388 | 0 | 0 | 576.9711 | 2.382% | CZ 1A | 8.3413 | 3.0474 | 0 | 0 | 0 | 35.7014 | 0 | 15.5438 | 0 | 0 | 12.4063 | 0 | 0 | 25.9692 | 0 | 0 | 101.0094 | 2.382% | CZ 1A | 0 | 0 | 0.51495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3233 | 2.382% | CZ 1A | 87.3246 | 31.9035 | 56.2842 | 0 | 0 | 373.7581 | 0 | 162.7276 | 0 | 0 | 129.882 | 0 | 0 | 469.5209 | 0 | 0 | 1311.4008 | 2.382%
CZ 1B | 0.88668 | 0.32359 | 0.50543 | 0.015004 | 0 | 4.0021 | 0 | 2.019 | 0 | 0 | 1.3213 | 0 | 0 | 4.5327 | 0 | 0 | 13.6057 | 0% | CZ 1B | 28.4604 | 10.3864 | 51.5747 | 1.5311 | 0 | 128.4583 | 0 | 64.8053 | 0 | 0 | 42.41 | 0 | 0 | 269.4388 | 0 | 0 | 597.065 | 0% | CZ 1B | 8.3413 | 3.0441 | 0 | 0 | 0 | 37.649 | 0 | 18.9934 | 0 | 0 | 12.4297 | 0 | 0 | 25.9692 | 0 | 0 | 106.4265 | 0% | CZ 1B | 0 | 0 | 0.51575 | 0.015311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3394 | 0% | CZ 1B | 87.3246 | 31.8686 | 56.3712 | 1.6734 | 0 | 394.147 | 0 | 198.8414 | 0 | 0 | 130.1262 | 0 | 0 | 469.5209 | 0 | 0 | 1369.8734 | 0%
CZ 2A | 0.88668 | 0.32347 | 0.55197 | 0.072311 | 0 | 3.2093 | 0 | 1.7091 | 0 | 0 | 1.3093 | 0 | 0 | 4.5327 | 0 | 0 | 12.5949 | 20.26% | CZ 2A | 28.4604 | 10.3826 | 56.3233 | 7.3786 | 0 | 103.0115 | 0 | 54.8586 | 0 | 0 | 42.0272 | 0 | 0 | 269.4388 | 0 | 0 | 571.881 | 20.26% | CZ 2A | 8.3413 | 3.043 | 0 | 0 | 0 | 30.1909 | 0 | 16.0781 | 0 | 0 | 12.3175 | 0 | 0 | 25.9692 | 0 | 0 | 95.94 | 20.26% | CZ 2A | 0 | 0 | 0.56323 | 0.073786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4453 | 20.26% | CZ 2A | 87.3246 | 31.857 | 61.5614 | 8.0649 | 0 | 316.069 | 0 | 168.322 | 0 | 0 | 128.9515 | 0 | 0 | 469.5209 | 0 | 0 | 1271.6711 | 20.26%
CZ 2B | 0.88668 | 0.32371 | 0.55498 | 0.038068 | 0 | 2.2826 | 0 | 1.9752 | 0 | 0 | 1.2956 | 0 | 0 | 4.5327 | 0 | 0 | 11.8895 | 2.859% | CZ 2B | 28.4604 | 10.3902 | 56.6303 | 3.8845 | 0 | 73.2661 | 0 | 63.399 | 0 | 0 | 41.5875 | 0 | 0 | 269.4388 | 0 | 0 | 547.0567 | 2.859% | CZ 2B | 8.3413 | 3.0452 | 0 | 0 | 0 | 21.4731 | 0 | 18.5812 | 0 | 0 | 12.1886 | 0 | 0 | 25.9692 | 0 | 0 | 89.5985 | 2.859% | CZ 2B | 0 | 0 | 0.5663 | 0.038845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4135 | 2.859% | CZ 2B | 87.3246 | 31.8802 | 61.8969 | 4.2458 | 0 | 224.8015 | 0 | 194.5264 | 0 | 0 | 127.6023 | 0 | 0 | 469.5209 | 0 | 0 | 1201.7985 | 2.859%
CZ 3A | 0.88668 | 0.32359 | 0.63342 | 0.47245 | 0 | 1.7811 | 0 | 1.704 | 0 | 0 | 1.2831 | 0 | 0 | 4.5327 | 0 | 0 | 11.6171 | 19.57% | CZ 3A | 28.4604 | 10.3864 | 64.6342 | 48.2094 | 0 | 57.1709 | 0 | 54.6956 | 0 | 0 | 41.1856 | 0 | 0 | 269.4388 | 0 | 0 | 574.1814 | 19.57% | CZ 3A | 8.3413 | 3.0441 | 0 | 0 | 0 | 16.7558 | 0 | 16.0304 | 0 | 0 | 12.0708 | 0 | 0 | 25.9692 | 0 | 0 | 82.2116 | 19.57% | CZ 3A | 0 | 0 | 0.64634 | 0.48209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.9368 | 19.57% | CZ 3A | 87.3246 | 31.8686 | 70.6452 | 52.6929 | 0 | 175.4168 | 0 | 167.8219 | 0 | 0 | 126.3694 | 0 | 0 | 469.5209 | 0 | 0 | 1181.6603 | 19.57%
CZ 3B | 0.88668 | 0.32359 | 0.61243 | 0.18633 | 0 | 1.4898 | 0 | 1.9243 | 0 | 0 | 1.2844 | 0 | 0 | 4.5327 | 0 | 0 | 11.2402 | 6.098% | CZ 3B | 28.4604 | 10.3864 | 62.493 | 19.0132 | 0 | 47.8193 | 0 | 61.7652 | 0 | 0 | 41.2273 | 0 | 0 | 269.4388 | 0 | 0 | 540.6037 | 6.098% | CZ 3B | 8.3413 | 3.0441 | 0 | 0 | 0 | 14.015 | 0 | 18.1023 | 0 | 0 | 12.083 | 0 | 0 | 25.9692 | 0 | 0 | 81.555 | 6.098% | CZ 3B | 0 | 0 | 0.62493 | 0.19013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.6234 | 6.098% | CZ 3B | 87.3246 | 31.8686 | 68.3049 | 20.7814 | 0 | 146.7235 | 0 | 189.5135 | 0 | 0 | 126.4974 | 0 | 0 | 469.5209 | 0 | 0 | 1140.5346 | 6.098%
CZ 3C | 0.88668 | 0.32359 | 0.64218 | 0.059572 | 0 | 0.46105 | 0 | 1.5819 | 0 | 0 | 1.29 | 0 | 0 | 4.5327 | 0 | 0 | 9.7776 | 0.5719% | CZ 3C | 28.4604 | 10.3864 | 65.5286 | 6.0788 | 0 | 14.7988 | 0 | 50.776 | 0 | 0 | 41.4055 | 0 | 0 | 269.4388 | 0 | 0 | 486.8733 | 0.5719% | CZ 3C | 8.3413 | 3.0441 | 0 | 0 | 0 | 4.3373 | 0 | 14.8816 | 0 | 0 | 12.1353 | 0 | 0 | 25.9692 | 0 | 0 | 68.7087 | 0.5719% | CZ 3C | 0 | 0 | 0.65529 | 0.060788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.5244 | 0.5719% | CZ 3C | 87.3246 | 31.8686 | 71.6228 | 6.6441 | 0 | 45.4069 | 0 | 155.7956 | 0 | 0 | 127.044 | 0 | 0 | 469.5209 | 0 | 0 | 995.2274 | 0.5719%
CZ 4A | 0.88668 | 0.32311 | 0.6977 | 1.1004 | 0 | 1.1053 | 0 | 1.5803 | 0 | 0 | 1.2638 | 0 | 0 | 4.5327 | 0 | 0 | 11.4898 | 16.6% | CZ 4A | 28.4604 | 10.3713 | 71.1943 | 112.2828 | 0 | 35.4769 | 0 | 50.723 | 0 | 0 | 40.564 | 0 | 0 | 269.4388 | 0 | 0 | 618.5113 | 16.6% | CZ 4A | 8.3413 | 3.0396 | 0 | 0 | 0 | 10.3977 | 0 | 14.8661 | 0 | 0 | 11.8886 | 0 | 0 | 25.9692 | 0 | 0 | 74.5025 | 16.6% | CZ 4A | 0 | 0 | 0.71194 | 1.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.6431 | 16.6% | CZ 4A | 87.3246 | 31.8221 | 77.8154 | 122.7251 | 0 | 108.8533 | 0 | 155.6327 | 0 | 0 | 124.462 | 0 | 0 | 469.5209 | 0 | 0 | 1178.156 | 16.6%
CZ 4B | 0.88668 | 0.32335 | 0.67925 | 0.50417 | 0 | 0.87935 | 0 | 1.876 | 0 | 0 | 1.2662 | 0 | 0 | 4.5327 | 0 | 0 | 10.9477 | 0.604% | CZ 4B | 28.4604 | 10.3789 | 69.3108 | 51.4459 | 0 | 28.2253 | 0 | 60.2148 | 0 | 0 | 40.6436 | 0 | 0 | 269.4388 | 0 | 0 | 558.1184 | 0.604% | CZ 4B | 8.3413 | 3.0419 | 0 | 0 | 0 | 8.2724 | 0 | 17.648 | 0 | 0 | 11.912 | 0 | 0 | 25.9692 | 0 | 0 | 75.1846 | 0.604% | CZ 4B | 0 | 0 | 0.69311 | 0.51446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.0159 | 0.604% | CZ 4B | 87.3246 | 31.8453 | 75.7567 | 56.2304 | 0 | 86.6035 | 0 | 184.7564 | 0 | 0 | 124.7062 | 0 | 0 | 469.5209 | 0 | 0 | 1116.744 | 0.604%
CZ 4C | 0.88668 | 0.32276 | 0.71739 | 0.72994 | 0 | 0.19557 | 0 | 1.4933 | 0 | 0 | 1.2557 | 0 | 0 | 4.5327 | 0 | 0 | 10.1341 | 1.378% | CZ 4C | 28.4604 | 10.3599 | 73.2029 | 74.4838 | 0 | 6.2774 | 0 | 47.933 | 0 | 0 | 40.3062 | 0 | 0 | 269.4388 | 0 | 0 | 550.4623 | 1.378% | CZ 4C | 8.3413 | 3.0363 | 0 | 0 | 0 | 1.8398 | 0 | 14.0484 | 0 | 0 | 11.8131 | 0 | 0 | 25.9692 | 0 | 0 | 65.048 | 1.378% | CZ 4C | 0 | 0 | 0.73203 | 0.74484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2852 | 1.378% | CZ 4C | 87.3246 | 31.7872 | 80.0107 | 81.4108 | 0 | 19.2607 | 0 | 147.0724 | 0 | 0 | 123.6711 | 0 | 0 | 469.5209 | 0 | 0 | 1040.0584 | 1.378%
CZ 5A | 0.88668 | 0.32323 | 0.75163 | 1.4692 | 0 | 0.60702 | 0 | 1.4411 | 0 | 0 | 1.2532 | 0 | 0 | 4.5327 | 0 | 0 | 11.2648 | 20.38% | CZ 5A | 28.4604 | 10.3751 | 76.697 | 149.915 | 0 | 19.4841 | 0 | 46.2576 | 0 | 0 | 40.2266 | 0 | 0 | 269.4388 | 0 | 0 | 640.8545 | 20.38% | CZ 5A | 8.3413 | 3.0408 | 0 | 0 | 0 | 5.7104 | 0 | 13.5573 | 0 | 0 | 11.7897 | 0 | 0 | 25.9692 | 0 | 0 | 68.4087 | 20.38% | CZ 5A | 0 | 0 | 0.76697 | 1.4992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.0744 | 20.38% | CZ 5A | 87.3246 | 31.8337 | 83.8298 | 163.8571 | 0 | 59.7827 | 0 | 141.9315 | 0 | 0 | 123.4268 | 0 | 0 | 469.5209 | 0 | 0 | 1161.5072 | 20.38%
CZ 5B | 0.88668 | 0.32323 | 0.73603 | 0.87003 | 0 | 0.70067 | 0 | 1.6837 | 0 | 0 | 1.2563 | 0 | 0 | 4.5327 | 0 | 0 | 10.9894 | 5.254% | CZ 5B | 28.4604 | 10.3751 | 75.1053 | 88.7787 | 0 | 22.4901 | 0 | 54.0436 | 0 | 0 | 40.3252 | 0 | 0 | 269.4388 | 0 | 0 | 589.0171 | 5.254% | CZ 5B | 8.3413 | 3.0408 | 0 | 0 | 0 | 6.5915 | 0 | 15.8393 | 0 | 0 | 11.8186 | 0 | 0 | 25.9692 | 0 | 0 | 71.6006 | 5.254% | CZ 5B | 0 | 0 | 0.75105 | 0.88779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.4472 | 5.254% | CZ 5B | 87.3246 | 31.8337 | 82.0901 | 97.0352 | 0 | 69.006 | 0 | 165.8214 | 0 | 0 | 123.7292 | 0 | 0 | 469.5209 | 0 | 0 | 1126.361 | 5.254%
CZ 5C | 0.88668 | 0.32276 | 0.74836 | 0.76857 | 0 | 0.060938 | 0 | 1.3414 | 0 | 0 | 1.2465 | 0 | 0 | 4.5327 | 0 | 0 | 9.9079 | 0.02535% | CZ 5C | 28.4604 | 10.3599 | 76.3635 | 78.4251 | 0 | 1.956 | 0 | 43.0544 | 0 | 0 | 40.0105 | 0 | 0 | 269.4388 | 0 | 0 | 548.0687 | 0.02535% | CZ 5C | 8.3413 | 3.0363 | 0 | 0 | 0 | 0.57327 | 0 | 12.6185 | 0 | 0 | 11.7264 | 0 | 0 | 25.9692 | 0 | 0 | 62.265 | 0.02535% | CZ 5C | 0 | 0 | 0.76364 | 0.78425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.3562 | 0.02535% | CZ 5C | 87.3246 | 31.7872 | 83.4653 | 85.7187 | 0 | 6.0015 | 0 | 132.1035 | 0 | 0 | 122.7639 | 0 | 0 | 469.5209 | 0 | 0 | 1018.6855 | 0.02535%
CZ 6A | 0.88668 | 0.323 | 0.79118 | 2.0706 | 0 | 0.67871 | 0 | 1.4922 | 0 | 0 | 1.2507 | 0 | 0 | 4.5327 | 0 | 0 | 12.0256 | 3.192% | CZ 6A | 28.4604 | 10.3675 | 80.7331 | 211.2825 | 0 | 21.785 | 0 | 47.8951 | 0 | 0 | 40.1432 | 0 | 0 | 269.4388 | 0 | 0 | 710.1056 | 3.192% | CZ 6A | 8.3413 | 3.0385 | 0 | 0 | 0 | 6.3848 | 0 | 14.0373 | 0 | 0 | 11.7653 | 0 | 0 | 25.9692 | 0 | 0 | 69.5364 | 3.192% | CZ 6A | 0 | 0 | 0.80733 | 2.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.7285 | 3.192% | CZ 6A | 87.3246 | 31.8104 | 88.2413 | 230.9318 | 0 | 66.8426 | 0 | 146.9561 | 0 | 0 | 123.171 | 0 | 0 | 469.5209 | 0 | 0 | 1244.7986 | 3.192%
CZ 6B | 0.88668 | 0.32276 | 0.78119 | 1.4272 | 0 | 0.45704 | 0 | 1.6007 | 0 | 0 | 1.2459 | 0 | 0 | 4.5327 | 0 | 0 | 11.2541 | 0.5438% | CZ 6B | 28.4604 | 10.3599 | 79.7137 | 145.6288 | 0 | 14.6699 | 0 | 51.3788 | 0 | 0 | 39.9916 | 0 | 0 | 269.4388 | 0 | 0 | 639.6418 | 0.5438% | CZ 6B | 8.3413 | 3.0363 | 0 | 0 | 0 | 4.2995 | 0 | 15.0583 | 0 | 0 | 11.7209 | 0 | 0 | 25.9692 | 0 | 0 | 68.4254 | 0.5438% | CZ 6B | 0 | 0 | 0.79714 | 1.4563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.0617 | 0.5438% | CZ 6B | 87.3246 | 31.7872 | 87.127 | 159.1723 | 0 | 45.0115 | 0 | 157.6449 | 0 | 0 | 122.7057 | 0 | 0 | 469.5209 | 0 | 0 | 1160.294 | 0.5438%
CZ 7 | 0.88668 | 0.32264 | 0.83854 | 2.6805 | 0 | 0.48479 | 0 | 1.4661 | 0 | 0 | 1.2438 | 0 | 0 | 4.5327 | 0 | 0 | 12.4557 | 0.271% | CZ 7 | 28.4604 | 10.3561 | 85.565 | 273.5178 | 0 | 15.5607 | 0 | 47.0574 | 0 | 0 | 39.9234 | 0 | 0 | 269.4388 | 0 | 0 | 769.8796 | 0.271% | CZ 7 | 8.3413 | 3.0352 | 0 | 0 | 0 | 4.5606 | 0 | 13.7917 | 0 | 0 | 11.7009 | 0 | 0 | 25.9692 | 0 | 0 | 67.3989 | 0.271% | CZ 7 | 0 | 0 | 0.85565 | 2.7352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.3991 | 0.271% | CZ 7 | 87.3246 | 31.7755 | 93.5226 | 298.955 | 0 | 47.7447 | 0 | 144.3857 | 0 | 0 | 122.4964 | 0 | 0 | 469.5209 | 0 | 0 | 1295.7253 | 0.271%
CZ 8 | 0.88668 | 0.32087 | 0.90234 | 3.8994 | 0 | 0.16817 | 0 | 1.3945 | 0 | 0 | 1.2325 | 0 | 0 | 4.5327 | 0 | 0 | 13.3371 | 0.008189% | CZ 8 | 28.4604 | 10.2993 | 92.0758 | 397.8937 | 0 | 5.3979 | 0 | 44.7602 | 0 | 0 | 39.5594 | 0 | 0 | 269.4388 | 0 | 0 | 887.8855 | 0.008189% | CZ 8 | 8.3413 | 3.0185 | 0 | 0 | 0 | 1.582 | 0 | 13.1185 | 0 | 0 | 11.5942 | 0 | 0 | 25.9692 | 0 | 0 | 63.6237 | 0.008189% | CZ 8 | 0 | 0 | 0.92076 | 3.9789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.708 | 0.008189% | CZ 8 | 87.3246 | 31.6011 | 100.6389 | 434.8978 | 0 | 16.5624 | 0 | 137.3374 | 0 | 0 | 121.3798 | 0 | 0 | 469.5209 | 0 | 0 | 1399.2628 | 0.008189%
US Weighted | 0.88668 | 0.32337 | 0.65841 | 0.74246 | 0 | 1.6254 | 0 | 1.6392 | 0 | 0 | 1.2772 | 0 | 0 | 4.5327 | 0 | 0 | 11.6854 | 100% | US Weighted | 28.4604 | 10.3794 | 67.1851 | 75.7613 | 0 | 52.1728 | 0 | 52.6137 | 0 | 0 | 40.9958 | 0 | 0 | 269.4388 | 0 | 0 | 597.0073 | 100% | US Weighted | 8.3413 | 3.042 | 0 | 0 | 0 | 15.291 | 0 | 15.4202 | 0 | 0 | 12.0152 | 0 | 0 | 25.9692 | 0 | 0 | 80.0789 | 100% | US Weighted | 0 | 0 | 0.67185 | 0.75761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.2378 | 100% | US Weighted | 87.3246 | 31.8469 | 73.4333 | 82.8071 | 0 | 160.0813 | 0 | 161.4341 | 0 | 0 | 125.7869 | 0 | 0 | 469.5209 | 0 | 0 | 1192.2351 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 2501 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.88668 | 0.32382 | 0.46332 | 0 | 0 | 6.2275 | 0 | 1.8081 | 0 | 0 | 1.3291 | 0 | 0 | 4.5327 | 0 | 0 | 15.5711 | 0% | CZ 0A | 28.4604 | 10.394 | 47.2772 | 0 | 0 | 199.8897 | 0 | 58.0352 | 0 | 0 | 42.6602 | 0 | 0 | 269.4388 | 0 | 0 | 656.1554 | 0% | CZ 0A | 8.3413 | 3.0463 | 0 | 0 | 0 | 58.5843 | 0 | 17.0091 | 0 | 0 | 12.503 | 0 | 0 | 25.9692 | 0 | 0 | 125.4532 | 0% | CZ 0A | 0 | 0 | 0.47277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2811 | 0% | CZ 0A | 87.3246 | 31.8919 | 51.6739 | 0 | 0 | 613.3192 | 0 | 178.0687 | 0 | 0 | 130.8939 | 0 | 0 | 469.5209 | 0 | 0 | 1562.693 | 0%
CZ 0B | 0.88668 | 0.32394 | 0.46064 | 0.0012999 | 0 | 5.4318 | 0 | 2.0725 | 0 | 0 | 1.3293 | 0 | 0 | 4.5327 | 0 | 0 | 15.0388 | 0% | CZ 0B | 28.4604 | 10.3978 | 47.0043 | 0.13264 | 0 | 174.3481 | 0 | 66.5225 | 0 | 0 | 42.6678 | 0 | 0 | 269.4388 | 0 | 0 | 638.9723 | 0% | CZ 0B | 8.3413 | 3.0474 | 0 | 0 | 0 | 51.0985 | 0 | 19.4966 | 0 | 0 | 12.5052 | 0 | 0 | 25.9692 | 0 | 0 | 120.4583 | 0% | CZ 0B | 0 | 0 | 0.47004 | 0.0013264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.2797 | 0% | CZ 0B | 87.3246 | 31.9035 | 51.3757 | 0.14498 | 0 | 534.9504 | 0 | 204.1102 | 0 | 0 | 130.9171 | 0 | 0 | 469.5209 | 0 | 0 | 1510.2473 | 0%
CZ 1A | 0.88668 | 0.32394 | 0.50469 | 7.4279e-05 | 0 | 3.9499 | 0 | 1.6524 | 0 | 0 | 1.3177 | 0 | 0 | 4.5327 | 0 | 0 | 13.1681 | 2.382% | CZ 1A | 28.4604 | 10.3978 | 51.4989 | 0.0075795 | 0 | 126.7828 | 0 | 53.0391 | 0 | 0 | 42.2963 | 0 | 0 | 269.4388 | 0 | 0 | 581.9217 | 2.382% | CZ 1A | 8.3413 | 3.0474 | 0 | 0 | 0 | 37.1579 | 0 | 15.5449 | 0 | 0 | 12.3963 | 0 | 0 | 25.9692 | 0 | 0 | 102.457 | 2.382% | CZ 1A | 0 | 0 | 0.51499 | 7.5795e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3234 | 2.382% | CZ 1A | 87.3246 | 31.9035 | 56.2883 | 0.0082844 | 0 | 389.0062 | 0 | 162.7392 | 0 | 0 | 129.7773 | 0 | 0 | 469.5209 | 0 | 0 | 1326.5682 | 2.382%
CZ 1B | 0.88668 | 0.32359 | 0.50536 | 0.055487 | 0 | 4.3936 | 0 | 2.0242 | 0 | 0 | 1.3214 | 0 | 0 | 4.5327 | 0 | 0 | 14.0429 | 0% | CZ 1B | 28.4604 | 10.3864 | 51.5672 | 5.6619 | 0 | 141.0244 | 0 | 64.9721 | 0 | 0 | 42.4138 | 0 | 0 | 269.4388 | 0 | 0 | 613.9249 | 0% | CZ 1B | 8.3413 | 3.0441 | 0 | 0 | 0 | 41.3319 | 0 | 19.0422 | 0 | 0 | 12.4308 | 0 | 0 | 25.9692 | 0 | 0 | 110.1594 | 0% | CZ 1B | 0 | 0 | 0.51567 | 0.056619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.3806 | 0% | CZ 1B | 87.3246 | 31.8686 | 56.3629 | 6.1884 | 0 | 432.7034 | 0 | 199.3532 | 0 | 0 | 130.1378 | 0 | 0 | 469.5209 | 0 | 0 | 1413.4598 | 0%
CZ 2A | 0.88668 | 0.32347 | 0.55163 | 0.14072 | 0 | 3.416 | 0 | 1.7286 | 0 | 0 | 1.3129 | 0 | 0 | 4.5327 | 0 | 0 | 12.8926 | 20.26% | CZ 2A | 28.4604 | 10.3826 | 56.2892 | 14.3594 | 0 | 109.6452 | 0 | 55.4841 | 0 | 0 | 42.1409 | 0 | 0 | 269.4388 | 0 | 0 | 586.2005 | 20.26% | CZ 2A | 8.3413 | 3.043 | 0 | 0 | 0 | 32.1352 | 0 | 16.2614 | 0 | 0 | 12.3508 | 0 | 0 | 25.9692 | 0 | 0 | 98.1008 | 20.26% | CZ 2A | 0 | 0 | 0.56289 | 0.14359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.5148 | 20.26% | CZ 2A | 87.3246 | 31.857 | 61.5241 | 15.6948 | 0 | 336.423 | 0 | 170.2411 | 0 | 0 | 129.3004 | 0 | 0 | 469.5209 | 0 | 0 | 1301.8858 | 20.26%
CZ 2B | 0.88668 | 0.32371 | 0.55427 | 0.11487 | 0 | 2.4805 | 0 | 2.0035 | 0 | 0 | 1.305 | 0 | 0 | 4.5327 | 0 | 0 | 12.2012 | 2.859% | CZ 2B | 28.4604 | 10.3902 | 56.5583 | 11.7217 | 0 | 79.6193 | 0 | 64.3087 | 0 | 0 | 41.8869 | 0 | 0 | 269.4388 | 0 | 0 | 562.3843 | 2.859% | CZ 2B | 8.3413 | 3.0452 | 0 | 0 | 0 | 23.3351 | 0 | 18.8478 | 0 | 0 | 12.2764 | 0 | 0 | 25.9692 | 0 | 0 | 91.8149 | 2.859% | CZ 2B | 0 | 0 | 0.56558 | 0.11722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.4911 | 2.859% | CZ 2B | 87.3246 | 31.8802 | 61.8182 | 12.8118 | 0 | 244.2949 | 0 | 197.3178 | 0 | 0 | 128.5212 | 0 | 0 | 469.5209 | 0 | 0 | 1233.4895 | 2.859%
CZ 3A | 0.88668 | 0.32359 | 0.6326 | 0.58213 | 0 | 1.909 | 0 | 1.7101 | 0 | 0 | 1.2934 | 0 | 0 | 4.5327 | 0 | 0 | 11.8702 | 19.57% | CZ 3A | 28.4604 | 10.3864 | 64.5509 | 59.4006 | 0 | 61.2762 | 0 | 54.8889 | 0 | 0 | 41.5154 | 0 | 0 | 269.4388 | 0 | 0 | 589.9176 | 19.57% | CZ 3A | 8.3413 | 3.0441 | 0 | 0 | 0 | 17.959 | 0 | 16.087 | 0 | 0 | 12.1675 | 0 | 0 | 25.9692 | 0 | 0 | 83.5681 | 19.57% | CZ 3A | 0 | 0 | 0.64551 | 0.59401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.0478 | 19.57% | CZ 3A | 87.3246 | 31.8686 | 70.5541 | 64.9248 | 0 | 188.0131 | 0 | 168.415 | 0 | 0 | 127.3813 | 0 | 0 | 469.5209 | 0 | 0 | 1208.0024 | 19.57%
CZ 3B | 0.88668 | 0.32359 | 0.61139 | 0.30061 | 0 | 1.5578 | 0 | 1.9303 | 0 | 0 | 1.2981 | 0 | 0 | 4.5327 | 0 | 0 | 11.4412 | 6.098% | CZ 3B | 28.4604 | 10.3864 | 62.3869 | 30.6743 | 0 | 50.0027 | 0 | 61.9585 | 0 | 0 | 41.6671 | 0 | 0 | 269.4388 | 0 | 0 | 554.9751 | 6.098% | CZ 3B | 8.3413 | 3.0441 | 0 | 0 | 0 | 14.655 | 0 | 18.159 | 0 | 0 | 12.2119 | 0 | 0 | 25.9692 | 0 | 0 | 82.3804 | 6.098% | CZ 3B | 0 | 0 | 0.62387 | 0.30674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.7389 | 6.098% | CZ 3B | 87.3246 | 31.8686 | 68.1889 | 33.527 | 0 | 153.4229 | 0 | 190.1066 | 0 | 0 | 127.8466 | 0 | 0 | 469.5209 | 0 | 0 | 1161.8059 | 6.098%
CZ 3C | 0.88668 | 0.32359 | 0.64092 | 0.19209 | 0 | 0.52471 | 0 | 1.6286 | 0 | 0 | 1.3054 | 0 | 0 | 4.5327 | 0 | 0 | 10.0347 | 0.5719% | CZ 3C | 28.4604 | 10.3864 | 65.3998 | 19.6006 | 0 | 16.842 | 0 | 52.2734 | 0 | 0 | 41.9021 | 0 | 0 | 269.4388 | 0 | 0 | 504.3033 | 0.5719% | CZ 3C | 8.3413 | 3.0441 | 0 | 0 | 0 | 4.9361 | 0 | 15.3204 | 0 | 0 | 12.2808 | 0 | 0 | 25.9692 | 0 | 0 | 69.8919 | 0.5719% | CZ 3C | 0 | 0 | 0.654 | 0.19601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 2.6583 | 0.5719% | CZ 3C | 87.3246 | 31.8686 | 71.4819 | 21.4235 | 0 | 51.676 | 0 | 160.3897 | 0 | 0 | 128.5677 | 0 | 0 | 469.5209 | 0 | 0 | 1022.2528 | 0.5719%
CZ 4A | 0.88668 | 0.32311 | 0.69685 | 1.2572 | 0 | 1.1863 | 0 | 1.5862 | 0 | 0 | 1.2746 | 0 | 0 | 4.5327 | 0 | 0 | 11.7436 | 16.6% | CZ 4A | 28.4604 | 10.3713 | 71.1071 | 128.2831 | 0 | 38.0773 | 0 | 50.9125 | 0 | 0 | 40.9127 | 0 | 0 | 269.4388 | 0 | 0 | 637.5632 | 16.6% | CZ 4A | 8.3413 | 3.0396 | 0 | 0 | 0 | 11.1598 | 0 | 14.9216 | 0 | 0 | 11.9908 | 0 | 0 | 25.9692 | 0 | 0 | 75.4224 | 16.6% | CZ 4A | 0 | 0 | 0.71107 | 1.2828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.8022 | 16.6% | CZ 4A | 87.3246 | 31.8221 | 77.7201 | 140.2135 | 0 | 116.8321 | 0 | 156.2143 | 0 | 0 | 125.532 | 0 | 0 | 469.5209 | 0 | 0 | 1205.1795 | 16.6%
CZ 4B | 0.88668 | 0.32335 | 0.67809 | 0.63765 | 0 | 0.8966 | 0 | 1.8824 | 0 | 0 | 1.2814 | 0 | 0 | 4.5327 | 0 | 0 | 11.1188 | 0.604% | CZ 4B | 28.4604 | 10.3789 | 69.1933 | 65.0663 | 0 | 28.7788 | 0 | 60.4195 | 0 | 0 | 41.1288 | 0 | 0 | 269.4388 | 0 | 0 | 572.8646 | 0.604% | CZ 4B | 8.3413 | 3.0419 | 0 | 0 | 0 | 8.4346 | 0 | 17.7079 | 0 | 0 | 12.0542 | 0 | 0 | 25.9692 | 0 | 0 | 75.549 | 0.604% | CZ 4B | 0 | 0 | 0.69193 | 0.65066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.1509 | 0.604% | CZ 4B | 87.3246 | 31.8453 | 75.6283 | 71.1174 | 0 | 88.3016 | 0 | 185.3845 | 0 | 0 | 126.195 | 0 | 0 | 469.5209 | 0 | 0 | 1135.3176 | 0.604%
CZ 4C | 0.88668 | 0.32276 | 0.71572 | 1.0027 | 0 | 0.20986 | 0 | 1.5046 | 0 | 0 | 1.2764 | 0 | 0 | 4.5327 | 0 | 0 | 10.4514 | 1.378% | CZ 4C | 28.4604 | 10.3599 | 73.0323 | 102.3195 | 0 | 6.736 | 0 | 48.2932 | 0 | 0 | 40.9696 | 0 | 0 | 269.4388 | 0 | 0 | 579.6097 | 1.378% | CZ 4C | 8.3413 | 3.0363 | 0 | 0 | 0 | 1.9742 | 0 | 14.1539 | 0 | 0 | 12.0075 | 0 | 0 | 25.9692 | 0 | 0 | 65.4824 | 1.378% | CZ 4C | 0 | 0 | 0.73032 | 1.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.5618 | 1.378% | CZ 4C | 87.3246 | 31.7872 | 79.8243 | 111.8352 | 0 | 20.6681 | 0 | 148.1773 | 0 | 0 | 125.7065 | 0 | 0 | 469.5209 | 0 | 0 | 1074.8441 | 1.378%
CZ 5A | 0.88668 | 0.32323 | 0.75081 | 1.9005 | 0 | 0.68213 | 0 | 1.516 | 0 | 0 | 1.2642 | 0 | 0 | 4.5327 | 0 | 0 | 11.8563 | 20.38% | CZ 5A | 28.4604 | 10.3751 | 76.6136 | 193.9254 | 0 | 21.8949 | 0 | 48.6609 | 0 | 0 | 40.5791 | 0 | 0 | 269.4388 | 0 | 0 | 689.9482 | 20.38% | CZ 5A | 8.3413 | 3.0408 | 0 | 0 | 0 | 6.417 | 0 | 14.2617 | 0 | 0 | 11.8931 | 0 | 0 | 25.9692 | 0 | 0 | 69.923 | 20.38% | CZ 5A | 0 | 0 | 0.76614 | 1.9393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.5137 | 20.38% | CZ 5A | 87.3246 | 31.8337 | 83.7387 | 211.9605 | 0 | 67.1799 | 0 | 149.3055 | 0 | 0 | 124.5085 | 0 | 0 | 469.5209 | 0 | 0 | 1225.3723 | 20.38%
CZ 5B | 0.88668 | 0.32323 | 0.73503 | 1.2103 | 0 | 0.7733 | 0 | 1.8017 | 0 | 0 | 1.27 | 0 | 0 | 4.5327 | 0 | 0 | 11.5329 | 5.254% | CZ 5B | 28.4604 | 10.3751 | 75.003 | 123.5005 | 0 | 24.8213 | 0 | 57.8305 | 0 | 0 | 40.7649 | 0 | 0 | 269.4388 | 0 | 0 | 630.1943 | 5.254% | CZ 5B | 8.3413 | 3.0408 | 0 | 0 | 0 | 7.2747 | 0 | 16.9491 | 0 | 0 | 11.9475 | 0 | 0 | 25.9692 | 0 | 0 | 73.5226 | 5.254% | CZ 5B | 0 | 0 | 0.75003 | 1.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.7934 | 5.254% | CZ 5B | 87.3246 | 31.8337 | 81.9783 | 134.986 | 0 | 76.159 | 0 | 177.4406 | 0 | 0 | 125.0784 | 0 | 0 | 469.5209 | 0 | 0 | 1184.3214 | 5.254%
CZ 5C | 0.88668 | 0.32276 | 0.74669 | 1.3147 | 0 | 0.0633 | 0 | 1.3757 | 0 | 0 | 1.2677 | 0 | 0 | 4.5327 | 0 | 0 | 10.5102 | 0.02535% | CZ 5C | 28.4604 | 10.3599 | 76.193 | 134.1535 | 0 | 2.0318 | 0 | 44.1575 | 0 | 0 | 40.6891 | 0 | 0 | 269.4388 | 0 | 0 | 605.4839 | 0.02535% | CZ 5C | 8.3413 | 3.0363 | 0 | 0 | 0 | 0.59549 | 0 | 12.9418 | 0 | 0 | 11.9253 | 0 | 0 | 25.9692 | 0 | 0 | 62.8094 | 0.02535% | CZ 5C | 0 | 0 | 0.76193 | 1.3415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.9118 | 0.02535% | CZ 5C | 87.3246 | 31.7872 | 83.2789 | 146.6297 | 0 | 6.2341 | 0 | 135.488 | 0 | 0 | 124.8458 | 0 | 0 | 469.5209 | 0 | 0 | 1085.1093 | 0.02535%
CZ 6A | 0.88668 | 0.323 | 0.79055 | 2.6388 | 0 | 0.73622 | 0 | 1.5614 | 0 | 0 | 1.2595 | 0 | 0 | 4.5327 | 0 | 0 | 12.7288 | 3.192% | CZ 6A | 28.4604 | 10.3675 | 80.6687 | 269.2619 | 0 | 23.631 | 0 | 50.1165 | 0 | 0 | 40.4275 | 0 | 0 | 269.4388 | 0 | 0 | 772.3723 | 3.192% | CZ 6A | 8.3413 | 3.0385 | 0 | 0 | 0 | 6.9259 | 0 | 14.6883 | 0 | 0 | 11.8486 | 0 | 0 | 25.9692 | 0 | 0 | 70.8118 | 3.192% | CZ 6A | 0 | 0 | 0.80669 | 2.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 5.3076 | 3.192% | CZ 6A | 87.3246 | 31.8104 | 88.1709 | 294.3033 | 0 | 72.5069 | 0 | 153.7718 | 0 | 0 | 124.0433 | 0 | 0 | 469.5209 | 0 | 0 | 1321.4519 | 3.192%
CZ 6B | 0.88668 | 0.32276 | 0.78023 | 1.9352 | 0 | 0.50286 | 0 | 1.693 | 0 | 0 | 1.2592 | 0 | 0 | 4.5327 | 0 | 0 | 11.9126 | 0.5438% | CZ 6B | 28.4604 | 10.3599 | 79.6151 | 197.4688 | 0 | 16.1407 | 0 | 54.3431 | 0 | 0 | 40.4161 | 0 | 0 | 269.4388 | 0 | 0 | 696.2429 | 0.5438% | CZ 6B | 8.3413 | 3.0363 | 0 | 0 | 0 | 4.7306 | 0 | 15.927 | 0 | 0 | 11.8453 | 0 | 0 | 25.9692 | 0 | 0 | 69.8497 | 0.5438% | CZ 6B | 0 | 0 | 0.79615 | 1.9747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 4.5792 | 0.5438% | CZ 6B | 87.3246 | 31.7872 | 87.0193 | 215.8335 | 0 | 49.5243 | 0 | 166.7402 | 0 | 0 | 124.0084 | 0 | 0 | 469.5209 | 0 | 0 | 1231.7583 | 0.5438%
CZ 7 | 0.88668 | 0.32264 | 0.83791 | 3.3739 | 0 | 0.53014 | 0 | 1.5298 | 0 | 0 | 1.252 | 0 | 0 | 4.5327 | 0 | 0 | 13.2657 | 0.271% | CZ 7 | 28.4604 | 10.3561 | 85.5006 | 344.2763 | 0 | 17.0163 | 0 | 49.1044 | 0 | 0 | 40.1849 | 0 | 0 | 269.4388 | 0 | 0 | 844.3377 | 0.271% | CZ 7 | 8.3413 | 3.0352 | 0 | 0 | 0 | 4.9872 | 0 | 14.3917 | 0 | 0 | 11.7775 | 0 | 0 | 25.9692 | 0 | 0 | 68.5021 | 0.271% | CZ 7 | 0 | 0 | 0.85501 | 3.4428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 6.1061 | 0.271% | CZ 7 | 87.3246 | 31.7755 | 93.4522 | 376.294 | 0 | 52.211 | 0 | 150.6663 | 0 | 0 | 123.2989 | 0 | 0 | 469.5209 | 0 | 0 | 1384.5434 | 0.271%
CZ 8 | 0.88668 | 0.32087 | 0.90164 | 4.5906 | 0 | 0.19581 | 0 | 1.4263 | 0 | 0 | 1.2424 | 0 | 0 | 4.5327 | 0 | 0 | 14.0969 | 0.008189% | CZ 8 | 28.4604 | 10.2993 | 92.0038 | 468.4286 | 0 | 6.2849 | 0 | 45.7799 | 0 | 0 | 39.8779 | 0 | 0 | 269.4388 | 0 | 0 | 960.5735 | 0.008189% | CZ 8 | 8.3413 | 3.0185 | 0 | 0 | 0 | 1.842 | 0 | 13.4173 | 0 | 0 | 11.6875 | 0 | 0 | 25.9692 | 0 | 0 | 64.2759 | 0.008189% | CZ 8 | 0 | 0 | 0.92004 | 4.6843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 7.4126 | 0.008189% | CZ 8 | 87.3246 | 31.6011 | 100.5602 | 511.9924 | 0 | 19.284 | 0 | 140.4661 | 0 | 0 | 122.3568 | 0 | 0 | 469.5209 | 0 | 0 | 1483.106 | 0.008189%
US Weighted | 0.88668 | 0.32337 | 0.65768 | 0.94706 | 0 | 1.7413 | 0 | 1.6713 | 0 | 0 | 1.2866 | 0 | 0 | 4.5327 | 0 | 0 | 12.0466 | 100% | US Weighted | 28.4604 | 10.3794 | 67.11 | 96.6386 | 0 | 55.8912 | 0 | 53.6441 | 0 | 0 | 41.298 | 0 | 0 | 269.4388 | 0 | 0 | 622.8604 | 100% | US Weighted | 8.3413 | 3.042 | 0 | 0 | 0 | 16.3808 | 0 | 15.7222 | 0 | 0 | 12.1037 | 0 | 0 | 25.9692 | 0 | 0 | 81.5592 | 100% | US Weighted | 0 | 0 | 0.6711 | 0.96639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8083 | 0 | 0 | 3.4458 | 100% | US Weighted | 87.3246 | 31.8469 | 73.3512 | 105.626 | 0 | 171.4904 | 0 | 164.5955 | 0 | 0 | 126.7142 | 0 | 0 | 469.5209 | 0 | 0 | 1230.4696 | 100%
Building Type: | Quick-service Restaurant |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 2501 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 2501 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.58706 | 0.22002 | 0.0011142 | 0 | 0 | 2.156 | 0 | 0.90581 | 0 | 0 | 0.62202 | 0 | 0 | 0.0034248 | 0 | 0 | 4.4954 | 0% | CZ 0A | 18.8434 | 7.062 | 0.11369 | 0 | 0 | 69.2025 | 0 | 29.0745 | 0 | 0 | 19.9655 | 0 | 0 | 0.10993 | 0 | 0 | 144.3715 | 0% | CZ 0A | 5.5227 | 2.0698 | 0 | 0 | 0 | 20.2821 | 0 | 8.5212 | 0 | 0 | 5.8515 | 0 | 0 | 0.032218 | 0 | 0 | 42.2795 | 0% | CZ 0A | 0 | 0 | 0.0011369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011369 | 0% | CZ 0A | 57.8171 | 21.6683 | 0.12427 | 0 | 0 | 212.3332 | 0 | 89.2088 | 0 | 0 | 61.2598 | 0 | 0 | 0.3373 | 0 | 0 | 442.7488 | 0%
CZ 0B | 0.58765 | 0.22013 | 0.00025998 | 0.00092849 | 0 | 1.7879 | 0 | 1.1664 | 0 | 0 | 0.62698 | 0 | 0 | 0.0034248 | 0 | 0 | 4.3937 | 0% | CZ 0B | 18.8624 | 7.0658 | 0.026528 | 0.094744 | 0 | 57.387 | 0 | 37.4405 | 0 | 0 | 20.1247 | 0 | 0 | 0.10993 | 0 | 0 | 141.1115 | 0% | CZ 0B | 5.5282 | 2.0709 | 0 | 0 | 0 | 16.8192 | 0 | 10.9732 | 0 | 0 | 5.8982 | 0 | 0 | 0.032218 | 0 | 0 | 41.3219 | 0% | CZ 0B | 0 | 0 | 0.00026528 | 0.00094744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012127 | 0% | CZ 0B | 57.8752 | 21.6799 | 0.028995 | 0.10355 | 0 | 176.0798 | 0 | 114.8781 | 0 | 0 | 61.7483 | 0 | 0 | 0.3373 | 0 | 0 | 432.7313 | 0%
CZ 1A | 0.58706 | 0.22013 | 0.0003714 | 7.4279e-05 | 0 | 1.452 | 0 | 0.97041 | 0 | 0 | 0.62178 | 0 | 0 | 0.0034248 | 0 | 0 | 3.8553 | 2.382% | CZ 1A | 18.8434 | 7.0658 | 0.037898 | 0.0075795 | 0 | 46.6063 | 0 | 31.1479 | 0 | 0 | 19.9579 | 0 | 0 | 0.10993 | 0 | 0 | 123.7768 | 2.382% | CZ 1A | 5.5227 | 2.0709 | 0 | 0 | 0 | 13.6595 | 0 | 9.1289 | 0 | 0 | 5.8493 | 0 | 0 | 0.032218 | 0 | 0 | 36.2636 | 2.382% | CZ 1A | 0 | 0 | 0.00037898 | 7.5795e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00045477 | 2.382% | CZ 1A | 57.8171 | 21.6799 | 0.041422 | 0.0082844 | 0 | 143.0016 | 0 | 95.5709 | 0 | 0 | 61.2365 | 0 | 0 | 0.3373 | 0 | 0 | 379.693 | 2.382%
CZ 1B | 0.58683 | 0.22002 | 0 | 0.020984 | 0 | 1.6319 | 0 | 1.163 | 0 | 0 | 0.62568 | 0 | 0 | 0.0034248 | 0 | 0 | 4.2518 | 0% | CZ 1B | 18.8358 | 7.062 | 0 | 2.1412 | 0 | 52.3795 | 0 | 37.3305 | 0 | 0 | 20.083 | 0 | 0 | 0.10993 | 0 | 0 | 137.942 | 0% | CZ 1B | 5.5205 | 2.0698 | 0 | 0 | 0 | 15.3516 | 0 | 10.941 | 0 | 0 | 5.886 | 0 | 0 | 0.032218 | 0 | 0 | 39.8009 | 0% | CZ 1B | 0 | 0 | 0 | 0.021412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021412 | 0% | CZ 1B | 57.7938 | 21.6683 | 0 | 2.3403 | 0 | 160.7154 | 0 | 114.5408 | 0 | 0 | 61.6204 | 0 | 0 | 0.3373 | 0 | 0 | 419.0164 | 0%
CZ 2A | 0.58813 | 0.2199 | 0.00011142 | 0.048541 | 0 | 1.2877 | 0 | 0.99828 | 0 | 0 | 0.62155 | 0 | 0 | 0.0034248 | 0 | 0 | 3.7677 | 20.26% | CZ 2A | 18.8775 | 7.0582 | 0.011369 | 4.9532 | 0 | 41.3335 | 0 | 32.0425 | 0 | 0 | 19.9503 | 0 | 0 | 0.10993 | 0 | 0 | 124.3366 | 20.26% | CZ 2A | 5.5327 | 2.0686 | 0 | 0 | 0 | 12.1142 | 0 | 9.3911 | 0 | 0 | 5.8471 | 0 | 0 | 0.032218 | 0 | 0 | 34.9859 | 20.26% | CZ 2A | 0 | 0 | 0.00011369 | 0.049532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049646 | 20.26% | CZ 2A | 57.9217 | 21.6567 | 0.012427 | 5.4139 | 0 | 126.823 | 0 | 98.3158 | 0 | 0 | 61.2133 | 0 | 0 | 0.3373 | 0 | 0 | 371.6941 | 20.26%
CZ 2B | 0.58813 | 0.22002 | -0.00081707 | 0.03662 | 0 | 1.0224 | 0 | 1.2305 | 0 | 0 | 0.62403 | 0 | 0 | 0.0034248 | 0 | 0 | 3.7242 | 2.859% | CZ 2B | 18.8775 | 7.062 | -0.083375 | 3.7367 | 0 | 32.8158 | 0 | 39.495 | 0 | 0 | 20.0299 | 0 | 0 | 0.10993 | 0 | 0 | 122.0436 | 2.859% | CZ 2B | 5.5327 | 2.0698 | 0 | 0 | 0 | 9.6178 | 0 | 11.5753 | 0 | 0 | 5.8704 | 0 | 0 | 0.032218 | 0 | 0 | 34.6982 | 2.859% | CZ 2B | 0 | 0 | -0.00083375 | 0.037367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036533 | 2.859% | CZ 2B | 57.9217 | 21.6683 | -0.091128 | 4.0842 | 0 | 100.6885 | 0 | 121.1821 | 0 | 0 | 61.4575 | 0 | 0 | 0.3373 | 0 | 0 | 367.2485 | 2.859%
CZ 3A | 0.58801 | 0.2199 | -0.00048281 | 0.099608 | 0 | 0.79291 | 0 | 1.028 | 0 | 0 | 0.61753 | 0 | 0 | 0.0034248 | 0 | 0 | 3.3489 | 19.57% | CZ 3A | 18.8738 | 7.0582 | -0.049267 | 10.1641 | 0 | 25.4506 | 0 | 32.9978 | 0 | 0 | 19.8214 | 0 | 0 | 0.10993 | 0 | 0 | 114.4265 | 19.57% | CZ 3A | 5.5316 | 2.0686 | 0 | 0 | 0 | 7.4591 | 0 | 9.6711 | 0 | 0 | 5.8093 | 0 | 0 | 0.032218 | 0 | 0 | 30.572 | 19.57% | CZ 3A | 0 | 0 | -0.00049267 | 0.10164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10115 | 19.57% | CZ 3A | 57.9101 | 21.6567 | -0.053849 | 11.1094 | 0 | 78.0897 | 0 | 101.2468 | 0 | 0 | 60.8178 | 0 | 0 | 0.3373 | 0 | 0 | 331.1139 | 19.57%
CZ 3B | 0.5873 | 0.2199 | -0.0011142 | 0.034837 | 0 | 0.5527 | 0 | 1.1929 | 0 | 0 | 0.62403 | 0 | 0 | 0.0034248 | 0 | 0 | 3.214 | 6.098% | CZ 3B | 18.851 | 7.0582 | -0.11369 | 3.5548 | 0 | 17.7403 | 0 | 38.2896 | 0 | 0 | 20.0299 | 0 | 0 | 0.10993 | 0 | 0 | 105.5201 | 6.098% | CZ 3B | 5.5249 | 2.0686 | 0 | 0 | 0 | 5.1994 | 0 | 11.222 | 0 | 0 | 5.8704 | 0 | 0 | 0.032218 | 0 | 0 | 29.9176 | 6.098% | CZ 3B | 0 | 0 | -0.0011369 | 0.035548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034411 | 6.098% | CZ 3B | 57.8403 | 21.6567 | -0.12427 | 3.8854 | 0 | 54.4325 | 0 | 117.4835 | 0 | 0 | 61.4575 | 0 | 0 | 0.3373 | 0 | 0 | 316.9689 | 6.098%
CZ 3C | 0.58624 | 0.21954 | -0.00059423 | 0.073425 | 0 | 0.13829 | 0 | 1.0505 | 0 | 0 | 0.62403 | 0 | 0 | 0.0034248 | 0 | 0 | 2.6948 | 0.5719% | CZ 3C | 18.8169 | 7.0469 | -0.060636 | 7.4923 | 0 | 4.4389 | 0 | 33.718 | 0 | 0 | 20.0299 | 0 | 0 | 0.10993 | 0 | 0 | 91.5922 | 0.5719% | CZ 3C | 5.5149 | 2.0653 | 0 | 0 | 0 | 1.301 | 0 | 9.8822 | 0 | 0 | 5.8704 | 0 | 0 | 0.032218 | 0 | 0 | 24.666 | 0.5719% | CZ 3C | 0 | 0 | -0.00060636 | 0.074923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074317 | 0.5719% | CZ 3C | 57.7357 | 21.6218 | -0.066275 | 8.1891 | 0 | 13.6198 | 0 | 103.4566 | 0 | 0 | 61.4575 | 0 | 0 | 0.3373 | 0 | 0 | 266.3515 | 0.5719%
CZ 4A | 0.58647 | 0.21883 | -0.00044567 | 0.45158 | 0 | 0.50073 | 0 | 0.99013 | 0 | 0 | 0.60986 | 0 | 0 | 0.0034248 | 0 | 0 | 3.3606 | 16.6% | CZ 4A | 18.8245 | 7.0241 | -0.045477 | 46.0796 | 0 | 16.0724 | 0 | 31.781 | 0 | 0 | 19.575 | 0 | 0 | 0.10993 | 0 | 0 | 139.4211 | 16.6% | CZ 4A | 5.5171 | 2.0587 | 0 | 0 | 0 | 4.7106 | 0 | 9.3145 | 0 | 0 | 5.7371 | 0 | 0 | 0.032218 | 0 | 0 | 27.3702 | 16.6% | CZ 4A | 0 | 0 | -0.00045477 | 0.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46034 | 16.6% | CZ 4A | 57.7589 | 21.552 | -0.049706 | 50.365 | 0 | 49.3149 | 0 | 97.5132 | 0 | 0 | 60.0618 | 0 | 0 | 0.3373 | 0 | 0 | 336.8535 | 16.6%
CZ 4B | 0.58789 | 0.21966 | -0.0010028 | 0.17207 | 0 | 0.31319 | 0 | 1.2196 | 0 | 0 | 0.61647 | 0 | 0 | 0.0034248 | 0 | 0 | 3.1313 | 0.604% | CZ 4B | 18.87 | 7.0506 | -0.10232 | 17.5579 | 0 | 10.0529 | 0 | 39.1463 | 0 | 0 | 19.7873 | 0 | 0 | 0.10993 | 0 | 0 | 112.4726 | 0.604% | CZ 4B | 5.5305 | 2.0664 | 0 | 0 | 0 | 2.9463 | 0 | 11.4731 | 0 | 0 | 5.7993 | 0 | 0 | 0.032218 | 0 | 0 | 27.8479 | 0.604% | CZ 4B | 0 | 0 | -0.0010232 | 0.17558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17456 | 0.604% | CZ 4B | 57.8985 | 21.6334 | -0.11184 | 19.1908 | 0 | 30.8451 | 0 | 120.112 | 0 | 0 | 60.7132 | 0 | 0 | 0.3373 | 0 | 0 | 310.6184 | 0.604%
CZ 4C | 0.58635 | 0.21848 | -0.0010028 | 0.46042 | 0 | 0.039799 | 0 | 0.96226 | 0 | 0 | 0.6147 | 0 | 0 | 0.0034248 | 0 | 0 | 2.8844 | 1.378% | CZ 4C | 18.8207 | 7.0127 | -0.10232 | 46.9816 | 0 | 1.2775 | 0 | 30.8864 | 0 | 0 | 19.7304 | 0 | 0 | 0.10993 | 0 | 0 | 124.7169 | 1.378% | CZ 4C | 5.516 | 2.0553 | 0 | 0 | 0 | 0.3744 | 0 | 9.0523 | 0 | 0 | 5.7827 | 0 | 0 | 0.032218 | 0 | 0 | 22.8129 | 1.378% | CZ 4C | 0 | 0 | -0.0010232 | 0.46982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46879 | 1.378% | CZ 4C | 57.7473 | 21.5171 | -0.11184 | 51.3508 | 0 | 3.9196 | 0 | 94.7684 | 0 | 0 | 60.5387 | 0 | 0 | 0.3373 | 0 | 0 | 290.0674 | 1.378%
CZ 5A | 0.58753 | 0.21942 | -0.00040854 | 0.64155 | 0 | 0.30717 | 0 | 0.94194 | 0 | 0 | 0.60572 | 0 | 0 | 0.0034248 | 0 | 0 | 3.3064 | 20.38% | CZ 5A | 18.8586 | 7.0431 | -0.041687 | 65.4642 | 0 | 9.8595 | 0 | 30.2344 | 0 | 0 | 19.4424 | 0 | 0 | 0.10993 | 0 | 0 | 150.9704 | 20.38% | CZ 5A | 5.5271 | 2.0642 | 0 | 0 | 0 | 2.8897 | 0 | 8.8612 | 0 | 0 | 5.6982 | 0 | 0 | 0.032218 | 0 | 0 | 25.0726 | 20.38% | CZ 5A | 0 | 0 | -0.00041687 | 0.65464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65422 | 20.38% | CZ 5A | 57.8636 | 21.6102 | -0.045564 | 71.5524 | 0 | 30.2519 | 0 | 92.7678 | 0 | 0 | 59.6548 | 0 | 0 | 0.3373 | 0 | 0 | 333.9923 | 20.38%
CZ 5B | 0.5873 | 0.21919 | -0.00092849 | 0.27936 | 0 | 0.37425 | 0 | 1.1381 | 0 | 0 | 0.61151 | 0 | 0 | 0.0034248 | 0 | 0 | 3.2122 | 5.254% | CZ 5B | 18.851 | 7.0355 | -0.094744 | 28.5065 | 0 | 12.0126 | 0 | 36.5307 | 0 | 0 | 19.6281 | 0 | 0 | 0.10993 | 0 | 0 | 122.5796 | 5.254% | CZ 5B | 5.5249 | 2.062 | 0 | 0 | 0 | 3.5207 | 0 | 10.7065 | 0 | 0 | 5.7527 | 0 | 0 | 0.032218 | 0 | 0 | 27.599 | 5.254% | CZ 5B | 0 | 0 | -0.00094744 | 0.28507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28412 | 5.254% | CZ 5B | 57.8403 | 21.5869 | -0.10355 | 31.1576 | 0 | 36.8582 | 0 | 112.0867 | 0 | 0 | 60.2247 | 0 | 0 | 0.3373 | 0 | 0 | 319.9882 | 5.254%
CZ 5C | 0.58647 | 0.2186 | -0.0010399 | 0.60047 | 0 | -0.0016534 | 0 | 0.85207 | 0 | 0 | 0.61186 | 0 | 0 | 0.0034248 | 0 | 0 | 2.8702 | 0.02535% | CZ 5C | 18.8245 | 7.0165 | -0.10611 | 61.2727 | 0 | -0.053069 | 0 | 27.3497 | 0 | 0 | 19.6395 | 0 | 0 | 0.10993 | 0 | 0 | 134.0536 | 0.02535% | CZ 5C | 5.5171 | 2.0564 | 0 | 0 | 0 | -0.015554 | 0 | 8.0157 | 0 | 0 | 5.756 | 0 | 0 | 0.032218 | 0 | 0 | 21.362 | 0.02535% | CZ 5C | 0 | 0 | -0.0010611 | 0.61273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61167 | 0.02535% | CZ 5C | 57.7589 | 21.5287 | -0.11598 | 66.9711 | 0 | -0.16283 | 0 | 83.9168 | 0 | 0 | 60.2596 | 0 | 0 | 0.3373 | 0 | 0 | 290.4935 | 0.02535%
CZ 6A | 0.5873 | 0.21895 | -0.00040854 | 0.78844 | 0 | 0.32512 | 0 | 0.95151 | 0 | 0 | 0.60348 | 0 | 0 | 0.0034248 | 0 | 0 | 3.4778 | 3.192% | CZ 6A | 18.851 | 7.0279 | -0.041687 | 80.4527 | 0 | 10.4357 | 0 | 30.5414 | 0 | 0 | 19.3703 | 0 | 0 | 0.10993 | 0 | 0 | 166.7473 | 3.192% | CZ 6A | 5.5249 | 2.0598 | 0 | 0 | 0 | 3.0585 | 0 | 8.9512 | 0 | 0 | 5.6771 | 0 | 0 | 0.032218 | 0 | 0 | 25.3037 | 3.192% | CZ 6A | 0 | 0 | -0.00041687 | 0.80453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80411 | 3.192% | CZ 6A | 57.8403 | 21.5636 | -0.045564 | 87.9348 | 0 | 32.0198 | 0 | 93.7099 | 0 | 0 | 59.4338 | 0 | 0 | 0.3373 | 0 | 0 | 352.794 | 3.192%
CZ 6B | 0.58789 | 0.21895 | -0.00085421 | 0.5263 | 0 | 0.24753 | 0 | 1.0564 | 0 | 0 | 0.60619 | 0 | 0 | 0.0034248 | 0 | 0 | 3.2458 | 0.5438% | CZ 6B | 18.87 | 7.0279 | -0.087164 | 53.7046 | 0 | 7.9452 | 0 | 33.9076 | 0 | 0 | 19.4575 | 0 | 0 | 0.10993 | 0 | 0 | 140.9355 | 0.5438% | CZ 6B | 5.5305 | 2.0598 | 0 | 0 | 0 | 2.3286 | 0 | 9.9377 | 0 | 0 | 5.7027 | 0 | 0 | 0.032218 | 0 | 0 | 25.5915 | 0.5438% | CZ 6B | 0 | 0 | -0.00087164 | 0.53705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53617 | 0.5438% | CZ 6B | 57.8985 | 21.5636 | -0.095271 | 58.6991 | 0 | 24.3783 | 0 | 104.0382 | 0 | 0 | 59.7013 | 0 | 0 | 0.3373 | 0 | 0 | 326.521 | 0.5438%
CZ 7 | 0.58753 | 0.21836 | -0.0003714 | 1.0223 | 0 | 0.2486 | 0 | 0.92872 | 0 | 0 | 0.59982 | 0 | 0 | 0.0034248 | 0 | 0 | 3.6083 | 0.271% | CZ 7 | 18.8586 | 7.009 | -0.037898 | 104.3129 | 0 | 7.9794 | 0 | 29.8098 | 0 | 0 | 19.2528 | 0 | 0 | 0.10993 | 0 | 0 | 187.2945 | 0.271% | CZ 7 | 5.5271 | 2.0542 | 0 | 0 | 0 | 2.3386 | 0 | 8.7368 | 0 | 0 | 5.6427 | 0 | 0 | 0.032218 | 0 | 0 | 24.3316 | 0.271% | CZ 7 | 0 | 0 | -0.00037898 | 1.0431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0428 | 0.271% | CZ 7 | 57.8636 | 21.5055 | -0.041422 | 114.014 | 0 | 24.483 | 0 | 91.4652 | 0 | 0 | 59.0732 | 0 | 0 | 0.3373 | 0 | 0 | 368.7004 | 0.271%
CZ 8 | 0.58305 | 0.2147 | -0.00044567 | 1.2606 | 0 | 0.10865 | 0 | 0.82526 | 0 | 0 | 0.59663 | 0 | 0 | 0.0034248 | 0 | 0 | 3.5918 | 0.008189% | CZ 8 | 18.7145 | 6.8914 | -0.045477 | 128.628 | 0 | 3.4874 | 0 | 26.4892 | 0 | 0 | 19.1505 | 0 | 0 | 0.10993 | 0 | 0 | 203.4255 | 0.008189% | CZ 8 | 5.4849 | 2.0198 | 0 | 0 | 0 | 1.0221 | 0 | 7.7635 | 0 | 0 | 5.6127 | 0 | 0 | 0.032218 | 0 | 0 | 21.9352 | 0.008189% | CZ 8 | 0 | 0 | -0.00045477 | 1.2863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2858 | 0.008189% | CZ 8 | 57.4216 | 21.1449 | -0.049706 | 140.5904 | 0 | 10.7004 | 0 | 81.2765 | 0 | 0 | 58.7592 | 0 | 0 | 0.3373 | 0 | 0 | 370.1807 | 0.008189%
US Weighted | 0.58752 | 0.21953 | -0.00040268 | 0.29176 | 0 | 0.69462 | 0 | 1.0162 | 0 | 0 | 0.61446 | 0 | 0 | 0.0034248 | 0 | 0 | 3.4271 | 100% | US Weighted | 18.8582 | 7.0465 | -0.04109 | 29.7714 | 0 | 22.2958 | 0 | 32.6172 | 0 | 0 | 19.7228 | 0 | 0 | 0.10993 | 0 | 0 | 130.3808 | 100% | US Weighted | 5.527 | 2.0652 | 0 | 0 | 0 | 6.5345 | 0 | 9.5596 | 0 | 0 | 5.7804 | 0 | 0 | 0.032218 | 0 | 0 | 29.499 | 100% | US Weighted | 0 | 0 | -0.0004109 | 0.29771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2973 | 100% | US Weighted | 57.8623 | 21.6208 | -0.044911 | 32.5401 | 0 | 68.4099 | 0 | 100.079 | 0 | 0 | 60.5154 | 0 | 0 | 0.3373 | 0 | 0 | 341.3199 | 100%
Building Type: | Quick-service Restaurant |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Quick-service Restaurant |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Quick-service Restaurant |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 2501 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 2501 | [17 empty] | Prototype Floor Area: | 2501 | Building Type: | Quick-service Restaurant | [15 empty] | Prototype Floor Area: | 2501 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 66.21% | 67.94% | 0.2405% |  |  | 34.62% |  | 50.1% |  |  | 46.8% |  |  | 0.07556% |  |  | 28.87% | 0% | CZ 0A | 66.21% | 67.94% | 0.2405% |  |  | 34.62% |  | 50.1% |  |  | 46.8% |  |  | 0.0408% |  |  | 22% | 0% | CZ 0A | 66.21% | 67.94% |  |  |  | 34.62% |  | 50.1% |  |  | 46.8% |  |  | 0.1241% |  |  | 33.7% | 0% | CZ 0A |  |  | 0.2405% | [10 empty] | 0% |  |  | 0.04984% | 0% | CZ 0A | 66.21% | 67.94% | 0.2405% |  |  | 34.62% |  | 50.1% |  |  | 46.8% |  |  | 0.07184% |  |  | 28.33% | 0%
CZ 0B | 66.28% | 67.95% | 0.05644% | 71.43% |  | 32.92% |  | 56.28% |  |  | 47.17% |  |  | 0.07556% |  |  | 29.22% | 0% | CZ 0B | 66.28% | 67.95% | 0.05644% | 71.43% |  | 32.92% |  | 56.28% |  |  | 47.17% |  |  | 0.0408% |  |  | 22.08% | 0% | CZ 0B | 66.28% | 67.95% |  |  |  | 32.92% |  | 56.28% |  |  | 47.17% |  |  | 0.1241% |  |  | 34.3% | 0% | CZ 0B |  |  | 0.05644% | 71.43% | [9 empty] | 0% |  |  | 0.0532% | 0% | CZ 0B | 66.28% | 67.95% | 0.05644% | 71.43% |  | 32.92% |  | 56.28% |  |  | 47.17% |  |  | 0.07184% |  |  | 28.65% | 0%
CZ 1A | 66.21% | 67.95% | 0.07359% | 100% |  | 36.76% |  | 58.73% |  |  | 47.19% |  |  | 0.07556% |  |  | 29.28% | 2.382% | CZ 1A | 66.21% | 67.95% | 0.07359% | 100% |  | 36.76% |  | 58.73% |  |  | 47.19% |  |  | 0.0408% |  |  | 21.27% | 2.382% | CZ 1A | 66.21% | 67.95% |  |  |  | 36.76% |  | 58.73% |  |  | 47.19% |  |  | 0.1241% |  |  | 35.39% | 2.382% | CZ 1A |  |  | 0.07359% | 100% | [9 empty] | 0% |  |  | 0.01957% | 2.382% | CZ 1A | 66.21% | 67.95% | 0.07359% | 100% |  | 36.76% |  | 58.73% |  |  | 47.19% |  |  | 0.07184% |  |  | 28.62% | 2.382%
CZ 1B | 66.18% | 67.99% | 0% | 37.82% |  | 37.14% |  | 57.46% |  |  | 47.35% |  |  | 0.07556% |  |  | 30.28% | 0% | CZ 1B | 66.18% | 67.99% | 0% | 37.82% |  | 37.14% |  | 57.46% |  |  | 47.35% |  |  | 0.0408% |  |  | 22.47% | 0% | CZ 1B | 66.18% | 67.99% |  |  |  | 37.14% |  | 57.46% |  |  | 47.35% |  |  | 0.1241% |  |  | 36.13% | 0% | CZ 1B |  |  | 0% | 37.82% | [9 empty] | 0% |  |  | 0.8994% | 0% | CZ 1B | 66.18% | 67.99% | 0% | 37.82% |  | 37.14% |  | 57.46% |  |  | 47.35% |  |  | 0.07184% |  |  | 29.64% | 0%
CZ 2A | 66.33% | 67.98% | 0.0202% | 34.49% |  | 37.7% |  | 57.75% |  |  | 47.34% |  |  | 0.07556% |  |  | 29.22% | 20.26% | CZ 2A | 66.33% | 67.98% | 0.0202% | 34.49% |  | 37.7% |  | 57.75% |  |  | 47.34% |  |  | 0.0408% |  |  | 21.21% | 20.26% | CZ 2A | 66.33% | 67.98% |  |  |  | 37.7% |  | 57.75% |  |  | 47.34% |  |  | 0.1241% |  |  | 35.66% | 20.26% | CZ 2A |  |  | 0.0202% | 34.49% | [9 empty] | 0% |  |  | 1.974% | 20.26% | CZ 2A | 66.33% | 67.98% | 0.0202% | 34.49% |  | 37.7% |  | 57.75% |  |  | 47.34% |  |  | 0.07184% |  |  | 28.55% | 20.26%
CZ 2B | 66.33% | 67.97% | -0.1474% | 31.88% |  | 41.22% |  | 61.41% |  |  | 47.82% |  |  | 0.07556% |  |  | 30.52% | 2.859% | CZ 2B | 66.33% | 67.97% | -0.1474% | 31.88% |  | 41.22% |  | 61.41% |  |  | 47.82% |  |  | 0.0408% |  |  | 21.7% | 2.859% | CZ 2B | 66.33% | 67.97% |  |  |  | 41.22% |  | 61.41% |  |  | 47.82% |  |  | 0.1241% |  |  | 37.79% | 2.859% | CZ 2B |  |  | -0.1474% | 31.88% | [9 empty] | 0% |  |  | 1.467% | 2.859% | CZ 2B | 66.33% | 67.97% | -0.1474% | 31.88% |  | 41.22% |  | 61.41% |  |  | 47.82% |  |  | 0.07184% |  |  | 29.77% | 2.859%
CZ 3A | 66.32% | 67.96% | -0.07632% | 17.11% |  | 41.53% |  | 60.12% |  |  | 47.74% |  |  | 0.07556% |  |  | 28.21% | 19.57% | CZ 3A | 66.32% | 67.96% | -0.07632% | 17.11% |  | 41.53% |  | 60.12% |  |  | 47.74% |  |  | 0.0408% |  |  | 19.4% | 19.57% | CZ 3A | 66.32% | 67.96% |  |  |  | 41.53% |  | 60.12% |  |  | 47.74% |  |  | 0.1241% |  |  | 36.58% | 19.57% | CZ 3A |  |  | -0.07632% | 17.11% | [9 empty] | 0% |  |  | 3.319% | 19.57% | CZ 3A | 66.32% | 67.96% | -0.07632% | 17.11% |  | 41.53% |  | 60.12% |  |  | 47.74% |  |  | 0.07184% |  |  | 27.41% | 19.57%
CZ 3B | 66.24% | 67.96% | -0.1822% | 11.59% |  | 35.48% |  | 61.8% |  |  | 48.07% |  |  | 0.07556% |  |  | 28.09% | 6.098% | CZ 3B | 66.24% | 67.96% | -0.1822% | 11.59% |  | 35.48% |  | 61.8% |  |  | 48.07% |  |  | 0.0408% |  |  | 19.01% | 6.098% | CZ 3B | 66.24% | 67.96% |  |  |  | 35.48% |  | 61.8% |  |  | 48.07% |  |  | 0.1241% |  |  | 36.32% | 6.098% | CZ 3B |  |  | -0.1822% | 11.59% | [9 empty] | 0% |  |  | 1.256% | 6.098% | CZ 3B | 66.24% | 67.96% | -0.1822% | 11.59% |  | 35.48% |  | 61.8% |  |  | 48.07% |  |  | 0.07184% |  |  | 27.28% | 6.098%
CZ 3C | 66.12% | 67.85% | -0.09272% | 38.23% |  | 26.36% |  | 64.5% |  |  | 47.8% |  |  | 0.07556% |  |  | 26.86% | 0.5719% | CZ 3C | 66.12% | 67.85% | -0.09272% | 38.23% |  | 26.36% |  | 64.5% |  |  | 47.8% |  |  | 0.0408% |  |  | 18.16% | 0.5719% | CZ 3C | 66.12% | 67.85% |  |  |  | 26.36% |  | 64.5% |  |  | 47.8% |  |  | 0.1241% |  |  | 35.29% | 0.5719% | CZ 3C |  |  | -0.09272% | 38.23% | [9 empty] | 0% |  |  | 2.796% | 0.5719% | CZ 3C | 66.12% | 67.85% | -0.09272% | 38.23% |  | 26.36% |  | 64.5% |  |  | 47.8% |  |  | 0.07184% |  |  | 26.06% | 0.5719%
CZ 4A | 66.14% | 67.73% | -0.06396% | 35.92% |  | 42.21% |  | 62.42% |  |  | 47.85% |  |  | 0.07556% |  |  | 28.62% | 16.6% | CZ 4A | 66.14% | 67.73% | -0.06396% | 35.92% |  | 42.21% |  | 62.42% |  |  | 47.85% |  |  | 0.0408% |  |  | 21.87% | 16.6% | CZ 4A | 66.14% | 67.73% |  |  |  | 42.21% |  | 62.42% |  |  | 47.85% |  |  | 0.1241% |  |  | 36.29% | 16.6% | CZ 4A |  |  | -0.06396% | 35.92% | [9 empty] | 0% |  |  | 12.11% | 16.6% | CZ 4A | 66.14% | 67.73% | -0.06396% | 35.92% |  | 42.21% |  | 62.42% |  |  | 47.85% |  |  | 0.07184% |  |  | 27.95% | 16.6%
CZ 4B | 66.3% | 67.93% | -0.1479% | 26.98% |  | 34.93% |  | 64.79% |  |  | 48.11% |  |  | 0.07556% |  |  | 28.16% | 0.604% | CZ 4B | 66.3% | 67.93% | -0.1479% | 26.98% |  | 34.93% |  | 64.79% |  |  | 48.11% |  |  | 0.0408% |  |  | 19.63% | 0.604% | CZ 4B | 66.3% | 67.93% |  |  |  | 34.93% |  | 64.79% |  |  | 48.11% |  |  | 0.1241% |  |  | 36.86% | 0.604% | CZ 4B |  |  | -0.1479% | 26.98% | [9 empty] | 0% |  |  | 5.54% | 0.604% | CZ 4B | 66.3% | 67.93% | -0.1479% | 26.98% |  | 34.93% |  | 64.79% |  |  | 48.11% |  |  | 0.07184% |  |  | 27.36% | 0.604%
CZ 4C | 66.13% | 67.69% | -0.1401% | 45.92% |  | 18.96% |  | 63.96% |  |  | 48.16% |  |  | 0.07556% |  |  | 27.6% | 1.378% | CZ 4C | 66.13% | 67.69% | -0.1401% | 45.92% |  | 18.96% |  | 63.96% |  |  | 48.16% |  |  | 0.0408% |  |  | 21.52% | 1.378% | CZ 4C | 66.13% | 67.69% |  |  |  | 18.96% |  | 63.96% |  |  | 48.16% |  |  | 0.1241% |  |  | 34.84% | 1.378% | CZ 4C |  |  | -0.1401% | 45.92% | [9 empty] | 0% |  |  | 13.16% | 1.378% | CZ 4C | 66.13% | 67.69% | -0.1401% | 45.92% |  | 18.96% |  | 63.96% |  |  | 48.16% |  |  | 0.07184% |  |  | 26.99% | 1.378%
CZ 5A | 66.26% | 67.88% | -0.05441% | 33.76% |  | 45.03% |  | 62.13% |  |  | 47.91% |  |  | 0.07556% |  |  | 27.89% | 20.38% | CZ 5A | 66.26% | 67.88% | -0.05441% | 33.76% |  | 45.03% |  | 62.13% |  |  | 47.91% |  |  | 0.0408% |  |  | 21.88% | 20.38% | CZ 5A | 66.26% | 67.88% |  |  |  | 45.03% |  | 62.13% |  |  | 47.91% |  |  | 0.1241% |  |  | 35.86% | 20.38% | CZ 5A |  |  | -0.05441% | 33.76% | [9 empty] | 0% |  |  | 14.49% | 20.38% | CZ 5A | 66.26% | 67.88% | -0.05441% | 33.76% |  | 45.03% |  | 62.13% |  |  | 47.91% |  |  | 0.07184% |  |  | 27.26% | 20.38%
CZ 5B | 66.24% | 67.81% | -0.1263% | 23.08% |  | 48.4% |  | 63.17% |  |  | 48.15% |  |  | 0.07556% |  |  | 27.85% | 5.254% | CZ 5B | 66.24% | 67.81% | -0.1263% | 23.08% |  | 48.4% |  | 63.17% |  |  | 48.15% |  |  | 0.0408% |  |  | 19.45% | 5.254% | CZ 5B | 66.24% | 67.81% |  |  |  | 48.4% |  | 63.17% |  |  | 48.15% |  |  | 0.1241% |  |  | 37.54% | 5.254% | CZ 5B |  |  | -0.1263% | 23.08% | [9 empty] | 0% |  |  | 7.49% | 5.254% | CZ 5B | 66.24% | 67.81% | -0.1263% | 23.08% |  | 48.4% |  | 63.17% |  |  | 48.15% |  |  | 0.07184% |  |  | 27.02% | 5.254%
CZ 5C | 66.14% | 67.73% | -0.1393% | 45.67% |  | -2.612% |  | 61.94% |  |  | 48.27% |  |  | 0.07556% |  |  | 27.31% | 0.02535% | CZ 5C | 66.14% | 67.73% | -0.1393% | 45.67% |  | -2.612% |  | 61.94% |  |  | 48.27% |  |  | 0.0408% |  |  | 22.14% | 0.02535% | CZ 5C | 66.14% | 67.73% |  |  |  | -2.612% |  | 61.94% |  |  | 48.27% |  |  | 0.1241% |  |  | 34.01% | 0.02535% | CZ 5C |  |  | -0.1393% | 45.67% | [9 empty] | 0% |  |  | 15.64% | 0.02535% | CZ 5C | 66.14% | 67.73% | -0.1393% | 45.67% |  | -2.612% |  | 61.94% |  |  | 48.27% |  |  | 0.07184% |  |  | 26.77% | 0.02535%
CZ 6A | 66.24% | 67.79% | -0.05168% | 29.88% |  | 44.16% |  | 60.94% |  |  | 47.91% |  |  | 0.07556% |  |  | 27.32% | 3.192% | CZ 6A | 66.24% | 67.79% | -0.05168% | 29.88% |  | 44.16% |  | 60.94% |  |  | 47.91% |  |  | 0.0408% |  |  | 21.59% | 3.192% | CZ 6A | 66.24% | 67.79% |  |  |  | 44.16% |  | 60.94% |  |  | 47.91% |  |  | 0.1241% |  |  | 35.73% | 3.192% | CZ 6A |  |  | -0.05168% | 29.88% | [9 empty] | 0% |  |  | 15.15% | 3.192% | CZ 6A | 66.24% | 67.79% | -0.05168% | 29.88% |  | 44.16% |  | 60.94% |  |  | 47.91% |  |  | 0.07184% |  |  | 26.7% | 3.192%
CZ 6B | 66.3% | 67.84% | -0.1095% | 27.2% |  | 49.22% |  | 62.4% |  |  | 48.14% |  |  | 0.07556% |  |  | 27.25% | 0.5438% | CZ 6B | 66.3% | 67.84% | -0.1095% | 27.2% |  | 49.22% |  | 62.4% |  |  | 48.14% |  |  | 0.0408% |  |  | 20.24% | 0.5438% | CZ 6B | 66.3% | 67.84% |  |  |  | 49.22% |  | 62.4% |  |  | 48.14% |  |  | 0.1241% |  |  | 36.64% | 0.5438% | CZ 6B |  |  | -0.1095% | 27.2% | [9 empty] | 0% |  |  | 11.71% | 0.5438% | CZ 6B | 66.3% | 67.84% | -0.1095% | 27.2% |  | 49.22% |  | 62.4% |  |  | 48.14% |  |  | 0.07184% |  |  | 26.51% | 0.5438%
CZ 7 | 66.26% | 67.68% | -0.04432% | 30.3% |  | 46.89% |  | 60.71% |  |  | 47.91% |  |  | 0.07556% |  |  | 27.2% | 0.271% | CZ 7 | 66.26% | 67.68% | -0.04432% | 30.3% |  | 46.89% |  | 60.71% |  |  | 47.91% |  |  | 0.0408% |  |  | 22.18% | 0.271% | CZ 7 | 66.26% | 67.68% |  |  |  | 46.89% |  | 60.71% |  |  | 47.91% |  |  | 0.1241% |  |  | 35.52% | 0.271% | CZ 7 |  |  | -0.04432% | 30.3% | [9 empty] | 0% |  |  | 17.08% | 0.271% | CZ 7 | 66.26% | 67.68% | -0.04432% | 30.3% |  | 46.89% |  | 60.71% |  |  | 47.91% |  |  | 0.07184% |  |  | 26.63% | 0.271%
CZ 8 | 65.76% | 66.91% | -0.04943% | 27.46% |  | 55.49% |  | 57.86% |  |  | 48.02% |  |  | 0.07556% |  |  | 25.48% | 0.008189% | CZ 8 | 65.76% | 66.91% | -0.04943% | 27.46% |  | 55.49% |  | 57.86% |  |  | 48.02% |  |  | 0.0408% |  |  | 21.18% | 0.008189% | CZ 8 | 65.76% | 66.91% |  |  |  | 55.49% |  | 57.86% |  |  | 48.02% |  |  | 0.1241% |  |  | 34.13% | 0.008189% | CZ 8 |  |  | -0.04943% | 27.46% | [9 empty] | 0% |  |  | 17.35% | 0.008189% | CZ 8 | 65.76% | 66.91% | -0.04943% | 27.46% |  | 55.49% |  | 57.86% |  |  | 48.02% |  |  | 0.07184% |  |  | 24.96% | 0.008189%
US Weighted | 66.26% | 67.89% | -0.05852% | 30.61% | 0% | 41.14% | 0% | 60.85% | 0% | 0% | 47.76% | 0% | 0% | 0.07556% | 0% | 0% | 28.43% | 100% | US Weighted | 66.26% | 67.89% | -0.05852% | 30.61% | 0% | 41.14% | 0% | 60.85% | 0% | 0% | 47.76% | 0% | 0% | 0.0408% | 0% | 0% | 20.88% | 100% | US Weighted | 66.26% | 67.89% | 0% | 0% | 0% | 41.14% | 0% | 60.85% | 0% | 0% | 47.76% | 0% | 0% | 0.1241% | 0% | 0% | 36.18% | 100% | US Weighted | 0% | 0% | -0.05852% | 30.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.356% | 100% | US Weighted | 66.26% | 67.89% | -0.05852% | 30.61% | 0% | 41.14% | 0% | 60.85% | 0% | 0% | 47.76% | 0% | 0% | 0.07184% | 0% | 0% | 27.72% | 100%

## RestFS
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 5502 |  | Building Type: | Full-service Restaurant |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Building Type: | Full-service Restaurant |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Full-service Restaurant |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Full-service Restaurant | [14 empty] | Prototype Floor Area: | 5502 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.26975 | 0.10005 | 0.92483 | 0.46682 | 0 | 0.9176 | 0 | 0.56104 | 0 | 0.0024157 | 0.29892 | 0 | 0 | 3.0318 | 0 | 0 | 6.5733 |  | STD2019 | 8.6582 | 3.2114 | 66.0368 | 47.635 | 0 | 29.4529 | 0 | 18.0081 | 0 | 0.077539 | 9.5945 | 0 | 0 | 152.7879 | 0 | 0 | 335.4624 |  | STD2019 | 2.5376 | 0.94119 | 3.8109 | 0 | 0 | 8.6322 | 0 | 5.2779 | 0 | 0.022725 | 2.812 | 0 | 0 | 21.0604 | 0 | 0 | 45.0949 |  | STD2019 | 0 | 0 | 0.53034 | 0.47635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.816 |  | STD2019 | 26.566 | 9.8534 | 97.8623 | 52.0651 | 0 | 90.3701 | 0 | 55.2542 | 0 | 0.23791 | 29.4388 | 0 | 0 | 308.9379 | 0 | 0 | 670.5855
STD2016 | 0.2939 | 0.10005 | 0.92474 | 0.46438 | 0 | 0.95587 | 0 | 0.57144 | 0 | 0.0024157 | 0.45301 | 0 | 0 | 3.0318 | 0 | 0 | 6.7976 |  | STD2016 | 9.4336 | 3.2114 | 66.0296 | 47.386 | 0 | 30.6812 | 0 | 18.3419 | 0 | 0.077539 | 14.5405 | 0 | 0 | 152.7879 | 0 | 0 | 342.4895 |  | STD2016 | 2.7648 | 0.94119 | 3.8106 | 0 | 0 | 8.9921 | 0 | 5.3757 | 0 | 0.022725 | 4.2616 | 0 | 0 | 21.0604 | 0 | 0 | 47.2292 |  | STD2016 | 0 | 0 | 0.53028 | 0.47386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8134 |  | STD2016 | 28.945 | 9.8534 | 97.8523 | 51.7928 | 0 | 94.1388 | 0 | 56.2782 | 0 | 0.23791 | 44.6144 | 0 | 0 | 308.9379 | 0 | 0 | 692.6507
STD2013 | 0.37519 | 0.17725 | 0.92504 | 0.4593 | 0 | 0.97433 | 0 | 0.5769 | 0 | 0.0024157 | 0.45301 | 0 | 0 | 3.0318 | 0 | 0 | 6.9753 |  | STD2013 | 12.0429 | 5.6892 | 66.0606 | 46.8673 | 0 | 31.2739 | 0 | 18.5171 | 0 | 0.077539 | 14.5405 | 0 | 0 | 152.7879 | 0 | 0 | 347.857 |  | STD2013 | 3.5296 | 1.6674 | 3.8106 | 0 | 0 | 9.1659 | 0 | 5.4271 | 0 | 0.022725 | 4.2616 | 0 | 0 | 21.0604 | 0 | 0 | 48.9452 |  | STD2013 | 0 | 0 | 0.53059 | 0.46867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8086 |  | STD2013 | 36.9512 | 17.4561 | 97.8861 | 51.2259 | 0 | 95.9575 | 0 | 56.8159 | 0 | 0.23791 | 44.6145 | 0 | 0 | 308.9379 | 0 | 0 | 710.083
STD2010 | 0.40254 | 0.17725 | 0.92521 | 0.46384 | 0 | 1.0153 | 0 | 0.77941 | 0 | 0.0024157 | 0.57459 | 0 | 0 | 3.0327 | 0 | 0 | 7.3732 |  | STD2010 | 12.9206 | 5.6892 | 66.0753 | 47.3311 | 0 | 32.5887 | 0 | 25.0172 | 0 | 0.077539 | 18.4432 | 0 | 0 | 152.8155 | 0 | 0 | 360.9584 |  | STD2010 | 3.7868 | 1.6674 | 3.8109 | 0 | 0 | 9.5512 | 0 | 7.3321 | 0 | 0.022725 | 5.4054 | 0 | 0 | 21.0685 | 0 | 0 | 52.6451 |  | STD2010 | 0 | 0 | 0.53072 | 0.47331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8133 |  | STD2010 | 39.6442 | 17.4561 | 97.9049 | 51.7329 | 0 | 99.9914 | 0 | 76.7601 | 0 | 0.23791 | 56.5892 | 0 | 0 | 309.0225 | 0 | 0 | 749.3391
STD2007 | 0.99662 | 0.31167 | 0.93757 | 0.43682 | 0 | 1.4895 | 0 | 1.659 | 0 | 0.0024157 | 0.57248 | 0 | 0 | 3.0348 | 0 | 0 | 9.4409 |  | STD2007 | 31.9893 | 10.0041 | 66.5135 | 44.5733 | 0 | 47.8105 | 0 | 53.2497 | 0 | 0.077539 | 18.3753 | 0 | 0 | 152.8844 | 0 | 0 | 425.4776 |  | STD2007 | 9.3755 | 2.932 | 3.9216 | 0 | 0 | 14.0125 | 0 | 15.6066 | 0 | 0.022725 | 5.3855 | 0 | 0 | 21.0887 | 0 | 0 | 72.3452 |  | STD2007 | 0 | 0 | 0.53133 | 0.44573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7864 |  | STD2007 | 98.1523 | 30.6954 | 99.1297 | 48.7186 | 0 | 146.6964 | 0 | 163.3856 | 0 | 0.23791 | 56.3808 | 0 | 0 | 309.234 | 0 | 0 | 952.6307
STD2004 | 0.99662 | 0.31167 | 0.93528 | 0.72345 | 0 | 1.7986 | 0 | 1.7809 | 0 | 0.0024157 | 0.58688 | 0 | 0 | 3.0348 | 0 | 0 | 10.1707 |  | STD2004 | 31.9893 | 10.0041 | 66.3398 | 73.8219 | 0 | 57.7319 | 0 | 57.1645 | 0 | 0.077539 | 18.8377 | 0 | 0 | 152.8844 | 0 | 0 | 468.851 |  | STD2004 | 9.3755 | 2.932 | 3.9135 | 0 | 0 | 16.9202 | 0 | 16.754 | 0 | 0.022725 | 5.521 | 0 | 0 | 21.0887 | 0 | 0 | 76.5277 |  | STD2004 | 0 | 0 | 0.52987 | 0.73822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0774 |  | STD2004 | 98.1523 | 30.6954 | 98.8851 | 80.6874 | 0 | 177.138 | 0 | 175.3973 | 0 | 0.23791 | 57.7994 | 0 | 0 | 309.234 | 0 | 0 | 1028.2267
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | -0.0022946 | 0.28664 | 0 | 0.3091 | 0 | 0.12196 | 0 | 0 | 0.014404 | 0 | 0 | 0 | 0 | 0 | 0.72981 |  | 2004-2007 | 0 | 0 | -0.1737 | 29.2487 | 0 | 9.9213 | 0 | 3.9148 | 0 | 0 | 0.46232 | 0 | 0 | 0 | 0 | 0 | 43.3734 |  | 2004-2007 | 0 | 0 | -0.0081299 | 0 | 0 | 2.9078 | 0 | 1.1474 | 0 | 0 | 0.1355 | 0 | 0 | 0 | 0 | 0 | 4.1825 |  | 2004-2007 | 0 | 0 | -0.0014596 | 0.29249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29103 |  | 2004-2007 | 0 | 0 | -0.24465 | 31.9688 | 0 | 30.4415 | 0 | 12.0117 | 0 | 0 | 1.4185 | 0 | 0 | 0 | 0 | 0 | 75.596
2007-2010 | 0.59408 | 0.13443 | 0.012358 | -0.027027 | 0 | 0.47423 | 0 | 0.87958 | 0 | 0 | -0.0021156 | 0 | 0 | 0.0021473 | 0 | 0 | 2.0677 |  | 2007-2010 | 19.0687 | 4.3149 | 0.43815 | -2.7578 | 0 | 15.2219 | 0 | 28.2325 | 0 | 0 | -0.067906 | 0 | 0 | 0.068924 | 0 | 0 | 64.5192 |  | 2007-2010 | 5.5887 | 1.2646 | 0.11068 | 0 | 0 | 4.4613 | 0 | 8.2745 | 0 | 0 | -0.019902 | 0 | 0 | 0.0202 | 0 | 0 | 19.7 |  | 2007-2010 | 0 | 0 | 0.00060521 | -0.027578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.026973 |  | 2007-2010 | 58.5081 | 13.2393 | 1.2248 | -3.0143 | 0 | 46.705 | 0 | 86.6255 | 0 | 0 | -0.20836 | 0 | 0 | 0.21148 | 0 | 0 | 203.2915
2010-2013 | 0.027344 | 0 | 0.0001731 | 0.0045454 | 0 | 0.04096 | 0 | 0.20251 | 0 | 0 | 0.12159 | 0 | 0 | 0.00085892 | 0 | 0 | 0.39798 |  | 2010-2013 | 0.87769 | 0 | 0.014764 | 0.46382 | 0 | 1.3147 | 0 | 6.5001 | 0 | 0 | 3.9027 | 0 | 0 | 0.02757 | 0 | 0 | 13.1014 |  | 2010-2013 | 0.25724 | 0 | 0.0003899 | 0 | 0 | 0.38532 | 0 | 1.9051 | 0 | 0 | 1.1438 | 0 | 0 | 0.0080802 | 0 | 0 | 3.6999 |  | 2010-2013 | 0 | 0 | 0.00013434 | 0.0046382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047725 |  | 2010-2013 | 2.693 | 0 | 0.018765 | 0.50695 | 0 | 4.034 | 0 | 19.9442 | 0 | 0 | 11.9747 | 0 | 0 | 0.084591 | 0 | 0 | 39.2562
2013-2016 | 0.081293 | 0.077197 | 0.00030305 | -0.0050832 | 0 | 0.018466 | 0 | 0.0054594 | 0 | 0 | 9.0093e-07 | 0 | 0 | 0 | 0 | 0 | 0.17764 |  | 2013-2016 | 2.6093 | 2.4779 | 0.030923 | -0.51869 | 0 | 0.59273 | 0 | 0.17524 | 0 | 0 | 2.8918e-05 | 0 | 0 | 0 | 0 | 0 | 5.3674 |  | 2013-2016 | 0.76475 | 0.72622 | 0 | 0 | 0 | 0.17372 | 0 | 0.051359 | 0 | 0 | 8.4754e-06 | 0 | 0 | 0 | 0 | 0 | 1.7161 |  | 2013-2016 | 0 | 0 | 0.00030923 | -0.0051869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0048777 |  | 2013-2016 | 8.0062 | 7.6028 | 0.033799 | -0.56693 | 0 | 1.8187 | 0 | 0.53767 | 0 | 0 | 8.8729e-05 | 0 | 0 | 0 | 0 | 0 | 17.4323
2016-2019 | 0.024156 | 0 | -9.3025e-05 | -0.0024409 | 0 | 0.038266 | 0 | 0.010398 | 0 | 0 | 0.15409 | 0 | 0 | 0 | 0 | 0 | 0.22438 |  | 2016-2019 | 0.77535 | 0 | -0.0071426 | -0.24907 | 0 | 1.2283 | 0 | 0.33376 | 0 | 0 | 4.946 | 0 | 0 | 0 | 0 | 0 | 7.0271 |  | 2016-2019 | 0.22724 | 0 | -0.00031604 | 0 | 0 | 0.35998 | 0 | 0.09782 | 0 | 0 | 1.4496 | 0 | 0 | 0 | 0 | 0 | 2.1343 |  | 2016-2019 | 0 | 0 | -6.0643e-05 | -0.0024907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0025513 |  | 2016-2019 | 2.379 | 0 | -0.0099368 | -0.27223 | 0 | 3.7687 | 0 | 1.0241 | 0 | 0 | 15.1756 | 0 | 0 | 0 | 0 | 0 | 22.0652
2004-2019 | 0.72687 | 0.21163 | 0.010446 | 0.25663 | 0 | 0.88102 | 0 | 1.2199 | 0 | 0 | 0.28797 | 0 | 0 | 0.0030062 | 0 | 0 | 3.5975 |  | 2004-2019 | 23.331 | 6.7927 | 0.30299 | 26.1869 | 0 | 28.2789 | 0 | 39.1564 | 0 | 0 | 9.2431 | 0 | 0 | 0.096493 | 0 | 0 | 133.3886 |  | 2004-2019 | 6.8379 | 1.9908 | 0.10262 | 0 | 0 | 8.2881 | 0 | 11.4761 | 0 | 0 | 2.709 | 0 | 0 | 0.028281 | 0 | 0 | 31.4328 |  | 2004-2019 | 0 | 0 | -0.00047148 | 0.26187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2614 |  | 2004-2019 | 71.5863 | 20.8421 | 1.0228 | 28.6223 | 0 | 86.7679 | 0 | 120.1431 | 0 | 0 | 28.3606 | 0 | 0 | 0.29607 | 0 | 0 | 357.6411
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.2453% | 39.62% |  | 17.19% |  | 6.848% |  | 0% | 2.454% |  |  | 0% |  |  | 7.176% |  | 2004-2007 | 0% | 0% | -0.2618% | 39.62% |  | 17.19% |  | 6.848% |  | 0% | 2.454% |  |  | 0% |  |  | 9.251% |  | 2004-2007 | 0% | 0% | -0.2077% |  |  | 17.19% |  | 6.848% |  | 0% | 2.454% |  |  | 0% |  |  | 5.465% |  | 2004-2007 |  |  | -0.2755% | 39.62% | [9 empty] | 0% |  |  | 14.01% |  | 2004-2007 | 0% | 0% | -0.2474% | 39.62% |  | 17.19% |  | 6.848% |  | 0% | 2.454% |  |  | 0% |  |  | 7.352%
2007-2010 | 59.61% | 43.13% | 1.318% | -6.187% |  | 31.84% |  | 53.02% |  | 0% | -0.3696% |  |  | 0.07076% |  |  | 21.9% |  | 2007-2010 | 59.61% | 43.13% | 0.6587% | -6.187% |  | 31.84% |  | 53.02% |  | 0% | -0.3696% |  |  | 0.04508% |  |  | 15.16% |  | 2007-2010 | 59.61% | 43.13% | 2.822% |  |  | 31.84% |  | 53.02% |  | 0% | -0.3696% |  |  | 0.09579% |  |  | 27.23% |  | 2007-2010 |  |  | 0.1139% | -6.187% | [9 empty] | 0% |  |  | -1.51% |  | 2007-2010 | 59.61% | 43.13% | 1.236% | -6.187% |  | 31.84% |  | 53.02% |  | 0% | -0.3696% |  |  | 0.06839% |  |  | 21.34%
2010-2013 | 6.793% | 0% | 0.01871% | 0.9799% |  | 4.034% |  | 25.98% |  | 0% | 21.16% |  |  | 0.02832% |  |  | 5.398% |  | 2010-2013 | 6.793% | 0% | 0.02234% | 0.9799% |  | 4.034% |  | 25.98% |  | 0% | 21.16% |  |  | 0.01804% |  |  | 3.63% |  | 2010-2013 | 6.793% | 0% | 0.01023% |  |  | 4.034% |  | 25.98% |  | 0% | 21.16% |  |  | 0.03835% |  |  | 7.028% |  | 2010-2013 |  |  | 0.02531% | 0.9799% | [9 empty] | 0% |  |  | 0.2632% |  | 2010-2013 | 6.793% | 0% | 0.01917% | 0.9799% |  | 4.034% |  | 25.98% |  | 0% | 21.16% |  |  | 0.02737% |  |  | 5.239%
2013-2016 | 21.67% | 43.55% | 0.03276% | -1.107% |  | 1.895% |  | 0.9463% |  | 0% | 0.0001989% |  |  | 0% |  |  | 2.547% |  | 2013-2016 | 21.67% | 43.55% | 0.04681% | -1.107% |  | 1.895% |  | 0.9463% |  | 0% | 0.0001989% |  |  | 0% |  |  | 1.543% |  | 2013-2016 | 21.67% | 43.55% | 0% |  |  | 1.895% |  | 0.9463% |  | 0% | 0.0001989% |  |  | 0% |  |  | 3.506% |  | 2013-2016 |  |  | 0.05828% | -1.107% | [9 empty] | 0% |  |  | -0.2697% |  | 2013-2016 | 21.67% | 43.55% | 0.03453% | -1.107% |  | 1.895% |  | 0.9463% |  | 0% | 0.0001989% |  |  | 0% |  |  | 2.455%
2016-2019 | 8.219% | 0% | -0.01006% | -0.5256% |  | 4.003% |  | 1.82% |  | 0% | 34.02% |  |  | 0% |  |  | 3.301% |  | 2016-2019 | 8.219% | 0% | -0.01082% | -0.5256% |  | 4.003% |  | 1.82% |  | 0% | 34.02% |  |  | 0% |  |  | 2.052% |  | 2016-2019 | 8.219% | 0% | -0.008294% |  |  | 4.003% |  | 1.82% |  | 0% | 34.02% |  |  | 0% |  |  | 4.519% |  | 2016-2019 |  |  | -0.01144% | -0.5256% | [9 empty] | 0% |  |  | -0.1407% |  | 2016-2019 | 8.219% | 0% | -0.01015% | -0.5256% |  | 4.003% |  | 1.82% |  | 0% | 34.02% |  |  | 0% |  |  | 3.186%
2004-2019 | 72.93% | 67.9% | 1.117% | 35.47% |  | 48.98% |  | 68.5% |  | 0% | 49.07% |  |  | 0.09906% |  |  | 35.37% |  | 2004-2019 | 72.93% | 67.9% | 0.4567% | 35.47% |  | 48.98% |  | 68.5% |  | 0% | 49.07% |  |  | 0.06312% |  |  | 28.45% |  | 2004-2019 | 72.93% | 67.9% | 2.622% |  |  | 48.98% |  | 68.5% |  | 0% | 49.07% |  |  | 0.1341% |  |  | 41.07% |  | 2004-2019 |  |  | -0.08898% | 35.47% | [9 empty] | 0% |  |  | 12.58% |  | 2004-2019 | 72.93% | 67.9% | 1.034% | 35.47% |  | 48.98% |  | 68.5% |  | 0% | 49.07% |  |  | 0.09574% |  |  | 34.78%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.27029 | 0.10006 | 0.7676 | 0 | 0 | 3.4818 | 0 | 0.88861 | 0 | 0.0024157 | 0.31351 | 0 | 0 | 3.0318 | 0 | 0 | 8.8561 | 0% | CZ 0A | 8.6758 | 3.2118 | 50.0349 | 0 | 0 | 111.7582 | 0 | 28.5224 | 0 | 0.077539 | 10.0629 | 0 | 0 | 152.7879 | 0 | 0 | 365.1314 | 0% | CZ 0A | 2.5427 | 0.94134 | 3.8053 | 0 | 0 | 32.7545 | 0 | 8.3594 | 0 | 0.022725 | 2.9493 | 0 | 0 | 21.0604 | 0 | 0 | 72.4356 | 0% | CZ 0A | 0 | 0 | 0.37051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1798 | 0% | CZ 0A | 26.6198 | 9.8549 | 80.3343 | 0 | 0 | 342.9065 | 0 | 87.5149 | 0 | 0.23791 | 30.8758 | 0 | 0 | 308.9379 | 0 | 0 | 887.282 | 0%
CZ 0B | 0.26959 | 0.10001 | 0.76598 | 5.0647e-05 | 0 | 2.9052 | 0 | 0.83739 | 0 | 0.0024157 | 0.31136 | 0 | 0 | 3.0318 | 0 | 0 | 8.2238 | 0% | CZ 0B | 8.6534 | 3.2101 | 49.866 | 0.005168 | 0 | 93.2505 | 0 | 26.8786 | 0 | 0.077539 | 9.994 | 0 | 0 | 152.7879 | 0 | 0 | 344.7231 | 0% | CZ 0B | 2.5362 | 0.94083 | 3.8058 | 0 | 0 | 27.3301 | 0 | 7.8777 | 0 | 0.022725 | 2.9291 | 0 | 0 | 21.0604 | 0 | 0 | 66.5028 | 0% | CZ 0B | 0 | 0 | 0.36881 | 5.168e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1782 | 0% | CZ 0B | 26.5511 | 9.8496 | 80.1532 | 0.0056487 | 0 | 286.1193 | 0 | 82.4712 | 0 | 0.23791 | 30.6643 | 0 | 0 | 308.9379 | 0 | 0 | 824.9902 | 0%
CZ 1A | 0.27018 | 0.10001 | 0.80129 | 0 | 0 | 2.1311 | 0 | 0.50349 | 0 | 0.0024157 | 0.30873 | 0 | 0 | 3.0318 | 0 | 0 | 7.149 | 3.201% | CZ 1A | 8.6723 | 3.2101 | 53.4613 | 0 | 0 | 68.4034 | 0 | 16.1609 | 0 | 0.077539 | 9.9095 | 0 | 0 | 152.7879 | 0 | 0 | 312.683 | 3.201% | CZ 1A | 2.5417 | 0.94083 | 3.8068 | 0 | 0 | 20.0479 | 0 | 4.7365 | 0 | 0.022725 | 2.9043 | 0 | 0 | 21.0604 | 0 | 0 | 56.0612 | 3.201% | CZ 1A | 0 | 0 | 0.40473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.214 | 3.201% | CZ 1A | 26.6092 | 9.8496 | 84.0896 | 0 | 0 | 209.8815 | 0 | 49.5863 | 0 | 0.23791 | 30.4053 | 0 | 0 | 308.9379 | 0 | 0 | 719.5973 | 3.201%
CZ 1B | 0.27056 | 0.09985 | 0.8021 | 0.018942 | 0 | 2.3436 | 0 | 0.78409 | 0 | 0.0024157 | 0.30857 | 0 | 0 | 3.0318 | 0 | 0 | 7.662 | 0% | CZ 1B | 8.6844 | 3.205 | 53.544 | 1.9328 | 0 | 75.2252 | 0 | 25.1675 | 0 | 0.077539 | 9.9044 | 0 | 0 | 152.7879 | 0 | 0 | 330.5286 | 0% | CZ 1B | 2.5453 | 0.93932 | 3.8068 | 0 | 0 | 22.0472 | 0 | 7.3762 | 0 | 0.022725 | 2.9028 | 0 | 0 | 21.0604 | 0 | 0 | 60.7007 | 0% | CZ 1B | 0 | 0 | 0.40555 | 0.019328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2342 | 0% | CZ 1B | 26.6462 | 9.8337 | 84.18 | 2.1126 | 0 | 230.8125 | 0 | 77.2212 | 0 | 0.23791 | 30.3894 | 0 | 0 | 308.9379 | 0 | 0 | 770.3715 | 0%
CZ 2A | 0.26874 | 0.099796 | 0.83915 | 0.047625 | 0 | 1.8651 | 0 | 0.68563 | 0 | 0.0024157 | 0.30701 | 0 | 0 | 3.0318 | 0 | 0 | 7.1473 | 18.21% | CZ 2A | 8.6258 | 3.2032 | 57.3166 | 4.8597 | 0 | 59.8655 | 0 | 22.0074 | 0 | 0.077539 | 9.8544 | 0 | 0 | 152.7879 | 0 | 0 | 318.598 | 18.21% | CZ 2A | 2.5281 | 0.93881 | 3.8078 | 0 | 0 | 17.5456 | 0 | 6.45 | 0 | 0.022725 | 2.8882 | 0 | 0 | 21.0604 | 0 | 0 | 55.2416 | 18.21% | CZ 2A | 0 | 0 | 0.44324 | 0.048597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3011 | 18.21% | CZ 2A | 26.4665 | 9.8284 | 88.3103 | 5.3116 | 0 | 183.6846 | 0 | 67.525 | 0 | 0.23791 | 30.2361 | 0 | 0 | 308.9379 | 0 | 0 | 720.5383 | 18.21%
CZ 2B | 0.26874 | 0.099903 | 0.8419 | 0.041277 | 0 | 1.2591 | 0 | 0.68542 | 0 | 0.0024157 | 0.30282 | 0 | 0 | 3.0318 | 0 | 0 | 6.5334 | 2.812% | CZ 2B | 8.6258 | 3.2067 | 57.5905 | 4.2119 | 0 | 40.4152 | 0 | 22.0005 | 0 | 0.077539 | 9.72 | 0 | 0 | 152.7879 | 0 | 0 | 298.6361 | 2.812% | CZ 2B | 2.5281 | 0.93982 | 3.8088 | 0 | 0 | 11.845 | 0 | 6.448 | 0 | 0.022725 | 2.8488 | 0 | 0 | 21.0604 | 0 | 0 | 49.5016 | 2.812% | CZ 2B | 0 | 0 | 0.44595 | 0.042119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2974 | 2.812% | CZ 2B | 26.4665 | 9.839 | 88.6165 | 4.6037 | 0 | 124.0055 | 0 | 67.5038 | 0 | 0.23791 | 29.8237 | 0 | 0 | 308.9379 | 0 | 0 | 660.0345 | 2.812%
CZ 3A | 0.26911 | 0.099903 | 0.90456 | 0.29117 | 0 | 1.0056 | 0 | 0.62889 | 0 | 0.0024157 | 0.30068 | 0 | 0 | 3.0318 | 0 | 0 | 6.5341 | 17.3% | CZ 3A | 8.6379 | 3.2067 | 63.9731 | 29.711 | 0 | 32.277 | 0 | 20.1861 | 0 | 0.077539 | 9.6511 | 0 | 0 | 152.7879 | 0 | 0 | 320.5082 | 17.3% | CZ 3A | 2.5316 | 0.93982 | 3.8103 | 0 | 0 | 9.4599 | 0 | 5.9162 | 0 | 0.022725 | 2.8286 | 0 | 0 | 21.0604 | 0 | 0 | 46.5695 | 17.3% | CZ 3A | 0 | 0 | 0.50972 | 0.29711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6161 | 17.3% | CZ 3A | 26.5035 | 9.839 | 95.6028 | 32.4741 | 0 | 99.0352 | 0 | 61.9367 | 0 | 0.23791 | 29.6122 | 0 | 0 | 308.9379 | 0 | 0 | 664.1793 | 17.3%
CZ 3B | 0.26986 | 0.099903 | 0.88797 | 0.14362 | 0 | 0.91416 | 0 | 0.66889 | 0 | 0.0024157 | 0.30009 | 0 | 0 | 3.0318 | 0 | 0 | 6.3187 | 8.647% | CZ 3B | 8.662 | 3.2067 | 62.2831 | 14.6548 | 0 | 29.3426 | 0 | 21.4698 | 0 | 0.077539 | 9.6321 | 0 | 0 | 152.7879 | 0 | 0 | 302.1165 | 8.647% | CZ 3B | 2.5387 | 0.93982 | 3.8098 | 0 | 0 | 8.5998 | 0 | 6.2924 | 0 | 0.022725 | 2.823 | 0 | 0 | 21.0604 | 0 | 0 | 46.0867 | 8.647% | CZ 3B | 0 | 0 | 0.49284 | 0.14655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4487 | 8.647% | CZ 3B | 26.5775 | 9.839 | 93.7523 | 16.0177 | 0 | 90.0315 | 0 | 65.8754 | 0 | 0.23791 | 29.5541 | 0 | 0 | 308.9379 | 0 | 0 | 640.8234 | 8.647%
CZ 3C | 0.27147 | 0.10023 | 0.91134 | 0.058041 | 0 | 0.37546 | 0 | 0.42495 | 0 | 0.0024157 | 0.30347 | 0 | 0 | 3.0318 | 0 | 0 | 5.4792 | 1.321% | CZ 3C | 8.7137 | 3.217 | 64.6759 | 5.9226 | 0 | 12.0513 | 0 | 13.64 | 0 | 0.077539 | 9.7407 | 0 | 0 | 152.7879 | 0 | 0 | 270.8266 | 1.321% | CZ 3C | 2.5538 | 0.94285 | 3.8088 | 0 | 0 | 3.532 | 0 | 3.9977 | 0 | 0.022725 | 2.8548 | 0 | 0 | 21.0604 | 0 | 0 | 38.7732 | 1.321% | CZ 3C | 0 | 0 | 0.5168 | 0.059226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3853 | 1.321% | CZ 3C | 26.7361 | 9.8707 | 96.3608 | 6.4734 | 0 | 36.9769 | 0 | 41.8515 | 0 | 0.23791 | 29.8871 | 0 | 0 | 308.9379 | 0 | 0 | 557.3325 | 1.321%
CZ 4A | 0.27104 | 0.10039 | 0.9561 | 0.61044 | 0 | 0.62889 | 0 | 0.44922 | 0 | 0.0024157 | 0.29579 | 0 | 0 | 3.0318 | 0 | 0 | 6.3461 | 16.82% | CZ 4A | 8.6999 | 3.2222 | 69.2169 | 62.2903 | 0 | 20.1861 | 0 | 14.4189 | 0 | 0.077539 | 9.4943 | 0 | 0 | 152.7879 | 0 | 0 | 340.3939 | 16.82% | CZ 4A | 2.5498 | 0.94437 | 3.8123 | 0 | 0 | 5.9162 | 0 | 4.2259 | 0 | 0.022725 | 2.7826 | 0 | 0 | 21.0604 | 0 | 0 | 41.3144 | 16.82% | CZ 4A | 0 | 0 | 0.56209 | 0.6229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9943 | 16.82% | CZ 4A | 26.6938 | 9.8866 | 101.3479 | 68.0833 | 0 | 61.9367 | 0 | 44.2412 | 0 | 0.23791 | 29.1311 | 0 | 0 | 308.9379 | 0 | 0 | 650.4964 | 16.82%
CZ 4B | 0.26911 | 0.099903 | 0.94147 | 0.30072 | 0 | 0.55975 | 0 | 0.64688 | 0 | 0.0024157 | 0.29601 | 0 | 0 | 3.0318 | 0 | 0 | 6.1481 | 0.7787% | CZ 4B | 8.6379 | 3.2067 | 67.7319 | 30.6861 | 0 | 17.9667 | 0 | 20.7633 | 0 | 0.077539 | 9.5011 | 0 | 0 | 152.7879 | 0 | 0 | 311.3591 | 0.7787% | CZ 4B | 2.5316 | 0.93982 | 3.8113 | 0 | 0 | 5.2657 | 0 | 6.0854 | 0 | 0.022725 | 2.7846 | 0 | 0 | 21.0604 | 0 | 0 | 42.5017 | 0.7787% | CZ 4B | 0 | 0 | 0.54728 | 0.30686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6634 | 0.7787% | CZ 4B | 26.5035 | 9.839 | 99.7181 | 33.5399 | 0 | 55.1271 | 0 | 63.7078 | 0 | 0.23791 | 29.1523 | 0 | 0 | 308.9379 | 0 | 0 | 626.7633 | 0.7787%
CZ 4C | 0.27147 | 0.10044 | 0.97156 | 0.4122 | 0 | 0.16738 | 0 | 0.41937 | 0 | 0.0024157 | 0.29493 | 0 | 0 | 3.0318 | 0 | 0 | 5.6716 | 2.174% | CZ 4C | 8.7137 | 3.2239 | 70.7949 | 42.0609 | 0 | 5.3726 | 0 | 13.4608 | 0 | 0.077539 | 9.4667 | 0 | 0 | 152.7879 | 0 | 0 | 305.9589 | 2.174% | CZ 4C | 2.5538 | 0.94487 | 3.8123 | 0 | 0 | 1.5746 | 0 | 3.9451 | 0 | 0.022725 | 2.7745 | 0 | 0 | 21.0604 | 0 | 0 | 36.6885 | 2.174% | CZ 4C | 0 | 0 | 0.57787 | 0.42061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8078 | 2.174% | CZ 4C | 26.7361 | 9.8919 | 103.0726 | 45.9726 | 0 | 16.4847 | 0 | 41.3017 | 0 | 0.23791 | 29.0465 | 0 | 0 | 308.9379 | 0 | 0 | 581.6819 | 2.174%
CZ 5A | 0.26976 | 0.10006 | 0.99941 | 0.96436 | 0 | 0.35694 | 0 | 0.44363 | 0 | 0.0024157 | 0.29311 | 0 | 0 | 3.0318 | 0 | 0 | 6.4615 | 20.06% | CZ 5A | 8.6586 | 3.2118 | 73.6287 | 98.4045 | 0 | 11.4569 | 0 | 14.2397 | 0 | 0.077539 | 9.4081 | 0 | 0 | 152.7879 | 0 | 0 | 371.8736 | 20.06% | CZ 5A | 2.5377 | 0.94134 | 3.8133 | 0 | 0 | 3.3578 | 0 | 4.1734 | 0 | 0.022725 | 2.7574 | 0 | 0 | 21.0604 | 0 | 0 | 38.6641 | 20.06% | CZ 5A | 0 | 0 | 0.60618 | 0.98405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3995 | 20.06% | CZ 5A | 26.5669 | 9.8549 | 106.1768 | 107.5561 | 0 | 35.1529 | 0 | 43.6914 | 0 | 0.23791 | 28.8668 | 0 | 0 | 308.9379 | 0 | 0 | 667.0416 | 20.06%
CZ 5B | 0.26997 | 0.10028 | 0.98718 | 0.61571 | 0 | 0.36612 | 0 | 0.65471 | 0 | 0.0024157 | 0.29316 | 0 | 0 | 3.0318 | 0 | 0 | 6.3214 | 4.626% | CZ 5B | 8.6654 | 3.2187 | 72.3849 | 62.8278 | 0 | 11.7515 | 0 | 21.0149 | 0 | 0.077539 | 9.4098 | 0 | 0 | 152.7879 | 0 | 0 | 342.1385 | 4.626% | CZ 5B | 2.5397 | 0.94336 | 3.8128 | 0 | 0 | 3.4442 | 0 | 6.1591 | 0 | 0.022725 | 2.7579 | 0 | 0 | 21.0604 | 0 | 0 | 40.7402 | 4.626% | CZ 5B | 0 | 0 | 0.59376 | 0.62828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0313 | 4.626% | CZ 5B | 26.5881 | 9.876 | 104.8139 | 68.6708 | 0 | 36.057 | 0 | 64.4797 | 0 | 0.23791 | 28.872 | 0 | 0 | 308.9379 | 0 | 0 | 648.5334 | 4.626%
CZ 5C | 0.27137 | 0.10039 | 0.99644 | 0.54509 | 0 | 0.072794 | 0 | 0.41191 | 0 | 0.0024157 | 0.29252 | 0 | 0 | 3.0318 | 0 | 0 | 5.7248 | 0.066% | CZ 5C | 8.7102 | 3.2222 | 73.322 | 55.6218 | 0 | 2.3365 | 0 | 13.2213 | 0 | 0.077539 | 9.3891 | 0 | 0 | 152.7879 | 0 | 0 | 318.6887 | 0.066% | CZ 5C | 2.5528 | 0.94437 | 3.8138 | 0 | 0 | 0.68479 | 0 | 3.8749 | 0 | 0.022725 | 2.7518 | 0 | 0 | 21.0604 | 0 | 0 | 35.7057 | 0.066% | CZ 5C | 0 | 0 | 0.60309 | 0.55622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9686 | 0.066% | CZ 5C | 26.7255 | 9.8866 | 105.845 | 60.7946 | 0 | 7.1691 | 0 | 40.5668 | 0 | 0.23791 | 28.8086 | 0 | 0 | 308.9379 | 0 | 0 | 588.9722 | 0.066%
CZ 6A | 0.27002 | 0.10023 | 1.0313 | 1.4093 | 0 | 0.38791 | 0 | 0.4658 | 0 | 0.0024157 | 0.29198 | 0 | 0 | 3.0318 | 0 | 0 | 6.9908 | 3.001% | CZ 6A | 8.6672 | 3.217 | 76.8811 | 143.8091 | 0 | 12.4511 | 0 | 14.9513 | 0 | 0.077539 | 9.3719 | 0 | 0 | 152.7879 | 0 | 0 | 422.2141 | 3.001% | CZ 6A | 2.5402 | 0.94285 | 3.8133 | 0 | 0 | 3.6492 | 0 | 4.382 | 0 | 0.022725 | 2.7468 | 0 | 0 | 21.0604 | 0 | 0 | 39.1575 | 3.001% | CZ 6A | 0 | 0 | 0.6387 | 1.4381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8861 | 3.001% | CZ 6A | 26.5934 | 9.8707 | 109.7317 | 157.1834 | 0 | 38.2035 | 0 | 45.8749 | 0 | 0.23791 | 28.7557 | 0 | 0 | 308.9379 | 0 | 0 | 725.3891 | 3.001%
CZ 6B | 0.26906 | 0.10006 | 1.0234 | 0.99869 | 0 | 0.25129 | 0 | 0.62809 | 0 | 0.0024157 | 0.2908 | 0 | 0 | 3.0318 | 0 | 0 | 6.5956 | 0.4557% | CZ 6B | 8.6362 | 3.2118 | 76.068 | 101.9067 | 0 | 8.0658 | 0 | 20.1602 | 0 | 0.077539 | 9.334 | 0 | 0 | 152.7879 | 0 | 0 | 380.2482 | 0.4557% | CZ 6B | 2.5311 | 0.94134 | 3.8138 | 0 | 0 | 2.364 | 0 | 5.9086 | 0 | 0.022725 | 2.7356 | 0 | 0 | 21.0604 | 0 | 0 | 39.3777 | 0.4557% | CZ 6B | 0 | 0 | 0.63055 | 1.0191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4589 | 0.4557% | CZ 6B | 26.4982 | 9.8549 | 108.8464 | 111.384 | 0 | 24.7482 | 0 | 61.8573 | 0 | 0.23791 | 28.6394 | 0 | 0 | 308.9379 | 0 | 0 | 681.0043 | 0.4557%
CZ 7 | 0.2697 | 0.10039 | 1.0694 | 1.8102 | 0 | 0.27416 | 0 | 0.4643 | 0 | 0.0024157 | 0.29026 | 0 | 0 | 3.0318 | 0 | 0 | 7.3126 | 0.4458% | CZ 7 | 8.6568 | 3.2222 | 80.7606 | 184.7158 | 0 | 8.7998 | 0 | 14.903 | 0 | 0.077539 | 9.3168 | 0 | 0 | 152.7879 | 0 | 0 | 463.2405 | 0.4458% | CZ 7 | 2.5372 | 0.94437 | 3.8143 | 0 | 0 | 2.5791 | 0 | 4.3678 | 0 | 0.022725 | 2.7306 | 0 | 0 | 21.0604 | 0 | 0 | 38.0566 | 0.4458% | CZ 7 | 0 | 0 | 0.67746 | 1.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3339 | 0.4458% | CZ 7 | 26.5617 | 9.8866 | 113.9787 | 201.8944 | 0 | 27.0005 | 0 | 45.7269 | 0 | 0.23791 | 28.5866 | 0 | 0 | 308.9379 | 0 | 0 | 762.8111 | 0.4458%
CZ 8 | 0.27604 | 0.1021 | 1.1205 | 2.5669 | 0 | 0.089328 | 0 | 0.4643 | 0 | 0.0024157 | 0.28758 | 0 | 0 | 3.0318 | 0 | 0 | 7.9411 | 0.08738% | CZ 8 | 8.8602 | 3.2773 | 85.9785 | 261.9314 | 0 | 2.8672 | 0 | 14.903 | 0 | 0.077539 | 9.2306 | 0 | 0 | 152.7879 | 0 | 0 | 539.9137 | 0.08738% | CZ 8 | 2.5968 | 0.96053 | 3.8148 | 0 | 0 | 0.84034 | 0 | 4.3678 | 0 | 0.022725 | 2.7053 | 0 | 0 | 21.0604 | 0 | 0 | 36.3688 | 0.08738% | CZ 8 | 0 | 0 | 0.72962 | 2.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.1582 | 0.08738% | CZ 8 | 27.1855 | 10.0558 | 119.6854 | 286.291 | 0 | 8.7975 | 0 | 45.7269 | 0 | 0.23791 | 28.3222 | 0 | 0 | 308.9379 | 0 | 0 | 835.2401 | 0.08738%
US Weighted | 0.26975 | 0.10005 | 0.92483 | 0.46682 | 0 | 0.9176 | 0 | 0.56104 | 0 | 0.0024157 | 0.29892 | 0 | 0 | 3.0318 | 0 | 0 | 6.5733 | 100% | US Weighted | 8.6582 | 3.2114 | 66.0368 | 47.635 | 0 | 29.4529 | 0 | 18.0081 | 0 | 0.077539 | 9.5945 | 0 | 0 | 152.7879 | 0 | 0 | 335.4624 | 100% | US Weighted | 2.5376 | 0.94119 | 3.8109 | 0 | 0 | 8.6322 | 0 | 5.2779 | 0 | 0.022725 | 2.812 | 0 | 0 | 21.0604 | 0 | 0 | 45.0949 | 100% | US Weighted | 0 | 0 | 0.53034 | 0.47635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.816 | 100% | US Weighted | 26.566 | 9.8534 | 97.8623 | 52.0651 | 0 | 90.3701 | 0 | 55.2542 | 0 | 0.23791 | 29.4388 | 0 | 0 | 308.9379 | 0 | 0 | 670.5855 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.2945 | 0.10006 | 0.76762 | 0 | 0 | 3.5902 | 0 | 0.90337 | 0 | 0.0024157 | 0.47885 | 0 | 0 | 3.0318 | 0 | 0 | 9.1688 | 0% | CZ 0A | 9.4529 | 3.2118 | 50.0366 | 0 | 0 | 115.2372 | 0 | 28.9962 | 0 | 0.077539 | 15.37 | 0 | 0 | 152.7879 | 0 | 0 | 375.1702 | 0% | CZ 0A | 2.7705 | 0.94134 | 3.8053 | 0 | 0 | 33.7741 | 0 | 8.4983 | 0 | 0.022725 | 4.5047 | 0 | 0 | 21.0604 | 0 | 0 | 75.3773 | 0% | CZ 0A | 0 | 0 | 0.37053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1798 | 0% | CZ 0A | 29.0042 | 9.8549 | 80.3362 | 0 | 0 | 353.5808 | 0 | 88.9688 | 0 | 0.23791 | 47.1596 | 0 | 0 | 308.9379 | 0 | 0 | 918.0804 | 0%
CZ 0B | 0.2938 | 0.10001 | 0.76598 | 3.3764e-05 | 0 | 2.992 | 0 | 0.84486 | 0 | 0.0024157 | 0.47482 | 0 | 0 | 3.0318 | 0 | 0 | 8.5058 | 0% | CZ 0B | 9.4305 | 3.2101 | 49.866 | 0.0034454 | 0 | 96.0367 | 0 | 27.1181 | 0 | 0.077539 | 15.2408 | 0 | 0 | 152.7879 | 0 | 0 | 353.7711 | 0% | CZ 0B | 2.7639 | 0.94083 | 3.8058 | 0 | 0 | 28.1467 | 0 | 7.9479 | 0 | 0.022725 | 4.4668 | 0 | 0 | 21.0604 | 0 | 0 | 69.1551 | 0% | CZ 0B | 0 | 0 | 0.36881 | 3.4454e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1781 | 0% | CZ 0B | 28.9355 | 9.8496 | 80.1532 | 0.0037658 | 0 | 294.6683 | 0 | 83.2061 | 0 | 0.23791 | 46.7631 | 0 | 0 | 308.9379 | 0 | 0 | 852.7554 | 0%
CZ 1A | 0.29386 | 0.10001 | 0.80129 | 0 | 0 | 2.2038 | 0 | 0.51594 | 0 | 0.0024157 | 0.46999 | 0 | 0 | 3.0318 | 0 | 0 | 7.4192 | 3.201% | CZ 1A | 9.4322 | 3.2101 | 53.4613 | 0 | 0 | 70.7382 | 0 | 16.5607 | 0 | 0.077539 | 15.0857 | 0 | 0 | 152.7879 | 0 | 0 | 321.3537 | 3.201% | CZ 1A | 2.7644 | 0.94083 | 3.8068 | 0 | 0 | 20.7322 | 0 | 4.8537 | 0 | 0.022725 | 4.4214 | 0 | 0 | 21.0604 | 0 | 0 | 58.6024 | 3.201% | CZ 1A | 0 | 0 | 0.40473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.214 | 3.201% | CZ 1A | 28.9408 | 9.8496 | 84.0896 | 0 | 0 | 217.0453 | 0 | 50.8129 | 0 | 0.23791 | 46.2873 | 0 | 0 | 308.9379 | 0 | 0 | 746.2012 | 3.201%
CZ 1B | 0.29466 | 0.09985 | 0.80208 | 0.018267 | 0 | 2.4287 | 0 | 0.79933 | 0 | 0.0024157 | 0.46994 | 0 | 0 | 3.0318 | 0 | 0 | 7.9471 | 0% | CZ 1B | 9.4581 | 3.205 | 53.5422 | 1.8639 | 0 | 77.9563 | 0 | 25.6569 | 0 | 0.077539 | 15.084 | 0 | 0 | 152.7879 | 0 | 0 | 339.6318 | 0% | CZ 1B | 2.772 | 0.93932 | 3.8068 | 0 | 0 | 22.8477 | 0 | 7.5196 | 0 | 0.022725 | 4.4209 | 0 | 0 | 21.0604 | 0 | 0 | 63.3894 | 0% | CZ 1B | 0 | 0 | 0.40554 | 0.018639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2335 | 0% | CZ 1B | 29.0201 | 9.8337 | 84.1781 | 2.0373 | 0 | 239.1923 | 0 | 78.7227 | 0 | 0.23791 | 46.282 | 0 | 0 | 308.9379 | 0 | 0 | 798.442 | 0%
CZ 2A | 0.29273 | 0.099796 | 0.83913 | 0.047608 | 0 | 1.9255 | 0 | 0.69879 | 0 | 0.0024157 | 0.46747 | 0 | 0 | 3.0318 | 0 | 0 | 7.4053 | 18.21% | CZ 2A | 9.396 | 3.2032 | 57.3149 | 4.858 | 0 | 61.8057 | 0 | 22.4295 | 0 | 0.077539 | 15.0047 | 0 | 0 | 152.7879 | 0 | 0 | 326.8775 | 18.21% | CZ 2A | 2.7538 | 0.93881 | 3.8078 | 0 | 0 | 18.1142 | 0 | 6.5737 | 0 | 0.022725 | 4.3976 | 0 | 0 | 21.0604 | 0 | 0 | 57.6691 | 18.21% | CZ 2A | 0 | 0 | 0.44323 | 0.04858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3011 | 18.21% | CZ 2A | 28.8298 | 9.8284 | 88.3084 | 5.3097 | 0 | 189.6377 | 0 | 68.8203 | 0 | 0.23791 | 46.0388 | 0 | 0 | 308.9379 | 0 | 0 | 745.9489 | 18.21%
CZ 2B | 0.29219 | 0.099903 | 0.8418 | 0.04126 | 0 | 1.2995 | 0 | 0.69428 | 0 | 0.0024157 | 0.45904 | 0 | 0 | 3.0318 | 0 | 0 | 6.7622 | 2.812% | CZ 2B | 9.3788 | 3.2067 | 57.5836 | 4.2102 | 0 | 41.711 | 0 | 22.2848 | 0 | 0.077539 | 14.7342 | 0 | 0 | 152.7879 | 0 | 0 | 305.9747 | 2.812% | CZ 2B | 2.7488 | 0.93982 | 3.8083 | 0 | 0 | 12.2248 | 0 | 6.5313 | 0 | 0.022725 | 4.3183 | 0 | 0 | 21.0604 | 0 | 0 | 51.6545 | 2.812% | CZ 2B | 0 | 0 | 0.4459 | 0.042102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2973 | 2.812% | CZ 2B | 28.7769 | 9.839 | 88.6055 | 4.6018 | 0 | 127.9813 | 0 | 68.3762 | 0 | 0.23791 | 45.2087 | 0 | 0 | 308.9379 | 0 | 0 | 682.5652 | 2.812%
CZ 3A | 0.29354 | 0.099903 | 0.90446 | 0.29054 | 0 | 1.0519 | 0 | 0.64022 | 0 | 0.0024157 | 0.45614 | 0 | 0 | 3.0318 | 0 | 0 | 6.7709 | 17.3% | CZ 3A | 9.4219 | 3.2067 | 63.9662 | 29.6473 | 0 | 33.7623 | 0 | 20.5496 | 0 | 0.077539 | 14.6411 | 0 | 0 | 152.7879 | 0 | 0 | 328.0605 | 17.3% | CZ 3A | 2.7614 | 0.93982 | 3.8098 | 0 | 0 | 9.8952 | 0 | 6.0228 | 0 | 0.022725 | 4.2911 | 0 | 0 | 21.0604 | 0 | 0 | 48.8032 | 17.3% | CZ 3A | 0 | 0 | 0.50967 | 0.29647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6154 | 17.3% | CZ 3A | 28.9091 | 9.839 | 95.5919 | 32.4045 | 0 | 103.5926 | 0 | 63.0522 | 0 | 0.23791 | 44.9232 | 0 | 0 | 308.9379 | 0 | 0 | 687.4882 | 17.3%
CZ 3B | 0.2937 | 0.099903 | 0.88793 | 0.13977 | 0 | 0.94895 | 0 | 0.67994 | 0 | 0.0024157 | 0.45426 | 0 | 0 | 3.0318 | 0 | 0 | 6.5387 | 8.647% | CZ 3B | 9.4271 | 3.2067 | 62.2797 | 14.262 | 0 | 30.4592 | 0 | 21.8247 | 0 | 0.077539 | 14.5808 | 0 | 0 | 152.7879 | 0 | 0 | 308.9056 | 8.647% | CZ 3B | 2.7629 | 0.93982 | 3.8098 | 0 | 0 | 8.9271 | 0 | 6.3965 | 0 | 0.022725 | 4.2734 | 0 | 0 | 21.0604 | 0 | 0 | 48.1926 | 8.647% | CZ 3B | 0 | 0 | 0.49281 | 0.14262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4447 | 8.647% | CZ 3B | 28.9249 | 9.839 | 93.7485 | 15.5884 | 0 | 93.4575 | 0 | 66.9645 | 0 | 0.23791 | 44.7382 | 0 | 0 | 308.9379 | 0 | 0 | 662.4369 | 8.647%
CZ 3C | 0.29552 | 0.10023 | 0.91126 | 0.055948 | 0 | 0.40793 | 0 | 0.43467 | 0 | 0.0024157 | 0.46146 | 0 | 0 | 3.0318 | 0 | 0 | 5.7013 | 1.321% | CZ 3C | 9.4856 | 3.217 | 64.6673 | 5.709 | 0 | 13.0938 | 0 | 13.9519 | 0 | 0.077539 | 14.8117 | 0 | 0 | 152.7879 | 0 | 0 | 277.8018 | 1.321% | CZ 3C | 2.7801 | 0.94285 | 3.8088 | 0 | 0 | 3.8376 | 0 | 4.0891 | 0 | 0.022725 | 4.3411 | 0 | 0 | 21.0604 | 0 | 0 | 40.8826 | 1.321% | CZ 3C | 0 | 0 | 0.51672 | 0.05709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3831 | 1.321% | CZ 3C | 29.1047 | 9.8707 | 96.3514 | 6.2399 | 0 | 40.1756 | 0 | 42.8085 | 0 | 0.23791 | 45.4466 | 0 | 0 | 308.9379 | 0 | 0 | 579.1732 | 1.321%
CZ 4A | 0.29552 | 0.10039 | 0.95596 | 0.6092 | 0 | 0.6574 | 0 | 0.4585 | 0 | 0.0024157 | 0.44771 | 0 | 0 | 3.0318 | 0 | 0 | 6.5589 | 16.82% | CZ 4A | 9.4856 | 3.2222 | 69.2066 | 62.1628 | 0 | 21.101 | 0 | 14.717 | 0 | 0.077539 | 14.3706 | 0 | 0 | 152.7879 | 0 | 0 | 347.1312 | 16.82% | CZ 4A | 2.7801 | 0.94437 | 3.8118 | 0 | 0 | 6.1844 | 0 | 4.3133 | 0 | 0.022725 | 4.2118 | 0 | 0 | 21.0604 | 0 | 0 | 43.3289 | 16.82% | CZ 4A | 0 | 0 | 0.56201 | 0.62163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9929 | 16.82% | CZ 4A | 29.1047 | 9.8866 | 101.3332 | 67.944 | 0 | 64.744 | 0 | 45.1559 | 0 | 0.23791 | 44.0932 | 0 | 0 | 308.9379 | 0 | 0 | 671.4373 | 16.82%
CZ 4B | 0.29262 | 0.099903 | 0.94139 | 0.28631 | 0 | 0.58772 | 0 | 0.65745 | 0 | 0.0024157 | 0.44755 | 0 | 0 | 3.0318 | 0 | 0 | 6.3472 | 0.7787% | CZ 4B | 9.3926 | 3.2067 | 67.7233 | 29.2149 | 0 | 18.8644 | 0 | 21.1027 | 0 | 0.077539 | 14.3654 | 0 | 0 | 152.7879 | 0 | 0 | 316.7356 | 0.7787% | CZ 4B | 2.7528 | 0.93982 | 3.8113 | 0 | 0 | 5.5289 | 0 | 6.1849 | 0 | 0.022725 | 4.2103 | 0 | 0 | 21.0604 | 0 | 0 | 44.5111 | 0.7787% | CZ 4B | 0 | 0 | 0.54719 | 0.29215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6486 | 0.7787% | CZ 4B | 28.8192 | 9.839 | 99.7086 | 31.9319 | 0 | 57.8816 | 0 | 64.7493 | 0 | 0.23791 | 44.0773 | 0 | 0 | 308.9379 | 0 | 0 | 646.1827 | 0.7787%
CZ 4C | 0.29638 | 0.10044 | 0.97146 | 0.40531 | 0 | 0.18048 | 0 | 0.4279 | 0 | 0.0024157 | 0.44653 | 0 | 0 | 3.0318 | 0 | 0 | 5.8628 | 2.174% | CZ 4C | 9.5132 | 3.2239 | 70.7845 | 41.358 | 0 | 5.793 | 0 | 13.7348 | 0 | 0.077539 | 14.3327 | 0 | 0 | 152.7879 | 0 | 0 | 311.6057 | 2.174% | CZ 4C | 2.7882 | 0.94487 | 3.8123 | 0 | 0 | 1.6978 | 0 | 4.0254 | 0 | 0.022725 | 4.2007 | 0 | 0 | 21.0604 | 0 | 0 | 38.5525 | 2.174% | CZ 4C | 0 | 0 | 0.57777 | 0.41358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8006 | 2.174% | CZ 4C | 29.1893 | 9.8919 | 103.0613 | 45.2043 | 0 | 17.7747 | 0 | 42.1423 | 0 | 0.23791 | 43.9769 | 0 | 0 | 308.9379 | 0 | 0 | 600.4166 | 2.174%
CZ 5A | 0.29397 | 0.10006 | 0.99927 | 0.96278 | 0 | 0.37819 | 0 | 0.45169 | 0 | 0.0024157 | 0.44288 | 0 | 0 | 3.0318 | 0 | 0 | 6.6631 | 20.06% | CZ 5A | 9.4357 | 3.2118 | 73.6183 | 98.2426 | 0 | 12.1392 | 0 | 14.4981 | 0 | 0.077539 | 14.2155 | 0 | 0 | 152.7879 | 0 | 0 | 378.2267 | 20.06% | CZ 5A | 2.7654 | 0.94134 | 3.8128 | 0 | 0 | 3.5578 | 0 | 4.2492 | 0 | 0.022725 | 4.1663 | 0 | 0 | 21.0604 | 0 | 0 | 40.5761 | 20.06% | CZ 5A | 0 | 0 | 0.60609 | 0.98243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3978 | 20.06% | CZ 5A | 28.9514 | 9.8549 | 106.1621 | 107.3791 | 0 | 37.2466 | 0 | 44.4844 | 0 | 0.23791 | 43.6174 | 0 | 0 | 308.9379 | 0 | 0 | 686.8716 | 20.06%
CZ 5B | 0.29375 | 0.10028 | 0.98703 | 0.59424 | 0 | 0.40573 | 0 | 0.66464 | 0 | 0.0024157 | 0.44261 | 0 | 0 | 3.0318 | 0 | 0 | 6.5225 | 4.626% | CZ 5B | 9.4288 | 3.2187 | 72.3728 | 60.6365 | 0 | 13.0232 | 0 | 21.3336 | 0 | 0.077539 | 14.2069 | 0 | 0 | 152.7879 | 0 | 0 | 347.086 | 4.626% | CZ 5B | 2.7634 | 0.94336 | 3.8123 | 0 | 0 | 3.8169 | 0 | 6.2525 | 0 | 0.022725 | 4.1638 | 0 | 0 | 21.0604 | 0 | 0 | 42.8355 | 4.626% | CZ 5B | 0 | 0 | 0.59365 | 0.60637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0093 | 4.626% | CZ 5B | 28.9302 | 9.876 | 104.7974 | 66.2757 | 0 | 39.9588 | 0 | 65.4578 | 0 | 0.23791 | 43.5909 | 0 | 0 | 308.9379 | 0 | 0 | 668.0626 | 4.626%
CZ 5C | 0.29601 | 0.10039 | 0.99627 | 0.53718 | 0 | 0.082671 | 0 | 0.41974 | 0 | 0.0024157 | 0.44245 | 0 | 0 | 3.0318 | 0 | 0 | 5.909 | 0.066% | CZ 5C | 9.5011 | 3.2222 | 73.3082 | 54.8139 | 0 | 2.6536 | 0 | 13.4729 | 0 | 0.077539 | 14.2018 | 0 | 0 | 152.7879 | 0 | 0 | 324.0391 | 0.066% | CZ 5C | 2.7846 | 0.94437 | 3.8133 | 0 | 0 | 0.77772 | 0 | 3.9487 | 0 | 0.022725 | 4.1623 | 0 | 0 | 21.0604 | 0 | 0 | 37.5142 | 0.066% | CZ 5C | 0 | 0 | 0.60297 | 0.54814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9604 | 0.066% | CZ 5C | 29.1523 | 9.8866 | 105.8266 | 59.9116 | 0 | 8.1419 | 0 | 41.3387 | 0 | 0.23791 | 43.5751 | 0 | 0 | 308.9379 | 0 | 0 | 607.0085 | 0.066%
CZ 6A | 0.29391 | 0.10023 | 1.0312 | 1.4057 | 0 | 0.41362 | 0 | 0.47552 | 0 | 0.0024157 | 0.44084 | 0 | 0 | 3.0318 | 0 | 0 | 7.1953 | 3.001% | CZ 6A | 9.4339 | 3.217 | 76.8725 | 143.4405 | 0 | 13.2764 | 0 | 15.2632 | 0 | 0.077539 | 14.1501 | 0 | 0 | 152.7879 | 0 | 0 | 428.519 | 3.001% | CZ 6A | 2.7649 | 0.94285 | 3.8133 | 0 | 0 | 3.8911 | 0 | 4.4734 | 0 | 0.022725 | 4.1471 | 0 | 0 | 21.0604 | 0 | 0 | 41.1159 | 3.001% | CZ 6A | 0 | 0 | 0.63861 | 1.4344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8823 | 3.001% | CZ 6A | 28.9461 | 9.8707 | 109.7223 | 156.7804 | 0 | 40.736 | 0 | 46.8318 | 0 | 0.23791 | 43.4165 | 0 | 0 | 308.9379 | 0 | 0 | 745.4796 | 3.001%
CZ 6B | 0.29257 | 0.10006 | 1.0232 | 0.98337 | 0 | 0.26632 | 0 | 0.63893 | 0 | 0.0024157 | 0.43832 | 0 | 0 | 3.0318 | 0 | 0 | 6.777 | 0.4557% | CZ 6B | 9.3909 | 3.2118 | 76.0576 | 100.3442 | 0 | 8.5483 | 0 | 20.5083 | 0 | 0.077539 | 14.0691 | 0 | 0 | 152.7879 | 0 | 0 | 384.9957 | 0.4557% | CZ 6B | 2.7523 | 0.94134 | 3.8133 | 0 | 0 | 2.5054 | 0 | 6.0106 | 0 | 0.022725 | 4.1234 | 0 | 0 | 21.0604 | 0 | 0 | 41.2295 | 0.4557% | CZ 6B | 0 | 0 | 0.63047 | 1.0034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4432 | 0.4557% | CZ 6B | 28.8139 | 9.8549 | 108.8317 | 109.6763 | 0 | 26.2286 | 0 | 62.9253 | 0 | 0.23791 | 43.168 | 0 | 0 | 308.9379 | 0 | 0 | 698.6744 | 0.4557%
CZ 7 | 0.29316 | 0.10039 | 1.0692 | 1.8076 | 0 | 0.2981 | 0 | 0.47579 | 0 | 0.0024157 | 0.43778 | 0 | 0 | 3.0318 | 0 | 0 | 7.5163 | 0.4458% | CZ 7 | 9.4098 | 3.2222 | 80.7502 | 184.4471 | 0 | 9.5683 | 0 | 15.2718 | 0 | 0.077539 | 14.0518 | 0 | 0 | 152.7879 | 0 | 0 | 469.5867 | 0.4458% | CZ 7 | 2.7579 | 0.94437 | 3.8138 | 0 | 0 | 2.8043 | 0 | 4.4759 | 0 | 0.022725 | 4.1184 | 0 | 0 | 21.0604 | 0 | 0 | 39.9978 | 0.4458% | CZ 7 | 0 | 0 | 0.67737 | 1.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3311 | 0.4458% | CZ 7 | 28.872 | 9.8866 | 113.964 | 201.6006 | 0 | 29.3584 | 0 | 46.8583 | 0 | 0.23791 | 43.1151 | 0 | 0 | 308.9379 | 0 | 0 | 782.831 | 0.4458%
CZ 8 | 0.30127 | 0.1021 | 1.1204 | 2.5788 | 0 | 0.09883 | 0 | 0.47557 | 0 | 0.0024157 | 0.43274 | 0 | 0 | 3.0318 | 0 | 0 | 8.144 | 0.08738% | CZ 8 | 9.67 | 3.2773 | 85.9682 | 263.1424 | 0 | 3.1722 | 0 | 15.2649 | 0 | 0.077539 | 13.8899 | 0 | 0 | 152.7879 | 0 | 0 | 547.2504 | 0.08738% | CZ 8 | 2.8341 | 0.96053 | 3.8148 | 0 | 0 | 0.92972 | 0 | 4.4739 | 0 | 0.022725 | 4.0709 | 0 | 0 | 21.0604 | 0 | 0 | 38.1672 | 0.08738% | CZ 8 | 0 | 0 | 0.72952 | 2.6314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.1702 | 0.08738% | CZ 8 | 29.6704 | 10.0558 | 119.6741 | 287.6147 | 0 | 9.7333 | 0 | 46.8371 | 0 | 0.23791 | 42.6181 | 0 | 0 | 308.9379 | 0 | 0 | 855.3793 | 0.08738%
US Weighted | 0.2939 | 0.10005 | 0.92474 | 0.46438 | 0 | 0.95587 | 0 | 0.57144 | 0 | 0.0024157 | 0.45301 | 0 | 0 | 3.0318 | 0 | 0 | 6.7976 | 100% | US Weighted | 9.4336 | 3.2114 | 66.0296 | 47.386 | 0 | 30.6812 | 0 | 18.3419 | 0 | 0.077539 | 14.5405 | 0 | 0 | 152.7879 | 0 | 0 | 342.4895 | 100% | US Weighted | 2.7648 | 0.94119 | 3.8106 | 0 | 0 | 8.9921 | 0 | 5.3757 | 0 | 0.022725 | 4.2616 | 0 | 0 | 21.0604 | 0 | 0 | 47.2292 | 100% | US Weighted | 0 | 0 | 0.53028 | 0.47386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8134 | 100% | US Weighted | 28.945 | 9.8534 | 97.8523 | 51.7928 | 0 | 94.1388 | 0 | 56.2782 | 0 | 0.23791 | 44.6144 | 0 | 0 | 308.9379 | 0 | 0 | 692.6507 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.3754 | 0.17742 | 0.76784 | 0 | 0 | 3.6393 | 0 | 0.9133 | 0 | 0.0024157 | 0.4788 | 0 | 0 | 3.0318 | 0 | 0 | 9.3863 | 0% | CZ 0A | 12.0496 | 5.6948 | 50.059 | 0 | 0 | 116.8121 | 0 | 29.315 | 0 | 0.077539 | 15.3683 | 0 | 0 | 152.7879 | 0 | 0 | 382.1642 | 0% | CZ 0A | 3.5315 | 1.6691 | 3.8053 | 0 | 0 | 34.2357 | 0 | 8.5917 | 0 | 0.022725 | 4.5042 | 0 | 0 | 21.0604 | 0 | 0 | 77.4206 | 0% | CZ 0A | 0 | 0 | 0.37075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1801 | 0% | CZ 0A | 36.9717 | 17.4734 | 80.3607 | 0 | 0 | 358.4131 | 0 | 89.9469 | 0 | 0.23791 | 47.1543 | 0 | 0 | 308.9379 | 0 | 0 | 939.4959 | 0%
CZ 0B | 0.3746 | 0.17737 | 0.7662 | 1.6882e-05 | 0 | 3.0375 | 0 | 0.85516 | 0 | 0.0024157 | 0.47477 | 0 | 0 | 3.0318 | 0 | 0 | 8.7198 | 0% | CZ 0B | 12.0238 | 5.6931 | 49.8884 | 0.0017227 | 0 | 97.4962 | 0 | 27.4489 | 0 | 0.077539 | 15.2391 | 0 | 0 | 152.7879 | 0 | 0 | 360.6566 | 0% | CZ 0B | 3.524 | 1.6686 | 3.8058 | 0 | 0 | 28.5745 | 0 | 8.0448 | 0 | 0.022725 | 4.4663 | 0 | 0 | 21.0604 | 0 | 0 | 71.1671 | 0% | CZ 0B | 0 | 0 | 0.36903 | 1.7227e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1783 | 0% | CZ 0B | 36.8924 | 17.4681 | 80.1777 | 0.0018829 | 0 | 299.1464 | 0 | 84.2212 | 0 | 0.23791 | 46.7578 | 0 | 0 | 308.9379 | 0 | 0 | 873.8412 | 0%
CZ 1A | 0.3754 | 0.17737 | 0.80153 | 0 | 0 | 2.2352 | 0 | 0.5197 | 0 | 0.0024157 | 0.46999 | 0 | 0 | 3.0318 | 0 | 0 | 7.6135 | 3.201% | CZ 1A | 12.0496 | 5.6931 | 53.4854 | 0 | 0 | 71.7462 | 0 | 16.6813 | 0 | 0.077539 | 15.0857 | 0 | 0 | 152.7879 | 0 | 0 | 327.6068 | 3.201% | CZ 1A | 3.5315 | 1.6686 | 3.8068 | 0 | 0 | 21.0276 | 0 | 4.889 | 0 | 0.022725 | 4.4214 | 0 | 0 | 21.0604 | 0 | 0 | 60.428 | 3.201% | CZ 1A | 0 | 0 | 0.40497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2143 | 3.201% | CZ 1A | 36.9717 | 17.4681 | 84.1159 | 0 | 0 | 220.1381 | 0 | 51.183 | 0 | 0.23791 | 46.2873 | 0 | 0 | 308.9379 | 0 | 0 | 765.3399 | 3.201%
CZ 1B | 0.37642 | 0.17715 | 0.80234 | 0.017 | 0 | 2.4559 | 0 | 0.80186 | 0 | 0.0024157 | 0.46983 | 0 | 0 | 3.0318 | 0 | 0 | 8.1347 | 0% | CZ 1B | 12.0823 | 5.6862 | 53.5681 | 1.7347 | 0 | 78.8282 | 0 | 25.7379 | 0 | 0.077539 | 15.0805 | 0 | 0 | 152.7879 | 0 | 0 | 345.5834 | 0% | CZ 1B | 3.5411 | 1.6665 | 3.8068 | 0 | 0 | 23.1032 | 0 | 7.5433 | 0 | 0.022725 | 4.4199 | 0 | 0 | 21.0604 | 0 | 0 | 65.164 | 0% | CZ 1B | 0 | 0 | 0.40579 | 0.017347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2324 | 0% | CZ 1B | 37.0721 | 17.4469 | 84.2063 | 1.8961 | 0 | 241.8675 | 0 | 78.9712 | 0 | 0.23791 | 46.2714 | 0 | 0 | 308.9379 | 0 | 0 | 816.9074 | 0%
CZ 2A | 0.37395 | 0.17705 | 0.83938 | 0.045886 | 0 | 1.9647 | 0 | 0.70496 | 0 | 0.0024157 | 0.46741 | 0 | 0 | 3.0318 | 0 | 0 | 7.6076 | 18.21% | CZ 2A | 12.0031 | 5.6828 | 57.3407 | 4.6822 | 0 | 63.0618 | 0 | 22.6277 | 0 | 0.077539 | 15.003 | 0 | 0 | 152.7879 | 0 | 0 | 333.2668 | 18.21% | CZ 2A | 3.5179 | 1.6655 | 3.8078 | 0 | 0 | 18.4824 | 0 | 6.6318 | 0 | 0.022725 | 4.3971 | 0 | 0 | 21.0604 | 0 | 0 | 59.5857 | 18.21% | CZ 2A | 0 | 0 | 0.44349 | 0.046822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2996 | 18.21% | CZ 2A | 36.8289 | 17.4364 | 88.3367 | 5.1177 | 0 | 193.4919 | 0 | 69.4283 | 0 | 0.23791 | 46.0335 | 0 | 0 | 308.9379 | 0 | 0 | 765.8491 | 18.21%
CZ 2B | 0.37331 | 0.17721 | 0.84207 | 0.039116 | 0 | 1.3158 | 0 | 0.70072 | 0 | 0.0024157 | 0.45904 | 0 | 0 | 3.0318 | 0 | 0 | 6.9415 | 2.812% | CZ 2B | 11.9824 | 5.6879 | 57.6112 | 3.9914 | 0 | 42.2348 | 0 | 22.4916 | 0 | 0.077539 | 14.7342 | 0 | 0 | 152.7879 | 0 | 0 | 311.599 | 2.812% | CZ 2B | 3.5118 | 1.667 | 3.8083 | 0 | 0 | 12.3783 | 0 | 6.5919 | 0 | 0.022725 | 4.3183 | 0 | 0 | 21.0604 | 0 | 0 | 53.3589 | 2.812% | CZ 2B | 0 | 0 | 0.44617 | 0.039914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2954 | 2.812% | CZ 2B | 36.7655 | 17.4522 | 88.6357 | 4.3626 | 0 | 129.5885 | 0 | 69.0106 | 0 | 0.23791 | 45.2087 | 0 | 0 | 308.9379 | 0 | 0 | 700.1997 | 2.812%
CZ 3A | 0.37497 | 0.17715 | 0.90473 | 0.28715 | 0 | 1.0672 | 0 | 0.64602 | 0 | 0.0024157 | 0.45609 | 0 | 0 | 3.0318 | 0 | 0 | 6.9476 | 17.3% | CZ 3A | 12.0358 | 5.6862 | 63.9937 | 29.301 | 0 | 34.2551 | 0 | 20.7357 | 0 | 0.077539 | 14.6394 | 0 | 0 | 152.7879 | 0 | 0 | 333.5125 | 17.3% | CZ 3A | 3.5275 | 1.6665 | 3.8098 | 0 | 0 | 10.0396 | 0 | 6.0773 | 0 | 0.022725 | 4.2906 | 0 | 0 | 21.0604 | 0 | 0 | 50.4945 | 17.3% | CZ 3A | 0 | 0 | 0.50995 | 0.29301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6123 | 17.3% | CZ 3A | 36.9294 | 17.4469 | 95.622 | 32.026 | 0 | 105.1046 | 0 | 63.6232 | 0 | 0.23791 | 44.918 | 0 | 0 | 308.9379 | 0 | 0 | 704.8459 | 17.3%
CZ 3B | 0.37524 | 0.17715 | 0.8882 | 0.13609 | 0 | 0.96162 | 0 | 0.68306 | 0 | 0.0024157 | 0.45432 | 0 | 0 | 3.0318 | 0 | 0 | 6.7099 | 8.647% | CZ 3B | 12.0444 | 5.6862 | 62.3072 | 13.8865 | 0 | 30.8658 | 0 | 21.9247 | 0 | 0.077539 | 14.5826 | 0 | 0 | 152.7879 | 0 | 0 | 314.1628 | 8.647% | CZ 3B | 3.53 | 1.6665 | 3.8098 | 0 | 0 | 9.0462 | 0 | 6.4258 | 0 | 0.022725 | 4.2739 | 0 | 0 | 21.0604 | 0 | 0 | 49.8354 | 8.647% | CZ 3B | 0 | 0 | 0.49308 | 0.13887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4412 | 8.647% | CZ 3B | 36.9558 | 17.4469 | 93.7786 | 15.1779 | 0 | 94.7052 | 0 | 67.2712 | 0 | 0.23791 | 44.7435 | 0 | 0 | 308.9379 | 0 | 0 | 679.255 | 8.647%
CZ 3C | 0.3775 | 0.17747 | 0.91154 | 0.05274 | 0 | 0.43504 | 0 | 0.43869 | 0 | 0.0024157 | 0.46146 | 0 | 0 | 3.0318 | 0 | 0 | 5.8887 | 1.321% | CZ 3C | 12.1168 | 5.6966 | 64.6966 | 5.3816 | 0 | 13.964 | 0 | 14.0811 | 0 | 0.077539 | 14.8117 | 0 | 0 | 152.7879 | 0 | 0 | 283.6138 | 1.321% | CZ 3C | 3.5512 | 1.6696 | 3.8088 | 0 | 0 | 4.0926 | 0 | 4.1269 | 0 | 0.022725 | 4.3411 | 0 | 0 | 21.0604 | 0 | 0 | 42.6734 | 1.321% | CZ 3C | 0 | 0 | 0.51701 | 0.053816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3801 | 1.321% | CZ 3C | 37.1779 | 17.4787 | 96.3834 | 5.8821 | 0 | 42.8455 | 0 | 43.205 | 0 | 0.23791 | 45.4466 | 0 | 0 | 308.9379 | 0 | 0 | 597.595 | 1.321%
CZ 4A | 0.37669 | 0.17753 | 0.9563 | 0.59988 | 0 | 0.6727 | 0 | 0.46425 | 0 | 0.0024157 | 0.44771 | 0 | 0 | 3.0318 | 0 | 0 | 6.7293 | 16.82% | CZ 4A | 12.091 | 5.6983 | 69.241 | 61.2119 | 0 | 21.5921 | 0 | 14.9013 | 0 | 0.077539 | 14.3706 | 0 | 0 | 152.7879 | 0 | 0 | 351.9716 | 16.82% | CZ 4A | 3.5437 | 1.6701 | 3.8118 | 0 | 0 | 6.3283 | 0 | 4.3673 | 0 | 0.022725 | 4.2118 | 0 | 0 | 21.0604 | 0 | 0 | 45.0161 | 16.82% | CZ 4A | 0 | 0 | 0.56235 | 0.61212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9838 | 16.82% | CZ 4A | 37.0985 | 17.484 | 101.3709 | 66.9046 | 0 | 66.2508 | 0 | 45.7216 | 0 | 0.23791 | 44.0932 | 0 | 0 | 308.9379 | 0 | 0 | 688.0994 | 16.82%
CZ 4B | 0.37342 | 0.1771 | 0.94168 | 0.27346 | 0 | 0.60221 | 0 | 0.66717 | 0 | 0.0024157 | 0.44777 | 0 | 0 | 3.0318 | 0 | 0 | 6.517 | 0.7787% | CZ 4B | 11.9858 | 5.6845 | 67.7526 | 27.9039 | 0 | 19.3297 | 0 | 21.4146 | 0 | 0.077539 | 14.3723 | 0 | 0 | 152.7879 | 0 | 0 | 321.309 | 0.7787% | CZ 4B | 3.5129 | 1.666 | 3.8113 | 0 | 0 | 5.6652 | 0 | 6.2763 | 0 | 0.022725 | 4.2123 | 0 | 0 | 21.0604 | 0 | 0 | 46.2271 | 0.7787% | CZ 4B | 0 | 0 | 0.54748 | 0.27904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6358 | 0.7787% | CZ 4B | 36.776 | 17.4417 | 99.7406 | 30.499 | 0 | 59.309 | 0 | 65.7063 | 0 | 0.23791 | 44.0985 | 0 | 0 | 308.9379 | 0 | 0 | 662.7469 | 0.7787%
CZ 4C | 0.3776 | 0.17747 | 0.97178 | 0.39363 | 0 | 0.18622 | 0 | 0.43413 | 0 | 0.0024157 | 0.44653 | 0 | 0 | 3.0318 | 0 | 0 | 6.0216 | 2.174% | CZ 4C | 12.1203 | 5.6966 | 70.8173 | 40.1659 | 0 | 5.9774 | 0 | 13.9347 | 0 | 0.077539 | 14.3327 | 0 | 0 | 152.7879 | 0 | 0 | 315.9102 | 2.174% | CZ 4C | 3.5522 | 1.6696 | 3.8123 | 0 | 0 | 1.7519 | 0 | 4.084 | 0 | 0.022725 | 4.2007 | 0 | 0 | 21.0604 | 0 | 0 | 40.1539 | 2.174% | CZ 4C | 0 | 0 | 0.5781 | 0.40166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7891 | 2.174% | CZ 4C | 37.1884 | 17.4787 | 103.0971 | 43.9014 | 0 | 18.3404 | 0 | 42.7556 | 0 | 0.23791 | 43.9769 | 0 | 0 | 308.9379 | 0 | 0 | 615.9143 | 2.174%
CZ 5A | 0.37513 | 0.17721 | 0.99963 | 0.9569 | 0 | 0.38984 | 0 | 0.45668 | 0 | 0.0024157 | 0.44288 | 0 | 0 | 3.0318 | 0 | 0 | 6.8325 | 20.06% | CZ 5A | 12.041 | 5.6879 | 73.6545 | 97.6431 | 0 | 12.5131 | 0 | 14.6584 | 0 | 0.077539 | 14.2155 | 0 | 0 | 152.7879 | 0 | 0 | 383.279 | 20.06% | CZ 5A | 3.529 | 1.667 | 3.8128 | 0 | 0 | 3.6674 | 0 | 4.2961 | 0 | 0.022725 | 4.1663 | 0 | 0 | 21.0604 | 0 | 0 | 42.2219 | 20.06% | CZ 5A | 0 | 0 | 0.60645 | 0.97643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3922 | 20.06% | CZ 5A | 36.9452 | 17.4522 | 106.2016 | 106.7239 | 0 | 38.3939 | 0 | 44.9761 | 0 | 0.23791 | 43.6174 | 0 | 0 | 308.9379 | 0 | 0 | 703.4861 | 20.06%
CZ 5B | 0.37497 | 0.17742 | 0.98737 | 0.58153 | 0 | 0.41416 | 0 | 0.67259 | 0 | 0.0024157 | 0.44283 | 0 | 0 | 3.0318 | 0 | 0 | 6.6851 | 4.626% | CZ 5B | 12.0358 | 5.6948 | 72.4073 | 59.3393 | 0 | 13.2937 | 0 | 21.5887 | 0 | 0.077539 | 14.2138 | 0 | 0 | 152.7879 | 0 | 0 | 351.4389 | 4.626% | CZ 5B | 3.5275 | 1.6691 | 3.8123 | 0 | 0 | 3.8962 | 0 | 6.3273 | 0 | 0.022725 | 4.1658 | 0 | 0 | 21.0604 | 0 | 0 | 44.4813 | 4.626% | CZ 5B | 0 | 0 | 0.594 | 0.59339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9967 | 4.626% | CZ 5B | 36.9294 | 17.4734 | 104.835 | 64.8579 | 0 | 40.7888 | 0 | 66.2402 | 0 | 0.23791 | 43.6121 | 0 | 0 | 308.9379 | 0 | 0 | 683.9126 | 4.626%
CZ 5C | 0.37766 | 0.17742 | 0.99662 | 0.52546 | 0 | 0.085355 | 0 | 0.42452 | 0 | 0.0024157 | 0.44245 | 0 | 0 | 3.0318 | 0 | 0 | 6.0637 | 0.066% | CZ 5C | 12.122 | 5.6948 | 73.3444 | 53.6183 | 0 | 2.7397 | 0 | 13.6262 | 0 | 0.077539 | 14.2018 | 0 | 0 | 152.7879 | 0 | 0 | 328.2127 | 0.066% | CZ 5C | 3.5527 | 1.6691 | 3.8133 | 0 | 0 | 0.80297 | 0 | 3.9936 | 0 | 0.022725 | 4.1623 | 0 | 0 | 21.0604 | 0 | 0 | 39.0772 | 0.066% | CZ 5C | 0 | 0 | 0.60333 | 0.53618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9488 | 0.066% | CZ 5C | 37.1937 | 17.4734 | 105.8661 | 58.6048 | 0 | 8.4063 | 0 | 41.8092 | 0 | 0.23791 | 43.5751 | 0 | 0 | 308.9379 | 0 | 0 | 622.1044 | 0.066%
CZ 6A | 0.37546 | 0.17731 | 1.0316 | 1.4039 | 0 | 0.41985 | 0 | 0.47912 | 0 | 0.0024157 | 0.44095 | 0 | 0 | 3.0318 | 0 | 0 | 7.3625 | 3.001% | CZ 6A | 12.0513 | 5.6914 | 76.9104 | 143.2596 | 0 | 13.4763 | 0 | 15.3786 | 0 | 0.077539 | 14.1535 | 0 | 0 | 152.7879 | 0 | 0 | 433.7865 | 3.001% | CZ 6A | 3.532 | 1.668 | 3.8133 | 0 | 0 | 3.9497 | 0 | 4.5072 | 0 | 0.022725 | 4.1482 | 0 | 0 | 21.0604 | 0 | 0 | 42.7017 | 3.001% | CZ 6A | 0 | 0 | 0.63899 | 1.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8809 | 3.001% | CZ 6A | 36.9769 | 17.4628 | 109.7637 | 156.5827 | 0 | 41.3493 | 0 | 47.1861 | 0 | 0.23791 | 43.427 | 0 | 0 | 308.9379 | 0 | 0 | 761.9243 | 3.001%
CZ 6B | 0.37379 | 0.1771 | 1.0236 | 0.97897 | 0 | 0.27018 | 0 | 0.6451 | 0 | 0.0024157 | 0.43843 | 0 | 0 | 3.0318 | 0 | 0 | 6.9414 | 0.4557% | CZ 6B | 11.9979 | 5.6845 | 76.0955 | 99.8946 | 0 | 8.6723 | 0 | 20.7064 | 0 | 0.077539 | 14.0725 | 0 | 0 | 152.7879 | 0 | 0 | 389.9893 | 0.4557% | CZ 6B | 3.5164 | 1.666 | 3.8133 | 0 | 0 | 2.5417 | 0 | 6.0687 | 0 | 0.022725 | 4.1244 | 0 | 0 | 21.0604 | 0 | 0 | 42.8138 | 0.4557% | CZ 6B | 0 | 0 | 0.63084 | 0.99895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4391 | 0.4557% | CZ 6B | 36.8131 | 17.4417 | 108.8731 | 109.1848 | 0 | 26.6092 | 0 | 63.5333 | 0 | 0.23791 | 43.1785 | 0 | 0 | 308.9379 | 0 | 0 | 714.8095 | 0.4557%
CZ 7 | 0.37454 | 0.17742 | 1.0696 | 1.8064 | 0 | 0.30304 | 0 | 0.48003 | 0 | 0.0024157 | 0.43778 | 0 | 0 | 3.0318 | 0 | 0 | 7.6831 | 0.4458% | CZ 7 | 12.022 | 5.6948 | 80.7898 | 184.3299 | 0 | 9.7269 | 0 | 15.4079 | 0 | 0.077539 | 14.0518 | 0 | 0 | 152.7879 | 0 | 0 | 474.8887 | 0.4458% | CZ 7 | 3.5235 | 1.6691 | 3.8138 | 0 | 0 | 2.8508 | 0 | 4.5158 | 0 | 0.022725 | 4.1184 | 0 | 0 | 21.0604 | 0 | 0 | 41.5745 | 0.4458% | CZ 7 | 0 | 0 | 0.67777 | 1.8433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3304 | 0.4458% | CZ 7 | 36.8871 | 17.4734 | 114.0074 | 201.4726 | 0 | 29.8448 | 0 | 47.2759 | 0 | 0.23791 | 43.1151 | 0 | 0 | 308.9379 | 0 | 0 | 799.2521 | 0.4458%
CZ 8 | 0.38431 | 0.17855 | 1.1209 | 2.5929 | 0 | 0.10039 | 0 | 0.48057 | 0 | 0.0024157 | 0.43274 | 0 | 0 | 3.0318 | 0 | 0 | 8.3246 | 0.08738% | CZ 8 | 12.3356 | 5.731 | 86.0113 | 264.586 | 0 | 3.2222 | 0 | 15.4251 | 0 | 0.077539 | 13.8899 | 0 | 0 | 152.7879 | 0 | 0 | 554.0666 | 0.08738% | CZ 8 | 3.6154 | 1.6797 | 3.8148 | 0 | 0 | 0.94437 | 0 | 4.5209 | 0 | 0.022725 | 4.0709 | 0 | 0 | 21.0604 | 0 | 0 | 39.7292 | 0.08738% | CZ 8 | 0 | 0 | 0.72995 | 2.6459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.1851 | 0.08738% | CZ 8 | 37.8493 | 17.5844 | 119.7212 | 289.1925 | 0 | 9.8866 | 0 | 47.3288 | 0 | 0.23791 | 42.6181 | 0 | 0 | 308.9379 | 0 | 0 | 873.3568 | 0.08738%
US Weighted | 0.37519 | 0.17725 | 0.92504 | 0.4593 | 0 | 0.97433 | 0 | 0.5769 | 0 | 0.0024157 | 0.45301 | 0 | 0 | 3.0318 | 0 | 0 | 6.9753 | 100% | US Weighted | 12.0429 | 5.6892 | 66.0606 | 46.8673 | 0 | 31.2739 | 0 | 18.5171 | 0 | 0.077539 | 14.5405 | 0 | 0 | 152.7879 | 0 | 0 | 347.857 | 100% | US Weighted | 3.5296 | 1.6674 | 3.8106 | 0 | 0 | 9.1659 | 0 | 5.4271 | 0 | 0.022725 | 4.2616 | 0 | 0 | 21.0604 | 0 | 0 | 48.9452 | 100% | US Weighted | 0 | 0 | 0.53059 | 0.46867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8086 | 100% | US Weighted | 36.9512 | 17.4561 | 97.8861 | 51.2259 | 0 | 95.9575 | 0 | 56.8159 | 0 | 0.23791 | 44.6145 | 0 | 0 | 308.9379 | 0 | 0 | 710.083 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.40278 | 0.17742 | 0.76818 | 0 | 0 | 3.8896 | 0 | 1.1393 | 0 | 0.0024157 | 0.59851 | 0 | 0 | 3.0327 | 0 | 0 | 10.0109 | 0% | CZ 0A | 12.9284 | 5.6948 | 50.09 | 0 | 0 | 124.8469 | 0 | 36.5692 | 0 | 0.077539 | 19.2108 | 0 | 0 | 152.8155 | 0 | 0 | 402.2331 | 0% | CZ 0A | 3.7891 | 1.6691 | 3.8058 | 0 | 0 | 36.5905 | 0 | 10.7178 | 0 | 0.022725 | 5.6304 | 0 | 0 | 21.0685 | 0 | 0 | 83.2939 | 0% | CZ 0A | 0 | 0 | 0.37105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1803 | 0% | CZ 0A | 39.668 | 17.4734 | 80.398 | 0 | 0 | 383.0662 | 0 | 112.205 | 0 | 0.23791 | 58.9442 | 0 | 0 | 309.0225 | 0 | 0 | 1001.0152 | 0%
CZ 0B | 0.4023 | 0.17737 | 0.76619 | 5.0647e-05 | 0 | 3.1358 | 0 | 1.0694 | 0 | 0.0024157 | 0.59695 | 0 | 0 | 3.0327 | 0 | 0 | 9.1831 | 0% | CZ 0B | 12.9129 | 5.6931 | 49.8867 | 0.005168 | 0 | 100.6529 | 0 | 34.3241 | 0 | 0.077539 | 19.1608 | 0 | 0 | 152.8155 | 0 | 0 | 375.5286 | 0% | CZ 0B | 3.7845 | 1.6686 | 3.8058 | 0 | 0 | 29.4997 | 0 | 10.0598 | 0 | 0.022725 | 5.6157 | 0 | 0 | 21.0685 | 0 | 0 | 75.5253 | 0% | CZ 0B | 0 | 0 | 0.36901 | 5.168e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1784 | 0% | CZ 0B | 39.6204 | 17.4681 | 80.1758 | 0.0056487 | 0 | 308.8321 | 0 | 105.3161 | 0 | 0.23791 | 58.7909 | 0 | 0 | 309.0225 | 0 | 0 | 919.4695 | 0%
CZ 1A | 0.40289 | 0.17737 | 0.8019 | 0 | 0 | 2.4265 | 0 | 0.8783 | 0 | 0.0024157 | 0.58986 | 0 | 0 | 3.0327 | 0 | 0 | 8.3119 | 3.201% | CZ 1A | 12.9318 | 5.6931 | 53.5164 | 0 | 0 | 77.8856 | 0 | 28.1916 | 0 | 0.077539 | 18.9334 | 0 | 0 | 152.8155 | 0 | 0 | 350.0449 | 3.201% | CZ 1A | 3.7901 | 1.6686 | 3.8078 | 0 | 0 | 22.827 | 0 | 8.2625 | 0 | 0.022725 | 5.5491 | 0 | 0 | 21.0685 | 0 | 0 | 66.9962 | 3.201% | CZ 1A | 0 | 0 | 0.40524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2145 | 3.201% | CZ 1A | 39.6786 | 17.4681 | 84.1566 | 0 | 0 | 238.9756 | 0 | 86.4998 | 0 | 0.23791 | 58.093 | 0 | 0 | 309.0225 | 0 | 0 | 834.1322 | 3.201%
CZ 1B | 0.4031 | 0.17715 | 0.8023 | 0.018554 | 0 | 2.5377 | 0 | 1.011 | 0 | 0.0024157 | 0.59228 | 0 | 0 | 3.0327 | 0 | 0 | 8.5772 | 0% | CZ 1B | 12.9387 | 5.6862 | 53.5646 | 1.8932 | 0 | 81.4559 | 0 | 32.4511 | 0 | 0.077539 | 19.0109 | 0 | 0 | 152.8155 | 0 | 0 | 359.8936 | 0% | CZ 1B | 3.7921 | 1.6665 | 3.8068 | 0 | 0 | 23.8734 | 0 | 9.5109 | 0 | 0.022725 | 5.5718 | 0 | 0 | 21.0685 | 0 | 0 | 69.3127 | 0% | CZ 1B | 0 | 0 | 0.40576 | 0.018932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.234 | 0% | CZ 1B | 39.6997 | 17.4469 | 84.2026 | 2.0693 | 0 | 249.9301 | 0 | 99.5692 | 0 | 0.23791 | 58.331 | 0 | 0 | 309.0225 | 0 | 0 | 860.5092 | 0%
CZ 2A | 0.40187 | 0.17705 | 0.83969 | 0.04754 | 0 | 2.0689 | 0 | 0.91797 | 0 | 0.0024157 | 0.58745 | 0 | 0 | 3.0327 | 0 | 0 | 8.0755 | 18.21% | CZ 2A | 12.8991 | 5.6828 | 57.3683 | 4.8511 | 0 | 66.4064 | 0 | 29.4649 | 0 | 0.077539 | 18.8558 | 0 | 0 | 152.8155 | 0 | 0 | 348.4214 | 18.21% | CZ 2A | 3.7805 | 1.6655 | 3.8083 | 0 | 0 | 19.4626 | 0 | 8.6357 | 0 | 0.022725 | 5.5263 | 0 | 0 | 21.0685 | 0 | 0 | 63.9702 | 18.21% | CZ 2A | 0 | 0 | 0.44374 | 0.048511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3016 | 18.21% | CZ 2A | 39.5781 | 17.4364 | 88.3702 | 5.3022 | 0 | 203.7539 | 0 | 90.4069 | 0 | 0.23791 | 57.8551 | 0 | 0 | 309.0225 | 0 | 0 | 811.9632 | 18.21%
CZ 2B | 0.40187 | 0.17721 | 0.84205 | 0.040467 | 0 | 1.3609 | 0 | 0.90299 | 0 | 0.0024157 | 0.5816 | 0 | 0 | 3.0327 | 0 | 0 | 7.3422 | 2.812% | CZ 2B | 12.8991 | 5.6879 | 57.6095 | 4.1293 | 0 | 43.6822 | 0 | 28.9842 | 0 | 0.077539 | 18.668 | 0 | 0 | 152.8155 | 0 | 0 | 324.5532 | 2.812% | CZ 2B | 3.7805 | 1.667 | 3.8083 | 0 | 0 | 12.8025 | 0 | 8.4948 | 0 | 0.022725 | 5.4713 | 0 | 0 | 21.0685 | 0 | 0 | 57.1157 | 2.812% | CZ 2B | 0 | 0 | 0.44616 | 0.041293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2967 | 2.812% | CZ 2B | 39.5781 | 17.4522 | 88.6338 | 4.5133 | 0 | 134.0295 | 0 | 88.9318 | 0 | 0.23791 | 57.2788 | 0 | 0 | 309.0225 | 0 | 0 | 739.6781 | 2.812%
CZ 3A | 0.40219 | 0.17715 | 0.90494 | 0.28622 | 0 | 1.1116 | 0 | 0.84872 | 0 | 0.0024157 | 0.5772 | 0 | 0 | 3.0327 | 0 | 0 | 7.3431 | 17.3% | CZ 3A | 12.9094 | 5.6862 | 64.011 | 29.2063 | 0 | 35.6801 | 0 | 27.2421 | 0 | 0.077539 | 18.5267 | 0 | 0 | 152.8155 | 0 | 0 | 346.1549 | 17.3% | CZ 3A | 3.7835 | 1.6665 | 3.8103 | 0 | 0 | 10.4572 | 0 | 7.9842 | 0 | 0.022725 | 5.4299 | 0 | 0 | 21.0685 | 0 | 0 | 54.223 | 17.3% | CZ 3A | 0 | 0 | 0.5101 | 0.29206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6115 | 17.3% | CZ 3A | 39.6099 | 17.4469 | 95.6442 | 31.9225 | 0 | 109.4769 | 0 | 83.5867 | 0 | 0.23791 | 56.8453 | 0 | 0 | 309.0225 | 0 | 0 | 743.7929 | 17.3%
CZ 3B | 0.40289 | 0.17715 | 0.8881 | 0.13246 | 0 | 0.99066 | 0 | 0.87529 | 0 | 0.0024157 | 0.57752 | 0 | 0 | 3.0327 | 0 | 0 | 7.0792 | 8.647% | CZ 3B | 12.9318 | 5.6862 | 62.3003 | 13.5161 | 0 | 31.798 | 0 | 28.0951 | 0 | 0.077539 | 18.5371 | 0 | 0 | 152.8155 | 0 | 0 | 325.7576 | 8.647% | CZ 3B | 3.7901 | 1.6665 | 3.8093 | 0 | 0 | 9.3195 | 0 | 8.2342 | 0 | 0.022725 | 5.4329 | 0 | 0 | 21.0685 | 0 | 0 | 53.3437 | 8.647% | CZ 3B | 0 | 0 | 0.49303 | 0.13516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.4375 | 8.647% | CZ 3B | 39.6786 | 17.4469 | 93.7677 | 14.7731 | 0 | 97.5654 | 0 | 86.2038 | 0 | 0.23791 | 56.877 | 0 | 0 | 309.0225 | 0 | 0 | 715.573 | 8.647%
CZ 3C | 0.40418 | 0.17747 | 0.9118 | 0.053263 | 0 | 0.44922 | 0 | 0.64118 | 0 | 0.0024157 | 0.58197 | 0 | 0 | 3.0327 | 0 | 0 | 6.2542 | 1.321% | CZ 3C | 12.9732 | 5.6966 | 64.719 | 5.435 | 0 | 14.4189 | 0 | 20.5806 | 0 | 0.077539 | 18.6801 | 0 | 0 | 152.8155 | 0 | 0 | 295.3963 | 1.321% | CZ 3C | 3.8022 | 1.6696 | 3.8093 | 0 | 0 | 4.2259 | 0 | 6.0318 | 0 | 0.022725 | 5.4748 | 0 | 0 | 21.0685 | 0 | 0 | 46.1049 | 1.321% | CZ 3C | 0 | 0 | 0.51722 | 0.05435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3809 | 1.321% | CZ 3C | 39.8055 | 17.4787 | 96.4113 | 5.9405 | 0 | 44.2412 | 0 | 63.1474 | 0 | 0.23791 | 57.3159 | 0 | 0 | 309.0225 | 0 | 0 | 633.6008 | 1.321%
CZ 4A | 0.40332 | 0.17753 | 0.95647 | 0.60626 | 0 | 0.68912 | 0 | 0.65444 | 0 | 0.0024157 | 0.56968 | 0 | 0 | 3.0327 | 0 | 0 | 7.0919 | 16.82% | CZ 4A | 12.9456 | 5.6983 | 69.2548 | 61.8631 | 0 | 22.1194 | 0 | 21.0063 | 0 | 0.077539 | 18.2855 | 0 | 0 | 152.8155 | 0 | 0 | 364.0659 | 16.82% | CZ 4A | 3.7941 | 1.6701 | 3.8123 | 0 | 0 | 6.4828 | 0 | 6.1566 | 0 | 0.022725 | 5.3592 | 0 | 0 | 21.0685 | 0 | 0 | 48.3664 | 16.82% | CZ 4A | 0 | 0 | 0.56247 | 0.61863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9904 | 16.82% | CZ 4A | 39.7209 | 17.484 | 101.3893 | 67.6163 | 0 | 67.8686 | 0 | 64.4532 | 0 | 0.23791 | 56.1051 | 0 | 0 | 309.0225 | 0 | 0 | 723.8979 | 16.82%
CZ 4B | 0.40192 | 0.1771 | 0.94183 | 0.27778 | 0 | 0.61944 | 0 | 0.86875 | 0 | 0.0024157 | 0.56936 | 0 | 0 | 3.0327 | 0 | 0 | 6.8913 | 0.7787% | CZ 4B | 12.9008 | 5.6845 | 67.7681 | 28.3449 | 0 | 19.8828 | 0 | 27.8848 | 0 | 0.077539 | 18.2751 | 0 | 0 | 152.8155 | 0 | 0 | 333.6342 | 0.7787% | CZ 4B | 3.781 | 1.666 | 3.8113 | 0 | 0 | 5.8273 | 0 | 8.1726 | 0 | 0.022725 | 5.3561 | 0 | 0 | 21.0685 | 0 | 0 | 49.7056 | 0.7787% | CZ 4B | 0 | 0 | 0.54764 | 0.28345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.6404 | 0.7787% | CZ 4B | 39.5834 | 17.4417 | 99.7576 | 30.981 | 0 | 61.0061 | 0 | 85.5588 | 0 | 0.23791 | 56.0734 | 0 | 0 | 309.0225 | 0 | 0 | 699.6624 | 0.7787%
CZ 4C | 0.40369 | 0.17747 | 0.9719 | 0.40185 | 0 | 0.18912 | 0 | 0.62701 | 0 | 0.0024157 | 0.56871 | 0 | 0 | 3.0327 | 0 | 0 | 6.3749 | 2.174% | CZ 4C | 12.9577 | 5.6966 | 70.8293 | 41.0049 | 0 | 6.0705 | 0 | 20.1258 | 0 | 0.077539 | 18.2545 | 0 | 0 | 152.8155 | 0 | 0 | 327.8321 | 2.174% | CZ 4C | 3.7977 | 1.6696 | 3.8123 | 0 | 0 | 1.7792 | 0 | 5.8985 | 0 | 0.022725 | 5.3501 | 0 | 0 | 21.0685 | 0 | 0 | 43.3986 | 2.174% | CZ 4C | 0 | 0 | 0.57822 | 0.41005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7976 | 2.174% | CZ 4C | 39.7579 | 17.4787 | 103.1103 | 44.8183 | 0 | 18.6259 | 0 | 61.7516 | 0 | 0.23791 | 56.01 | 0 | 0 | 309.0225 | 0 | 0 | 650.8131 | 2.174%
CZ 5A | 0.4024 | 0.17721 | 0.99978 | 0.96754 | 0 | 0.3928 | 0 | 0.64355 | 0 | 0.0024157 | 0.56517 | 0 | 0 | 3.0327 | 0 | 0 | 7.1836 | 20.06% | CZ 5A | 12.9163 | 5.6879 | 73.6666 | 98.7284 | 0 | 12.6079 | 0 | 20.6565 | 0 | 0.077539 | 18.1407 | 0 | 0 | 152.8155 | 0 | 0 | 395.2973 | 20.06% | CZ 5A | 3.7856 | 1.667 | 3.8133 | 0 | 0 | 3.6952 | 0 | 6.0541 | 0 | 0.022725 | 5.3167 | 0 | 0 | 21.0685 | 0 | 0 | 45.4232 | 20.06% | CZ 5A | 0 | 0 | 0.60655 | 0.98728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4031 | 20.06% | CZ 5A | 39.631 | 17.4522 | 106.2182 | 107.9101 | 0 | 38.6846 | 0 | 63.38 | 0 | 0.23791 | 55.661 | 0 | 0 | 309.0225 | 0 | 0 | 738.1976 | 20.06%
CZ 5B | 0.40273 | 0.17742 | 0.98752 | 0.59365 | 0 | 0.41921 | 0 | 0.86762 | 0 | 0.0024157 | 0.56485 | 0 | 0 | 3.0327 | 0 | 0 | 7.0481 | 4.626% | CZ 5B | 12.9267 | 5.6948 | 72.4193 | 60.5762 | 0 | 13.4557 | 0 | 27.8487 | 0 | 0.077539 | 18.1304 | 0 | 0 | 152.8155 | 0 | 0 | 363.9448 | 4.626% | CZ 5B | 3.7886 | 1.6691 | 3.8128 | 0 | 0 | 3.9436 | 0 | 8.162 | 0 | 0.022725 | 5.3137 | 0 | 0 | 21.0685 | 0 | 0 | 47.781 | 4.626% | CZ 5B | 0 | 0 | 0.5941 | 0.60576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0092 | 4.626% | CZ 5B | 39.6627 | 17.4734 | 104.8516 | 66.2098 | 0 | 41.2858 | 0 | 85.4477 | 0 | 0.23791 | 55.6293 | 0 | 0 | 309.0225 | 0 | 0 | 719.8208 | 4.626%
CZ 5C | 0.40375 | 0.17742 | 0.99705 | 0.57386 | 0 | 0.059749 | 0 | 0.75236 | 0 | 0.0024157 | 0.56259 | 0 | 0 | 3.0327 | 0 | 0 | 6.5619 | 0.066% | CZ 5C | 12.9594 | 5.6948 | 73.3806 | 58.5573 | 0 | 1.9178 | 0 | 24.1492 | 0 | 0.077539 | 18.058 | 0 | 0 | 152.8155 | 0 | 0 | 347.6101 | 0.066% | CZ 5C | 3.7982 | 1.6691 | 3.8143 | 0 | 0 | 0.56208 | 0 | 7.0777 | 0 | 0.022725 | 5.2925 | 0 | 0 | 21.0685 | 0 | 0 | 43.3051 | 0.066% | CZ 5C | 0 | 0 | 0.60366 | 0.58557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9985 | 0.066% | CZ 5C | 39.7632 | 17.4734 | 105.9125 | 64.0031 | 0 | 5.8844 | 0 | 74.0966 | 0 | 0.23791 | 55.4073 | 0 | 0 | 309.0225 | 0 | 0 | 671.8008 | 0.066%
CZ 6A | 0.40267 | 0.17731 | 1.0317 | 1.4185 | 0 | 0.43274 | 0 | 0.66921 | 0 | 0.0024157 | 0.56335 | 0 | 0 | 3.0327 | 0 | 0 | 7.7306 | 3.001% | CZ 6A | 12.9249 | 5.6914 | 76.9207 | 144.7497 | 0 | 13.8899 | 0 | 21.4801 | 0 | 0.077539 | 18.0822 | 0 | 0 | 152.8155 | 0 | 0 | 446.6319 | 3.001% | CZ 6A | 3.7881 | 1.668 | 3.8133 | 0 | 0 | 4.0709 | 0 | 6.2955 | 0 | 0.022725 | 5.2996 | 0 | 0 | 21.0685 | 0 | 0 | 46.0266 | 3.001% | CZ 6A | 0 | 0 | 0.6391 | 1.4475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8959 | 3.001% | CZ 6A | 39.6574 | 17.4628 | 109.775 | 158.2114 | 0 | 42.6181 | 0 | 65.9072 | 0 | 0.23791 | 55.4813 | 0 | 0 | 309.0225 | 0 | 0 | 798.3736 | 3.001%
CZ 6B | 0.40192 | 0.1771 | 1.0237 | 0.9881 | 0 | 0.27872 | 0 | 0.84174 | 0 | 0.0024157 | 0.56082 | 0 | 0 | 3.0327 | 0 | 0 | 7.3072 | 0.4557% | CZ 6B | 12.9008 | 5.6845 | 76.1059 | 100.8266 | 0 | 8.9463 | 0 | 27.0181 | 0 | 0.077539 | 18.0012 | 0 | 0 | 152.8155 | 0 | 0 | 402.3764 | 0.4557% | CZ 6B | 3.781 | 1.666 | 3.8138 | 0 | 0 | 2.622 | 0 | 7.9186 | 0 | 0.022725 | 5.2758 | 0 | 0 | 21.0685 | 0 | 0 | 46.1685 | 0.4557% | CZ 6B | 0 | 0 | 0.63093 | 1.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4485 | 0.4557% | CZ 6B | 39.5834 | 17.4417 | 108.8878 | 110.2035 | 0 | 27.4499 | 0 | 82.8994 | 0 | 0.23791 | 55.2328 | 0 | 0 | 309.0225 | 0 | 0 | 750.9588 | 0.4557%
CZ 7 | 0.40219 | 0.17742 | 1.0698 | 1.8325 | 0 | 0.31206 | 0 | 0.67028 | 0 | 0.0024157 | 0.56034 | 0 | 0 | 3.0327 | 0 | 0 | 8.0597 | 0.4458% | CZ 7 | 12.9094 | 5.6948 | 80.8002 | 186.9897 | 0 | 10.0164 | 0 | 21.5146 | 0 | 0.077539 | 17.9857 | 0 | 0 | 152.8155 | 0 | 0 | 488.8038 | 0.4458% | CZ 7 | 3.7835 | 1.6691 | 3.8143 | 0 | 0 | 2.9356 | 0 | 6.3056 | 0 | 0.022725 | 5.2713 | 0 | 0 | 21.0685 | 0 | 0 | 44.8707 | 0.4458% | CZ 7 | 0 | 0 | 0.67786 | 1.8699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3571 | 0.4458% | CZ 7 | 39.6099 | 17.4734 | 114.0221 | 204.3798 | 0 | 30.7331 | 0 | 66.0129 | 0 | 0.23791 | 55.1852 | 0 | 0 | 309.0225 | 0 | 0 | 836.6767 | 0.4458%
CZ 8 | 0.40756 | 0.17855 | 1.1211 | 2.6679 | 0 | 0.083369 | 0 | 0.79112 | 0 | 0.0024157 | 0.55459 | 0 | 0 | 3.0327 | 0 | 0 | 8.8393 | 0.08738% | CZ 8 | 13.0817 | 5.731 | 86.0302 | 272.2313 | 0 | 2.676 | 0 | 25.3933 | 0 | 0.077539 | 17.8013 | 0 | 0 | 152.8155 | 0 | 0 | 575.8378 | 0.08738% | CZ 8 | 3.834 | 1.6797 | 3.8154 | 0 | 0 | 0.78428 | 0 | 7.4423 | 0 | 0.022725 | 5.2173 | 0 | 0 | 21.0685 | 0 | 0 | 43.8642 | 0.08738% | CZ 8 | 0 | 0 | 0.73012 | 2.7223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.2617 | 0.08738% | CZ 8 | 40.1385 | 17.5844 | 119.7453 | 297.5488 | 0 | 8.2106 | 0 | 77.9138 | 0 | 0.23791 | 54.6195 | 0 | 0 | 309.0225 | 0 | 0 | 925.0214 | 0.08738%
US Weighted | 0.40254 | 0.17725 | 0.92521 | 0.46384 | 0 | 1.0153 | 0 | 0.77941 | 0 | 0.0024157 | 0.57459 | 0 | 0 | 3.0327 | 0 | 0 | 7.3732 | 100% | US Weighted | 12.9206 | 5.6892 | 66.0753 | 47.3311 | 0 | 32.5887 | 0 | 25.0172 | 0 | 0.077539 | 18.4432 | 0 | 0 | 152.8155 | 0 | 0 | 360.9584 | 100% | US Weighted | 3.7868 | 1.6674 | 3.8109 | 0 | 0 | 9.5512 | 0 | 7.3321 | 0 | 0.022725 | 5.4054 | 0 | 0 | 21.0685 | 0 | 0 | 52.6451 | 100% | US Weighted | 0 | 0 | 0.53072 | 0.47331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8133 | 100% | US Weighted | 39.6442 | 17.4561 | 97.9049 | 51.7329 | 0 | 99.9914 | 0 | 76.7601 | 0 | 0.23791 | 56.5892 | 0 | 0 | 309.0225 | 0 | 0 | 749.3391 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.99662 | 0.31216 | 0.77913 | 0 | 0 | 4.9858 | 0 | 1.7719 | 0 | 0.0024157 | 0.60044 | 0 | 0 | 3.0348 | 0 | 0 | 12.4833 | 0% | CZ 0A | 31.9893 | 10.0198 | 50.445 | 0 | 0 | 160.0325 | 0 | 56.8742 | 0 | 0.077539 | 19.2728 | 0 | 0 | 152.8844 | 0 | 0 | 481.5954 | 0% | CZ 0A | 9.3755 | 2.9366 | 3.9083 | 0 | 0 | 46.9028 | 0 | 16.6689 | 0 | 0.022725 | 5.6485 | 0 | 0 | 21.0887 | 0 | 0 | 106.5521 | 0% | CZ 0A | 0 | 0 | 0.3711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1804 | 0% | CZ 0A | 98.1523 | 30.7436 | 81.4769 | 0 | 0 | 491.0257 | 0 | 174.5065 | 0 | 0.23791 | 59.1346 | 0 | 0 | 309.234 | 0 | 0 | 1244.5114 | 0%
CZ 0B | 0.99662 | 0.31222 | 0.77732 | 0 | 0 | 4.1482 | 0 | 1.9059 | 0 | 0.0024157 | 0.5977 | 0 | 0 | 3.0348 | 0 | 0 | 11.7752 | 0% | CZ 0B | 31.9893 | 10.0215 | 50.2572 | 0 | 0 | 133.1487 | 0 | 61.175 | 0 | 0.077539 | 19.1849 | 0 | 0 | 152.8844 | 0 | 0 | 458.7386 | 0% | CZ 0B | 9.3755 | 2.9371 | 3.9088 | 0 | 0 | 39.0237 | 0 | 17.9294 | 0 | 0.022725 | 5.6228 | 0 | 0 | 21.0887 | 0 | 0 | 99.9087 | 0% | CZ 0B | 0 | 0 | 0.3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1785 | 0% | CZ 0B | 98.1523 | 30.7489 | 81.275 | 0 | 0 | 408.5387 | 0 | 187.7027 | 0 | 0.23791 | 58.8649 | 0 | 0 | 309.234 | 0 | 0 | 1174.7545 | 0%
CZ 1A | 0.99662 | 0.31227 | 0.81341 | 0 | 0 | 3.3756 | 0 | 1.6617 | 0 | 0.0024157 | 0.59008 | 0 | 0 | 3.0348 | 0 | 0 | 10.787 | 3.201% | CZ 1A | 31.9893 | 10.0232 | 53.9058 | 0 | 0 | 108.3499 | 0 | 53.3384 | 0 | 0.077539 | 18.9403 | 0 | 0 | 152.8844 | 0 | 0 | 429.5089 | 3.201% | CZ 1A | 9.3755 | 2.9376 | 3.9133 | 0 | 0 | 31.7556 | 0 | 15.6326 | 0 | 0.022725 | 5.5511 | 0 | 0 | 21.0887 | 0 | 0 | 90.2772 | 3.201% | CZ 1A | 0 | 0 | 0.40554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2148 | 3.201% | CZ 1A | 98.1523 | 30.7542 | 85.2936 | 0 | 0 | 332.4489 | 0 | 163.6576 | 0 | 0.23791 | 58.1142 | 0 | 0 | 309.234 | 0 | 0 | 1077.8927 | 3.201%
CZ 1B | 0.99662 | 0.31184 | 0.8137 | 0.0066854 | 0 | 3.4212 | 0 | 1.8765 | 0 | 0.0024157 | 0.59244 | 0 | 0 | 3.0348 | 0 | 0 | 11.0563 | 0% | CZ 1B | 31.9893 | 10.0095 | 53.9506 | 0.68218 | 0 | 109.8146 | 0 | 60.2308 | 0 | 0.077539 | 19.0161 | 0 | 0 | 152.8844 | 0 | 0 | 438.6549 | 0% | CZ 1B | 9.3755 | 2.9336 | 3.9113 | 0 | 0 | 32.1848 | 0 | 17.6526 | 0 | 0.022725 | 5.5733 | 0 | 0 | 21.0887 | 0 | 0 | 92.7426 | 0% | CZ 1B | 0 | 0 | 0.40605 | 0.0068218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2222 | 0% | CZ 1B | 98.1523 | 30.7119 | 85.329 | 0.74562 | 0 | 336.9428 | 0 | 184.8054 | 0 | 0.23791 | 58.3468 | 0 | 0 | 309.234 | 0 | 0 | 1104.5057 | 0%
CZ 2A | 0.99662 | 0.31173 | 0.85149 | 0.030962 | 0 | 2.8775 | 0 | 1.7011 | 0 | 0.0024157 | 0.58659 | 0 | 0 | 3.0348 | 0 | 0 | 10.3934 | 18.21% | CZ 2A | 31.9893 | 10.006 | 57.7767 | 3.1594 | 0 | 92.3631 | 0 | 54.6032 | 0 | 0.077539 | 18.8283 | 0 | 0 | 152.8844 | 0 | 0 | 421.6878 | 18.21% | CZ 2A | 9.3755 | 2.9326 | 3.9153 | 0 | 0 | 27.0701 | 0 | 16.0033 | 0 | 0.022725 | 5.5182 | 0 | 0 | 21.0887 | 0 | 0 | 85.9265 | 18.21% | CZ 2A | 0 | 0 | 0.44418 | 0.031594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2851 | 18.21% | CZ 2A | 98.1523 | 30.7013 | 89.5381 | 3.4532 | 0 | 283.3965 | 0 | 167.5382 | 0 | 0.23791 | 57.7705 | 0 | 0 | 309.234 | 0 | 0 | 1040.0221 | 18.21%
CZ 2B | 0.99662 | 0.312 | 0.85386 | 0.018132 | 0 | 2.0618 | 0 | 1.8845 | 0 | 0.0024157 | 0.58052 | 0 | 0 | 3.0348 | 0 | 0 | 9.7447 | 2.812% | CZ 2B | 31.9893 | 10.0146 | 58.0178 | 1.8502 | 0 | 66.1789 | 0 | 60.4893 | 0 | 0.077539 | 18.6336 | 0 | 0 | 152.8844 | 0 | 0 | 400.1355 | 2.812% | CZ 2B | 9.3755 | 2.9351 | 3.9153 | 0 | 0 | 19.3959 | 0 | 17.7284 | 0 | 0.022725 | 5.4612 | 0 | 0 | 21.0887 | 0 | 0 | 79.9229 | 2.812% | CZ 2B | 0 | 0 | 0.44659 | 0.018502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2744 | 2.812% | CZ 2B | 98.1523 | 30.7278 | 89.8017 | 2.0222 | 0 | 203.056 | 0 | 185.5985 | 0 | 0.23791 | 57.1731 | 0 | 0 | 309.234 | 0 | 0 | 976.0034 | 2.812%
CZ 3A | 0.99662 | 0.3119 | 0.91723 | 0.24395 | 0 | 1.668 | 0 | 1.6819 | 0 | 0.0024157 | 0.57499 | 0 | 0 | 3.0348 | 0 | 0 | 9.4318 | 17.3% | CZ 3A | 31.9893 | 10.0112 | 64.4469 | 24.8927 | 0 | 53.5383 | 0 | 53.9863 | 0 | 0.077539 | 18.4561 | 0 | 0 | 152.8844 | 0 | 0 | 410.2826 | 17.3% | CZ 3A | 9.3755 | 2.9341 | 3.9204 | 0 | 0 | 15.6912 | 0 | 15.8225 | 0 | 0.022725 | 5.4092 | 0 | 0 | 21.0887 | 0 | 0 | 74.2643 | 17.3% | CZ 3A | 0 | 0 | 0.5107 | 0.24893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.5689 | 17.3% | CZ 3A | 98.1523 | 30.7172 | 96.8627 | 27.2077 | 0 | 164.2709 | 0 | 165.6455 | 0 | 0.23791 | 56.6286 | 0 | 0 | 309.234 | 0 | 0 | 948.9567 | 17.3%
CZ 3B | 0.99662 | 0.3119 | 0.90011 | 0.080798 | 0 | 1.3886 | 0 | 1.8653 | 0 | 0.0024157 | 0.57618 | 0 | 0 | 3.0348 | 0 | 0 | 9.1568 | 8.647% | CZ 3B | 31.9893 | 10.0112 | 62.719 | 8.2447 | 0 | 44.5713 | 0 | 59.8724 | 0 | 0.077539 | 18.494 | 0 | 0 | 152.8844 | 0 | 0 | 388.8638 | 8.647% | CZ 3B | 9.3755 | 2.9341 | 3.9179 | 0 | 0 | 13.0631 | 0 | 17.5476 | 0 | 0.022725 | 5.4203 | 0 | 0 | 21.0887 | 0 | 0 | 73.3699 | 8.647% | CZ 3B | 0 | 0 | 0.49351 | 0.082447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3853 | 8.647% | CZ 3B | 98.1523 | 30.7172 | 94.9571 | 9.0115 | 0 | 136.7576 | 0 | 183.7058 | 0 | 0.23791 | 56.7449 | 0 | 0 | 309.234 | 0 | 0 | 919.5182 | 8.647%
CZ 3C | 0.99662 | 0.31184 | 0.92431 | 0.017558 | 0 | 0.55588 | 0 | 1.6117 | 0 | 0.0024157 | 0.57795 | 0 | 0 | 3.0348 | 0 | 0 | 8.0331 | 1.321% | CZ 3C | 31.9893 | 10.0095 | 65.1773 | 1.7916 | 0 | 17.8427 | 0 | 51.7325 | 0 | 0.077539 | 18.5508 | 0 | 0 | 152.8844 | 0 | 0 | 350.0555 | 1.321% | CZ 3C | 9.3755 | 2.9336 | 3.9194 | 0 | 0 | 5.2294 | 0 | 15.1619 | 0 | 0.022725 | 5.4369 | 0 | 0 | 21.0887 | 0 | 0 | 63.1682 | 1.321% | CZ 3C | 0 | 0 | 0.51804 | 0.017916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3453 | 1.321% | CZ 3C | 98.1523 | 30.7119 | 97.6542 | 1.9582 | 0 | 54.7464 | 0 | 158.7302 | 0 | 0.23791 | 56.9193 | 0 | 0 | 309.234 | 0 | 0 | 808.3444 | 1.321%
CZ 4A | 0.99662 | 0.31147 | 0.96912 | 0.60572 | 0 | 1.0768 | 0 | 1.5909 | 0 | 0.0024157 | 0.56678 | 0 | 0 | 3.0348 | 0 | 0 | 9.1546 | 16.82% | CZ 4A | 31.9893 | 9.9974 | 69.7079 | 61.8079 | 0 | 34.5618 | 0 | 51.0639 | 0 | 0.077539 | 18.1924 | 0 | 0 | 152.8844 | 0 | 0 | 430.2827 | 16.82% | CZ 4A | 9.3755 | 2.9301 | 3.9249 | 0 | 0 | 10.1295 | 0 | 14.966 | 0 | 0.022725 | 5.3319 | 0 | 0 | 21.0887 | 0 | 0 | 67.7694 | 16.82% | CZ 4A | 0 | 0 | 0.56316 | 0.61808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9905 | 16.82% | CZ 4A | 98.1523 | 30.6749 | 102.6436 | 67.5561 | 0 | 106.0457 | 0 | 156.6788 | 0 | 0.23791 | 55.8196 | 0 | 0 | 309.234 | 0 | 0 | 927.043 | 16.82%
CZ 4B | 0.99662 | 0.31168 | 0.95416 | 0.22195 | 0 | 0.86252 | 0 | 1.8947 | 0 | 0.0024157 | 0.5678 | 0 | 0 | 3.0348 | 0 | 0 | 8.8467 | 0.7787% | CZ 4B | 31.9893 | 10.0043 | 68.2006 | 22.648 | 0 | 27.685 | 0 | 60.8149 | 0 | 0.077539 | 18.2252 | 0 | 0 | 152.8844 | 0 | 0 | 392.5292 | 0.7787% | CZ 4B | 9.3755 | 2.9321 | 3.9224 | 0 | 0 | 8.114 | 0 | 17.8238 | 0 | 0.022725 | 5.3415 | 0 | 0 | 21.0887 | 0 | 0 | 68.6208 | 0.7787% | CZ 4B | 0 | 0 | 0.54817 | 0.22648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.584 | 0.7787% | CZ 4B | 98.1523 | 30.696 | 100.9791 | 24.7543 | 0 | 84.9455 | 0 | 186.5977 | 0 | 0.23791 | 55.9201 | 0 | 0 | 309.234 | 0 | 0 | 891.5169 | 0.7787%
CZ 4C | 0.99662 | 0.31109 | 0.98505 | 0.34313 | 0 | 0.23835 | 0 | 1.5625 | 0 | 0.0024157 | 0.56351 | 0 | 0 | 3.0348 | 0 | 0 | 8.0375 | 2.174% | CZ 4C | 31.9893 | 9.9853 | 71.3186 | 35.0134 | 0 | 7.6505 | 0 | 50.1524 | 0 | 0.077539 | 18.0873 | 0 | 0 | 152.8844 | 0 | 0 | 377.1589 | 2.174% | CZ 4C | 9.3755 | 2.9265 | 3.927 | 0 | 0 | 2.2422 | 0 | 14.6988 | 0 | 0.022725 | 5.3011 | 0 | 0 | 21.0887 | 0 | 0 | 59.5826 | 2.174% | CZ 4C | 0 | 0 | 0.5792 | 0.35013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7386 | 2.174% | CZ 4C | 98.1523 | 30.6379 | 104.4178 | 38.2697 | 0 | 23.4741 | 0 | 153.882 | 0 | 0.23791 | 55.4971 | 0 | 0 | 309.234 | 0 | 0 | 813.8028 | 2.174%
CZ 5A | 0.99662 | 0.31152 | 1.0126 | 0.94451 | 0 | 0.64709 | 0 | 1.5266 | 0 | 0.0024157 | 0.56211 | 0 | 0 | 3.0348 | 0 | 0 | 9.0383 | 20.06% | CZ 5A | 31.9893 | 9.9991 | 74.1301 | 96.3786 | 0 | 20.7702 | 0 | 49.0014 | 0 | 0.077539 | 18.0425 | 0 | 0 | 152.8844 | 0 | 0 | 453.2731 | 20.06% | CZ 5A | 9.3755 | 2.9306 | 3.927 | 0 | 0 | 6.0874 | 0 | 14.3615 | 0 | 0.022725 | 5.288 | 0 | 0 | 21.0887 | 0 | 0 | 63.0813 | 20.06% | CZ 5A | 0 | 0 | 0.60731 | 0.96379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3804 | 20.06% | CZ 5A | 98.1523 | 30.6802 | 107.4906 | 105.3418 | 0 | 63.7289 | 0 | 150.3504 | 0 | 0.23791 | 55.3597 | 0 | 0 | 309.234 | 0 | 0 | 920.5758 | 20.06%
CZ 5B | 0.99662 | 0.31157 | 1 | 0.50638 | 0 | 0.75569 | 0 | 1.7887 | 0 | 0.0024157 | 0.56351 | 0 | 0 | 3.0348 | 0 | 0 | 8.9597 | 4.626% | CZ 5B | 31.9893 | 10.0008 | 72.8587 | 51.6717 | 0 | 24.256 | 0 | 57.4135 | 0 | 0.077539 | 18.0873 | 0 | 0 | 152.8844 | 0 | 0 | 419.2393 | 4.626% | CZ 5B | 9.3755 | 2.9311 | 3.9249 | 0 | 0 | 7.109 | 0 | 16.8269 | 0 | 0.022725 | 5.3011 | 0 | 0 | 21.0887 | 0 | 0 | 66.5801 | 4.626% | CZ 5B | 0 | 0 | 0.59467 | 0.51672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.9207 | 4.626% | CZ 5B | 98.1523 | 30.6855 | 106.0874 | 56.4772 | 0 | 74.4244 | 0 | 176.1613 | 0 | 0.23791 | 55.4971 | 0 | 0 | 309.234 | 0 | 0 | 906.9571 | 4.626%
CZ 5C | 0.99662 | 0.31109 | 1.01 | 0.43446 | 0 | 0.094428 | 0 | 1.476 | 0 | 0.0024157 | 0.55948 | 0 | 0 | 3.0348 | 0 | 0 | 7.9194 | 0.066% | CZ 5C | 31.9893 | 9.9853 | 73.851 | 44.3331 | 0 | 3.0309 | 0 | 47.3765 | 0 | 0.077539 | 17.9581 | 0 | 0 | 152.8844 | 0 | 0 | 381.4861 | 0.066% | CZ 5C | 9.3755 | 2.9265 | 3.929 | 0 | 0 | 0.88831 | 0 | 13.8853 | 0 | 0.022725 | 5.2632 | 0 | 0 | 21.0887 | 0 | 0 | 57.3793 | 0.066% | CZ 5C | 0 | 0 | 0.60445 | 0.44333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8571 | 0.066% | CZ 5C | 98.1523 | 30.6379 | 107.1992 | 48.4561 | 0 | 9.2998 | 0 | 145.3648 | 0 | 0.23791 | 55.1006 | 0 | 0 | 309.234 | 0 | 0 | 803.6825 | 0.066%
CZ 6A | 0.99662 | 0.31141 | 1.0445 | 1.405 | 0 | 0.69825 | 0 | 1.5748 | 0 | 0.0024157 | 0.56088 | 0 | 0 | 3.0348 | 0 | 0 | 9.6288 | 3.001% | CZ 6A | 31.9893 | 9.9957 | 77.3808 | 143.3698 | 0 | 22.4123 | 0 | 50.5487 | 0 | 0.077539 | 18.0029 | 0 | 0 | 152.8844 | 0 | 0 | 506.6614 | 3.001% | CZ 6A | 9.3755 | 2.9296 | 3.9275 | 0 | 0 | 6.5687 | 0 | 14.815 | 0 | 0.022725 | 5.2763 | 0 | 0 | 21.0887 | 0 | 0 | 64.004 | 3.001% | CZ 6A | 0 | 0 | 0.6398 | 1.4337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8828 | 3.001% | CZ 6A | 98.1523 | 30.6696 | 111.047 | 156.7032 | 0 | 68.7674 | 0 | 155.098 | 0 | 0.23791 | 55.2381 | 0 | 0 | 309.234 | 0 | 0 | 985.1476 | 3.001%
CZ 6B | 0.99662 | 0.3112 | 1.0364 | 0.91956 | 0 | 0.51031 | 0 | 1.6916 | 0 | 0.0024157 | 0.55884 | 0 | 0 | 3.0348 | 0 | 0 | 9.0618 | 0.4557% | CZ 6B | 31.9893 | 9.9888 | 76.559 | 93.8325 | 0 | 16.3797 | 0 | 54.2965 | 0 | 0.077539 | 17.9374 | 0 | 0 | 152.8844 | 0 | 0 | 453.9451 | 0.4557% | CZ 6B | 9.3755 | 2.9275 | 3.9275 | 0 | 0 | 4.8006 | 0 | 15.9134 | 0 | 0.022725 | 5.2572 | 0 | 0 | 21.0887 | 0 | 0 | 63.3131 | 0.4557% | CZ 6B | 0 | 0 | 0.63159 | 0.93833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3792 | 0.4557% | CZ 6B | 98.1523 | 30.6485 | 110.1489 | 102.5589 | 0 | 50.2578 | 0 | 166.5972 | 0 | 0.23791 | 55.0372 | 0 | 0 | 309.234 | 0 | 0 | 922.8726 | 0.4557%
CZ 7 | 0.99662 | 0.31098 | 1.0826 | 1.8481 | 0 | 0.52443 | 0 | 1.5667 | 0 | 0.0024157 | 0.55798 | 0 | 0 | 3.0348 | 0 | 0 | 9.9247 | 0.4458% | CZ 7 | 31.9893 | 9.9819 | 81.2637 | 188.5815 | 0 | 16.8329 | 0 | 50.2885 | 0 | 0.077539 | 17.9099 | 0 | 0 | 152.8844 | 0 | 0 | 549.8095 | 0.4458% | CZ 7 | 9.3755 | 2.9255 | 3.9285 | 0 | 0 | 4.9334 | 0 | 14.7387 | 0 | 0.022725 | 5.2491 | 0 | 0 | 21.0887 | 0 | 0 | 62.2622 | 0.4458% | CZ 7 | 0 | 0 | 0.6786 | 1.8858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3737 | 0.4458% | CZ 7 | 98.1523 | 30.6273 | 115.2979 | 206.1196 | 0 | 51.6482 | 0 | 154.2997 | 0 | 0.23791 | 54.9526 | 0 | 0 | 309.234 | 0 | 0 | 1020.5695 | 0.4458%
CZ 8 | 0.99662 | 0.30927 | 1.134 | 2.7477 | 0 | 0.21881 | 0 | 1.5248 | 0 | 0.0024157 | 0.55298 | 0 | 0 | 3.0348 | 0 | 0 | 10.5214 | 0.08738% | CZ 8 | 31.9893 | 9.9268 | 86.4954 | 280.3726 | 0 | 7.0233 | 0 | 48.9428 | 0 | 0.077539 | 17.7496 | 0 | 0 | 152.8844 | 0 | 0 | 635.4618 | 0.08738% | CZ 8 | 9.3755 | 2.9094 | 3.9305 | 0 | 0 | 2.0584 | 0 | 14.3443 | 0 | 0.022725 | 5.2021 | 0 | 0 | 21.0887 | 0 | 0 | 58.9317 | 0.08738% | CZ 8 | 0 | 0 | 0.73085 | 2.8037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.3439 | 0.08738% | CZ 8 | 98.1523 | 30.4581 | 121.0298 | 306.4473 | 0 | 21.5496 | 0 | 150.1706 | 0 | 0.23791 | 54.4609 | 0 | 0 | 309.234 | 0 | 0 | 1091.7406 | 0.08738%
US Weighted | 0.99662 | 0.31167 | 0.93757 | 0.43682 | 0 | 1.4895 | 0 | 1.659 | 0 | 0.0024157 | 0.57248 | 0 | 0 | 3.0348 | 0 | 0 | 9.4409 | 100% | US Weighted | 31.9893 | 10.0041 | 66.5135 | 44.5733 | 0 | 47.8105 | 0 | 53.2497 | 0 | 0.077539 | 18.3753 | 0 | 0 | 152.8844 | 0 | 0 | 425.4776 | 100% | US Weighted | 9.3755 | 2.932 | 3.9216 | 0 | 0 | 14.0125 | 0 | 15.6066 | 0 | 0.022725 | 5.3855 | 0 | 0 | 21.0887 | 0 | 0 | 72.3452 | 100% | US Weighted | 0 | 0 | 0.53133 | 0.44573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7864 | 100% | US Weighted | 98.1523 | 30.6954 | 99.1297 | 48.7186 | 0 | 146.6964 | 0 | 163.3856 | 0 | 0.23791 | 56.3808 | 0 | 0 | 309.234 | 0 | 0 | 952.6307 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 5502 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.99662 | 0.31216 | 0.78058 | 0 | 0 | 5.2937 | 0 | 1.8789 | 0 | 0.0024157 | 0.5897 | 0 | 0 | 3.0348 | 0 | 0 | 12.889 | 0% | CZ 0A | 31.9893 | 10.0198 | 50.5552 | 0 | 0 | 169.9161 | 0 | 60.3101 | 0 | 0.077539 | 18.9282 | 0 | 0 | 152.8844 | 0 | 0 | 494.6806 | 0% | CZ 0A | 9.3755 | 2.9366 | 3.9133 | 0 | 0 | 49.7996 | 0 | 17.6759 | 0 | 0.022725 | 5.5475 | 0 | 0 | 21.0887 | 0 | 0 | 110.3599 | 0% | CZ 0A | 0 | 0 | 0.37203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1813 | 0% | CZ 0A | 98.1523 | 30.7436 | 81.6314 | 0 | 0 | 521.3517 | 0 | 185.0486 | 0 | 0.23791 | 58.0772 | 0 | 0 | 309.234 | 0 | 0 | 1284.4767 | 0%
CZ 0B | 0.99662 | 0.31222 | 0.77824 | 0.00082723 | 0 | 4.4728 | 0 | 2.0217 | 0 | 0.0024157 | 0.59105 | 0 | 0 | 3.0348 | 0 | 0 | 12.2107 | 0% | CZ 0B | 31.9893 | 10.0215 | 50.3278 | 0.084411 | 0 | 143.5666 | 0 | 64.8935 | 0 | 0.077539 | 18.9713 | 0 | 0 | 152.8844 | 0 | 0 | 472.8163 | 0% | CZ 0B | 9.3755 | 2.9371 | 3.9118 | 0 | 0 | 42.077 | 0 | 19.0192 | 0 | 0.022725 | 5.5602 | 0 | 0 | 21.0887 | 0 | 0 | 103.9922 | 0% | CZ 0B | 0 | 0 | 0.36981 | 0.00084411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.1799 | 0% | CZ 0B | 98.1523 | 30.7489 | 81.3727 | 0.092261 | 0 | 440.5036 | 0 | 199.1119 | 0 | 0.23791 | 58.2094 | 0 | 0 | 309.234 | 0 | 0 | 1217.6629 | 0%
CZ 1A | 0.99662 | 0.31227 | 0.81344 | 3.3764e-05 | 0 | 3.5507 | 0 | 1.7375 | 0 | 0.0024157 | 0.58841 | 0 | 0 | 3.0348 | 0 | 0 | 11.0363 | 3.201% | CZ 1A | 31.9893 | 10.0232 | 53.9093 | 0.0034454 | 0 | 113.9707 | 0 | 55.7697 | 0 | 0.077539 | 18.8868 | 0 | 0 | 152.8844 | 0 | 0 | 437.5144 | 3.201% | CZ 1A | 9.3755 | 2.9376 | 3.9133 | 0 | 0 | 33.4029 | 0 | 16.3452 | 0 | 0.022725 | 5.5354 | 0 | 0 | 21.0887 | 0 | 0 | 92.6214 | 3.201% | CZ 1A | 0 | 0 | 0.40557 | 3.4454e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2149 | 3.201% | CZ 1A | 98.1523 | 30.7542 | 85.2974 | 0.0037658 | 0 | 349.6949 | 0 | 171.1175 | 0 | 0.23791 | 57.9503 | 0 | 0 | 309.234 | 0 | 0 | 1102.4423 | 3.201%
CZ 1B | 0.99662 | 0.31184 | 0.81386 | 0.046983 | 0 | 3.7905 | 0 | 1.996 | 0 | 0.0024157 | 0.59056 | 0 | 0 | 3.0348 | 0 | 0 | 11.5836 | 0% | CZ 1B | 31.9893 | 10.0095 | 53.9627 | 4.7942 | 0 | 121.666 | 0 | 64.0664 | 0 | 0.077539 | 18.9558 | 0 | 0 | 152.8844 | 0 | 0 | 458.4057 | 0% | CZ 1B | 9.3755 | 2.9336 | 3.9118 | 0 | 0 | 35.6583 | 0 | 18.7768 | 0 | 0.022725 | 5.5556 | 0 | 0 | 21.0887 | 0 | 0 | 97.3231 | 0% | CZ 1B | 0 | 0 | 0.40616 | 0.047942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.2634 | 0% | CZ 1B | 98.1523 | 30.7119 | 85.3456 | 5.2401 | 0 | 373.3065 | 0 | 196.5742 | 0 | 0.23791 | 58.1618 | 0 | 0 | 309.234 | 0 | 0 | 1156.9641 | 0%
CZ 2A | 0.99662 | 0.31173 | 0.85096 | 0.11004 | 0 | 3.1869 | 0 | 1.8079 | 0 | 0.0024157 | 0.58825 | 0 | 0 | 3.0348 | 0 | 0 | 10.8896 | 18.21% | CZ 2A | 31.9893 | 10.006 | 57.737 | 11.2284 | 0 | 102.2933 | 0 | 58.0287 | 0 | 0.077539 | 18.8817 | 0 | 0 | 152.8844 | 0 | 0 | 443.1263 | 18.21% | CZ 2A | 9.3755 | 2.9326 | 3.9133 | 0 | 0 | 29.9804 | 0 | 17.0072 | 0 | 0.022725 | 5.5339 | 0 | 0 | 21.0887 | 0 | 0 | 89.8545 | 18.21% | CZ 2A | 0 | 0 | 0.44385 | 0.11228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3654 | 18.21% | CZ 2A | 98.1523 | 30.7013 | 89.4812 | 12.2727 | 0 | 313.8652 | 0 | 178.0487 | 0 | 0.23791 | 57.9344 | 0 | 0 | 309.234 | 0 | 0 | 1089.9277 | 18.21%
CZ 2B | 0.99662 | 0.312 | 0.85287 | 0.094963 | 0 | 2.4779 | 0 | 2.0411 | 0 | 0.0024157 | 0.5889 | 0 | 0 | 3.0348 | 0 | 0 | 10.4016 | 2.812% | CZ 2B | 31.9893 | 10.0146 | 57.9438 | 9.6901 | 0 | 79.5346 | 0 | 65.5155 | 0 | 0.077539 | 18.9024 | 0 | 0 | 152.8844 | 0 | 0 | 426.5522 | 2.812% | CZ 2B | 9.3755 | 2.9351 | 3.9118 | 0 | 0 | 23.3103 | 0 | 19.2015 | 0 | 0.022725 | 5.54 | 0 | 0 | 21.0887 | 0 | 0 | 85.3856 | 2.812% | CZ 2B | 0 | 0 | 0.44597 | 0.096901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.3522 | 2.812% | CZ 2B | 98.1523 | 30.7278 | 89.6969 | 10.5912 | 0 | 244.0352 | 0 | 201.0205 | 0 | 0.23791 | 57.9979 | 0 | 0 | 309.234 | 0 | 0 | 1041.6936 | 2.812%
CZ 3A | 0.99662 | 0.3119 | 0.91535 | 0.46836 | 0 | 2.0202 | 0 | 1.783 | 0 | 0.0024157 | 0.58691 | 0 | 0 | 3.0348 | 0 | 0 | 10.1195 | 17.3% | CZ 3A | 31.9893 | 10.0112 | 64.3039 | 47.7922 | 0 | 64.8435 | 0 | 57.2292 | 0 | 0.077539 | 18.8386 | 0 | 0 | 152.8844 | 0 | 0 | 447.9698 | 17.3% | CZ 3A | 9.3755 | 2.9341 | 3.9138 | 0 | 0 | 19.0045 | 0 | 16.7729 | 0 | 0.022725 | 5.5213 | 0 | 0 | 21.0887 | 0 | 0 | 78.6336 | 17.3% | CZ 3A | 0 | 0 | 0.5095 | 0.47792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.7967 | 17.3% | CZ 3A | 98.1523 | 30.7172 | 96.6621 | 52.2369 | 0 | 198.9586 | 0 | 175.5956 | 0 | 0.23791 | 57.8023 | 0 | 0 | 309.234 | 0 | 0 | 1019.5969 | 17.3%
CZ 3B | 0.99662 | 0.3119 | 0.89844 | 0.24285 | 0 | 1.5058 | 0 | 2.0059 | 0 | 0.0024157 | 0.58697 | 0 | 0 | 3.0348 | 0 | 0 | 9.5857 | 8.647% | CZ 3B | 31.9893 | 10.0112 | 62.5933 | 24.7807 | 0 | 48.3328 | 0 | 64.3835 | 0 | 0.077539 | 18.8403 | 0 | 0 | 152.8844 | 0 | 0 | 413.893 | 8.647% | CZ 3B | 9.3755 | 2.9341 | 3.9118 | 0 | 0 | 14.1655 | 0 | 18.8697 | 0 | 0.022725 | 5.5218 | 0 | 0 | 21.0887 | 0 | 0 | 75.8899 | 8.647% | CZ 3B | 0 | 0 | 0.49246 | 0.24781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.5496 | 8.647% | CZ 3B | 98.1523 | 30.7172 | 94.7788 | 27.0853 | 0 | 148.299 | 0 | 197.547 | 0 | 0.23791 | 57.8075 | 0 | 0 | 309.234 | 0 | 0 | 963.8591 | 8.647%
CZ 3C | 0.99662 | 0.31184 | 0.92274 | 0.13004 | 0 | 0.60006 | 0 | 1.7538 | 0 | 0.0024157 | 0.58723 | 0 | 0 | 3.0348 | 0 | 0 | 8.3396 | 1.321% | CZ 3C | 31.9893 | 10.0095 | 65.0584 | 13.2698 | 0 | 19.2608 | 0 | 56.2918 | 0 | 0.077539 | 18.8489 | 0 | 0 | 152.8844 | 0 | 0 | 367.6904 | 1.321% | CZ 3C | 9.3755 | 2.9336 | 3.9138 | 0 | 0 | 5.645 | 0 | 16.4982 | 0 | 0.022725 | 5.5243 | 0 | 0 | 21.0887 | 0 | 0 | 65.0019 | 1.321% | CZ 3C | 0 | 0 | 0.51704 | 0.1327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.459 | 1.321% | CZ 3C | 98.1523 | 30.7119 | 97.4868 | 14.5039 | 0 | 59.0976 | 0 | 172.7195 | 0 | 0.23791 | 57.834 | 0 | 0 | 309.234 | 0 | 0 | 839.9778 | 1.321%
CZ 4A | 0.99662 | 0.31147 | 0.96598 | 1.0002 | 0 | 1.4141 | 0 | 1.6952 | 0 | 0.0024157 | 0.58659 | 0 | 0 | 3.0348 | 0 | 0 | 10.0074 | 16.82% | CZ 4A | 31.9893 | 9.9974 | 69.4702 | 102.0583 | 0 | 45.3898 | 0 | 54.4136 | 0 | 0.077539 | 18.8283 | 0 | 0 | 152.8844 | 0 | 0 | 485.1088 | 16.82% | CZ 4A | 9.3755 | 2.9301 | 3.9138 | 0 | 0 | 13.303 | 0 | 15.9477 | 0 | 0.022725 | 5.5182 | 0 | 0 | 21.0887 | 0 | 0 | 72.0998 | 16.82% | CZ 4A | 0 | 0 | 0.56116 | 1.0206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.391 | 16.82% | CZ 4A | 98.1523 | 30.6749 | 102.3089 | 111.5497 | 0 | 139.2689 | 0 | 166.9567 | 0 | 0.23791 | 57.7705 | 0 | 0 | 309.234 | 0 | 0 | 1016.1538 | 16.82%
CZ 4B | 0.99662 | 0.31168 | 0.95171 | 0.50336 | 0 | 0.90509 | 0 | 2.035 | 0 | 0.0024157 | 0.58348 | 0 | 0 | 3.0348 | 0 | 0 | 9.3242 | 0.7787% | CZ 4B | 31.9893 | 10.0043 | 68.0145 | 51.3634 | 0 | 29.0514 | 0 | 65.3191 | 0 | 0.077539 | 18.7283 | 0 | 0 | 152.8844 | 0 | 0 | 427.4322 | 0.7787% | CZ 4B | 9.3755 | 2.9321 | 3.9138 | 0 | 0 | 8.5145 | 0 | 19.1439 | 0 | 0.022725 | 5.489 | 0 | 0 | 21.0887 | 0 | 0 | 70.4802 | 0.7787% | CZ 4B | 0 | 0 | 0.54661 | 0.51363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 1.8695 | 0.7787% | CZ 4B | 98.1523 | 30.696 | 100.7179 | 56.1401 | 0 | 89.138 | 0 | 200.4178 | 0 | 0.23791 | 57.4639 | 0 | 0 | 309.234 | 0 | 0 | 942.198 | 0.7787%
CZ 4C | 0.99662 | 0.31109 | 0.98131 | 0.79949 | 0 | 0.24699 | 0 | 1.6755 | 0 | 0.0024157 | 0.58584 | 0 | 0 | 3.0348 | 0 | 0 | 8.6341 | 2.174% | CZ 4C | 31.9893 | 9.9853 | 71.0344 | 81.5808 | 0 | 7.928 | 0 | 53.7812 | 0 | 0.077539 | 18.8041 | 0 | 0 | 152.8844 | 0 | 0 | 428.0651 | 2.174% | CZ 4C | 9.3755 | 2.9265 | 3.9138 | 0 | 0 | 2.3236 | 0 | 15.7624 | 0 | 0.022725 | 5.5112 | 0 | 0 | 21.0887 | 0 | 0 | 60.9244 | 2.174% | CZ 4C | 0 | 0 | 0.5768 | 0.81581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.2019 | 2.174% | CZ 4C | 98.1523 | 30.6379 | 104.0186 | 89.1679 | 0 | 24.3253 | 0 | 165.0164 | 0 | 0.23791 | 57.6965 | 0 | 0 | 309.234 | 0 | 0 | 878.4867 | 2.174%
CZ 5A | 0.99662 | 0.31152 | 1.0089 | 1.4324 | 0 | 1.0224 | 0 | 1.673 | 0 | 0.0024157 | 0.58611 | 0 | 0 | 3.0348 | 0 | 0 | 10.0681 | 20.06% | CZ 5A | 31.9893 | 9.9991 | 73.8475 | 146.1623 | 0 | 32.8163 | 0 | 53.6985 | 0 | 0.077539 | 18.8128 | 0 | 0 | 152.8844 | 0 | 0 | 520.2878 | 20.06% | CZ 5A | 9.3755 | 2.9306 | 3.9138 | 0 | 0 | 9.6179 | 0 | 15.7381 | 0 | 0.022725 | 5.5137 | 0 | 0 | 21.0887 | 0 | 0 | 68.2011 | 20.06% | CZ 5A | 0 | 0 | 0.60494 | 1.4616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8759 | 20.06% | CZ 5A | 98.1523 | 30.6802 | 107.0933 | 159.7554 | 0 | 100.69 | 0 | 164.7626 | 0 | 0.23791 | 57.723 | 0 | 0 | 309.234 | 0 | 0 | 1028.3286 | 20.06%
CZ 5B | 0.99662 | 0.31157 | 0.99684 | 0.91179 | 0 | 1.1376 | 0 | 1.9786 | 0 | 0.0024157 | 0.58552 | 0 | 0 | 3.0348 | 0 | 0 | 9.9558 | 4.626% | CZ 5B | 31.9893 | 10.0008 | 72.6193 | 93.0401 | 0 | 36.5158 | 0 | 63.5081 | 0 | 0.077539 | 18.7938 | 0 | 0 | 152.8844 | 0 | 0 | 479.4291 | 4.626% | CZ 5B | 9.3755 | 2.9311 | 3.9138 | 0 | 0 | 10.7022 | 0 | 18.6132 | 0 | 0.022725 | 5.5081 | 0 | 0 | 21.0887 | 0 | 0 | 72.1554 | 4.626% | CZ 5B | 0 | 0 | 0.59265 | 0.9304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.3324 | 4.626% | CZ 5B | 98.1523 | 30.6855 | 105.7508 | 101.6928 | 0 | 112.0411 | 0 | 194.8612 | 0 | 0.23791 | 57.6648 | 0 | 0 | 309.234 | 0 | 0 | 1010.3204 | 4.626%
CZ 5C | 0.99662 | 0.31109 | 1.0056 | 1.0271 | 0 | 0.088576 | 0 | 1.591 | 0 | 0.0024157 | 0.58595 | 0 | 0 | 3.0348 | 0 | 0 | 8.6432 | 0.066% | CZ 5C | 31.9893 | 9.9853 | 73.5151 | 104.8025 | 0 | 2.8431 | 0 | 51.0691 | 0 | 0.077539 | 18.8076 | 0 | 0 | 152.8844 | 0 | 0 | 445.9739 | 0.066% | CZ 5C | 9.3755 | 2.9265 | 3.9138 | 0 | 0 | 0.83327 | 0 | 14.9675 | 0 | 0.022725 | 5.5122 | 0 | 0 | 21.0887 | 0 | 0 | 58.6403 | 0.066% | CZ 5C | 0 | 0 | 0.60161 | 1.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.4589 | 0.066% | CZ 5C | 98.1523 | 30.6379 | 106.7299 | 114.5492 | 0 | 8.7235 | 0 | 156.6947 | 0 | 0.23791 | 57.7071 | 0 | 0 | 309.234 | 0 | 0 | 882.6664 | 0.066%
CZ 6A | 0.99662 | 0.31141 | 1.0407 | 1.91 | 0 | 1.0362 | 0 | 1.6916 | 0 | 0.0024157 | 0.58557 | 0 | 0 | 3.0348 | 0 | 0 | 10.6094 | 3.001% | CZ 6A | 31.9893 | 9.9957 | 77.0913 | 194.8986 | 0 | 33.2609 | 0 | 54.2982 | 0 | 0.077539 | 18.7955 | 0 | 0 | 152.8844 | 0 | 0 | 573.2914 | 3.001% | CZ 6A | 9.3755 | 2.9296 | 3.9138 | 0 | 0 | 9.7482 | 0 | 15.9139 | 0 | 0.022725 | 5.5087 | 0 | 0 | 21.0887 | 0 | 0 | 68.5011 | 3.001% | CZ 6A | 0 | 0 | 0.63737 | 1.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.3957 | 3.001% | CZ 6A | 98.1523 | 30.6696 | 110.6388 | 213.0241 | 0 | 102.0541 | 0 | 166.6025 | 0 | 0.23791 | 57.6701 | 0 | 0 | 309.234 | 0 | 0 | 1088.2833 | 3.001%
CZ 6B | 0.99662 | 0.3112 | 1.0326 | 1.4287 | 0 | 0.87744 | 0 | 1.8502 | 0 | 0.0024157 | 0.5853 | 0 | 0 | 3.0348 | 0 | 0 | 10.1193 | 0.4557% | CZ 6B | 31.9893 | 9.9888 | 76.2662 | 145.7833 | 0 | 28.164 | 0 | 59.3882 | 0 | 0.077539 | 18.7869 | 0 | 0 | 152.8844 | 0 | 0 | 523.3285 | 0.4557% | CZ 6B | 9.3755 | 2.9275 | 3.9138 | 0 | 0 | 8.2544 | 0 | 17.4057 | 0 | 0.022725 | 5.5061 | 0 | 0 | 21.0887 | 0 | 0 | 68.4945 | 0.4557% | CZ 6B | 0 | 0 | 0.62912 | 1.4578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.8963 | 0.4557% | CZ 6B | 98.1523 | 30.6485 | 109.7369 | 159.3411 | 0 | 86.4152 | 0 | 182.2201 | 0 | 0.23791 | 57.6436 | 0 | 0 | 309.234 | 0 | 0 | 1033.6297 | 0.4557%
CZ 7 | 0.99662 | 0.31098 | 1.0784 | 2.3736 | 0 | 0.86128 | 0 | 1.6885 | 0 | 0.0024157 | 0.58552 | 0 | 0 | 3.0348 | 0 | 0 | 10.9322 | 0.4458% | CZ 7 | 31.9893 | 9.9819 | 80.9467 | 242.2016 | 0 | 27.6453 | 0 | 54.1982 | 0 | 0.077539 | 18.7938 | 0 | 0 | 152.8844 | 0 | 0 | 618.7187 | 0.4458% | CZ 7 | 9.3755 | 2.9255 | 3.9138 | 0 | 0 | 8.1024 | 0 | 15.8846 | 0 | 0.022725 | 5.5081 | 0 | 0 | 21.0887 | 0 | 0 | 66.8214 | 0.4458% | CZ 7 | 0 | 0 | 0.67593 | 2.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 3.9072 | 0.4458% | CZ 7 | 98.1523 | 30.6273 | 114.8527 | 264.7263 | 0 | 84.8239 | 0 | 166.2958 | 0 | 0.23791 | 57.6648 | 0 | 0 | 309.234 | 0 | 0 | 1126.615 | 0.4458%
CZ 8 | 0.99662 | 0.30927 | 1.1294 | 3.2833 | 0 | 0.55841 | 0 | 1.6503 | 0 | 0.0024157 | 0.58509 | 0 | 0 | 3.0348 | 0 | 0 | 11.5496 | 0.08738% | CZ 8 | 31.9893 | 9.9268 | 86.1388 | 335.0298 | 0 | 17.9236 | 0 | 52.9697 | 0 | 0.077539 | 18.78 | 0 | 0 | 152.8844 | 0 | 0 | 705.7198 | 0.08738% | CZ 8 | 9.3755 | 2.9094 | 3.9143 | 0 | 0 | 5.2531 | 0 | 15.5245 | 0 | 0.022725 | 5.5041 | 0 | 0 | 21.0887 | 0 | 0 | 63.5924 | 0.08738% | CZ 8 | 0 | 0 | 0.72783 | 3.3503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 4.8874 | 0.08738% | CZ 8 | 98.1523 | 30.4581 | 120.5311 | 366.1875 | 0 | 54.9949 | 0 | 162.5262 | 0 | 0.23791 | 57.6225 | 0 | 0 | 309.234 | 0 | 0 | 1199.9446 | 0.08738%
US Weighted | 0.99662 | 0.31167 | 0.93528 | 0.72345 | 0 | 1.7986 | 0 | 1.7809 | 0 | 0.0024157 | 0.58688 | 0 | 0 | 3.0348 | 0 | 0 | 10.1707 | 100% | US Weighted | 31.9893 | 10.0041 | 66.3398 | 73.8219 | 0 | 57.7319 | 0 | 57.1645 | 0 | 0.077539 | 18.8377 | 0 | 0 | 152.8844 | 0 | 0 | 468.851 | 100% | US Weighted | 9.3755 | 2.932 | 3.9135 | 0 | 0 | 16.9202 | 0 | 16.754 | 0 | 0.022725 | 5.521 | 0 | 0 | 21.0887 | 0 | 0 | 76.5277 | 100% | US Weighted | 0 | 0 | 0.52987 | 0.73822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8093 | 0 | 0 | 2.0774 | 100% | US Weighted | 98.1523 | 30.6954 | 98.8851 | 80.6874 | 0 | 177.138 | 0 | 175.3973 | 0 | 0.23791 | 57.7994 | 0 | 0 | 309.234 | 0 | 0 | 1028.2267 | 100%
Building Type: | Full-service Restaurant |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 5502 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 5502 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.72633 | 0.2121 | 0.012974 | 0 | 0 | 1.8119 | 0 | 0.99034 | 0 | 0 | 0.2762 | 0 | 0 | 0.0030062 | 0 | 0 | 4.0328 | 0% | CZ 0A | 23.3135 | 6.8079 | 0.52034 | 0 | 0 | 58.1579 | 0 | 31.7877 | 0 | 0 | 8.8653 | 0 | 0 | 0.096493 | 0 | 0 | 129.5491 | 0% | CZ 0A | 6.8328 | 1.9953 | 0.10807 | 0 | 0 | 17.0451 | 0 | 9.3164 | 0 | 0 | 2.5983 | 0 | 0 | 0.028281 | 0 | 0 | 37.9243 | 0% | CZ 0A | 0 | 0 | 0.001516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001516 | 0% | CZ 0A | 71.5325 | 20.8888 | 1.2971 | 0 | 0 | 178.4452 | 0 | 97.5337 | 0 | 0 | 27.2014 | 0 | 0 | 0.29607 | 0 | 0 | 397.1947 | 0%
CZ 0B | 0.72702 | 0.21221 | 0.012253 | 0.00077658 | 0 | 1.5676 | 0 | 1.1843 | 0 | 0 | 0.27969 | 0 | 0 | 0.0030062 | 0 | 0 | 3.9869 | 0% | CZ 0B | 23.3359 | 6.8114 | 0.46177 | 0.079243 | 0 | 50.3161 | 0 | 38.0149 | 0 | 0 | 8.9773 | 0 | 0 | 0.096493 | 0 | 0 | 128.0931 | 0% | CZ 0B | 6.8394 | 1.9963 | 0.10605 | 0 | 0 | 14.7468 | 0 | 11.1415 | 0 | 0 | 2.6311 | 0 | 0 | 0.028281 | 0 | 0 | 37.4894 | 0% | CZ 0B | 0 | 0 | 0.00099915 | 0.00079243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017916 | 0% | CZ 0B | 71.6012 | 20.8993 | 1.2195 | 0.086613 | 0 | 154.3843 | 0 | 116.6408 | 0 | 0 | 27.545 | 0 | 0 | 0.29607 | 0 | 0 | 392.6728 | 0%
CZ 1A | 0.72643 | 0.21226 | 0.012154 | 3.3764e-05 | 0 | 1.4196 | 0 | 1.234 | 0 | 0 | 0.27969 | 0 | 0 | 0.0030062 | 0 | 0 | 3.8872 | 3.201% | CZ 1A | 23.3169 | 6.8131 | 0.44798 | 0.0034454 | 0 | 45.5673 | 0 | 39.6088 | 0 | 0 | 8.9773 | 0 | 0 | 0.096493 | 0 | 0 | 124.8313 | 3.201% | CZ 1A | 6.8338 | 1.9968 | 0.10656 | 0 | 0 | 13.355 | 0 | 11.6087 | 0 | 0 | 2.6311 | 0 | 0 | 0.028281 | 0 | 0 | 36.5602 | 3.201% | CZ 1A | 0 | 0 | 0.00084411 | 3.4454e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00087857 | 3.201% | CZ 1A | 71.543 | 20.9046 | 1.2078 | 0.0037658 | 0 | 139.8135 | 0 | 121.5312 | 0 | 0 | 27.545 | 0 | 0 | 0.29607 | 0 | 0 | 382.845 | 3.201%
CZ 1B | 0.72606 | 0.21199 | 0.011757 | 0.028041 | 0 | 1.4469 | 0 | 1.2119 | 0 | 0 | 0.28199 | 0 | 0 | 0.0030062 | 0 | 0 | 3.9216 | 0% | CZ 1B | 23.3049 | 6.8045 | 0.4187 | 2.8614 | 0 | 46.4409 | 0 | 38.8989 | 0 | 0 | 9.0514 | 0 | 0 | 0.096493 | 0 | 0 | 127.8771 | 0% | CZ 1B | 6.8303 | 1.9943 | 0.10504 | 0 | 0 | 13.611 | 0 | 11.4006 | 0 | 0 | 2.6528 | 0 | 0 | 0.028281 | 0 | 0 | 36.6223 | 0% | CZ 1B | 0 | 0 | 0.00060294 | 0.028614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029217 | 0% | CZ 1B | 71.506 | 20.8782 | 1.1656 | 3.1275 | 0 | 142.494 | 0 | 119.353 | 0 | 0 | 27.7724 | 0 | 0 | 0.29607 | 0 | 0 | 386.5926 | 0%
CZ 2A | 0.72788 | 0.21194 | 0.011811 | 0.062414 | 0 | 1.3218 | 0 | 1.1222 | 0 | 0 | 0.28124 | 0 | 0 | 0.0030062 | 0 | 0 | 3.7424 | 18.21% | CZ 2A | 23.3634 | 6.8028 | 0.42042 | 6.3687 | 0 | 42.4278 | 0 | 36.0213 | 0 | 0 | 9.0273 | 0 | 0 | 0.096493 | 0 | 0 | 124.5283 | 18.21% | CZ 2A | 6.8474 | 1.9938 | 0.10555 | 0 | 0 | 12.4349 | 0 | 10.5572 | 0 | 0 | 2.6457 | 0 | 0 | 0.028281 | 0 | 0 | 34.6129 | 18.21% | CZ 2A | 0 | 0 | 0.00060294 | 0.063687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06429 | 18.21% | CZ 2A | 71.6858 | 20.8729 | 1.1709 | 6.961 | 0 | 130.1806 | 0 | 110.5237 | 0 | 0 | 27.6983 | 0 | 0 | 0.29607 | 0 | 0 | 369.3894 | 18.21%
CZ 2B | 0.72788 | 0.2121 | 0.010968 | 0.053686 | 0 | 1.2188 | 0 | 1.3557 | 0 | 0 | 0.28607 | 0 | 0 | 0.0030062 | 0 | 0 | 3.8682 | 2.812% | CZ 2B | 23.3634 | 6.8079 | 0.35323 | 5.4781 | 0 | 39.1194 | 0 | 43.515 | 0 | 0 | 9.1824 | 0 | 0 | 0.096493 | 0 | 0 | 127.9161 | 2.812% | CZ 2B | 6.8474 | 1.9953 | 0.10302 | 0 | 0 | 11.4652 | 0 | 12.7535 | 0 | 0 | 2.6912 | 0 | 0 | 0.028281 | 0 | 0 | 35.884 | 2.812% | CZ 2B | 0 | 0 | 1.7227e-05 | 0.054781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054798 | 2.812% | CZ 2B | 71.6858 | 20.8888 | 1.0804 | 5.9876 | 0 | 120.0297 | 0 | 133.5167 | 0 | 0 | 28.1742 | 0 | 0 | 0.29607 | 0 | 0 | 381.6592 | 2.812%
CZ 3A | 0.72751 | 0.21199 | 0.010785 | 0.1772 | 0 | 1.0146 | 0 | 1.1541 | 0 | 0 | 0.28624 | 0 | 0 | 0.0030062 | 0 | 0 | 3.5854 | 17.3% | CZ 3A | 23.3514 | 6.8045 | 0.33084 | 18.0812 | 0 | 32.5665 | 0 | 37.0431 | 0 | 0 | 9.1875 | 0 | 0 | 0.096493 | 0 | 0 | 127.4616 | 17.3% | CZ 3A | 6.8439 | 1.9943 | 0.10353 | 0 | 0 | 9.5447 | 0 | 10.8567 | 0 | 0 | 2.6927 | 0 | 0 | 0.028281 | 0 | 0 | 32.0641 | 17.3% | CZ 3A | 0 | 0 | -0.00022395 | 0.18081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18059 | 17.3% | CZ 3A | 71.6488 | 20.8782 | 1.0593 | 19.7628 | 0 | 99.9234 | 0 | 113.6589 | 0 | 0 | 28.19 | 0 | 0 | 0.29607 | 0 | 0 | 355.4175 | 17.3%
CZ 3B | 0.72675 | 0.21199 | 0.010472 | 0.099234 | 0 | 0.59164 | 0 | 1.337 | 0 | 0 | 0.28688 | 0 | 0 | 0.0030062 | 0 | 0 | 3.2669 | 8.647% | CZ 3B | 23.3273 | 6.8045 | 0.31017 | 10.1259 | 0 | 18.9902 | 0 | 42.9137 | 0 | 0 | 9.2082 | 0 | 0 | 0.096493 | 0 | 0 | 111.7765 | 8.647% | CZ 3B | 6.8368 | 1.9943 | 0.10201 | 0 | 0 | 5.5657 | 0 | 12.5773 | 0 | 0 | 2.6988 | 0 | 0 | 0.028281 | 0 | 0 | 29.8032 | 8.647% | CZ 3B | 0 | 0 | -0.00037899 | 0.10126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10088 | 8.647% | CZ 3B | 71.5748 | 20.8782 | 1.0265 | 11.0676 | 0 | 58.2675 | 0 | 131.6716 | 0 | 0 | 28.2535 | 0 | 0 | 0.29607 | 0 | 0 | 323.0357 | 8.647%
CZ 3C | 0.72514 | 0.21162 | 0.011402 | 0.072003 | 0 | 0.22461 | 0 | 1.3288 | 0 | 0 | 0.28377 | 0 | 0 | 0.0030062 | 0 | 0 | 2.8604 | 1.321% | CZ 3C | 23.2756 | 6.7924 | 0.38252 | 7.3472 | 0 | 7.2094 | 0 | 42.6518 | 0 | 0 | 9.1083 | 0 | 0 | 0.096493 | 0 | 0 | 96.8637 | 1.321% | CZ 3C | 6.8217 | 1.9908 | 0.10504 | 0 | 0 | 2.113 | 0 | 12.5005 | 0 | 0 | 2.6695 | 0 | 0 | 0.028281 | 0 | 0 | 26.2287 | 1.321% | CZ 3C | 0 | 0 | 0.00024117 | 0.073472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073713 | 1.321% | CZ 3C | 71.4162 | 20.8412 | 1.126 | 8.0305 | 0 | 22.1206 | 0 | 130.8679 | 0 | 0 | 27.9468 | 0 | 0 | 0.29607 | 0 | 0 | 282.6453 | 1.321%
CZ 4A | 0.72557 | 0.21108 | 0.0098786 | 0.38973 | 0 | 0.78522 | 0 | 1.246 | 0 | 0 | 0.2908 | 0 | 0 | 0.0030062 | 0 | 0 | 3.6613 | 16.82% | CZ 4A | 23.2894 | 6.7752 | 0.25332 | 39.768 | 0 | 25.2037 | 0 | 39.9948 | 0 | 0 | 9.334 | 0 | 0 | 0.096493 | 0 | 0 | 144.7149 | 16.82% | CZ 4A | 6.8257 | 1.9857 | 0.10151 | 0 | 0 | 7.3868 | 0 | 11.7218 | 0 | 0 | 2.7356 | 0 | 0 | 0.028281 | 0 | 0 | 30.7854 | 16.82% | CZ 4A | 0 | 0 | -0.00093025 | 0.39768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39675 | 16.82% | CZ 4A | 71.4585 | 20.7883 | 0.961 | 43.4664 | 0 | 77.3323 | 0 | 122.7155 | 0 | 0 | 28.6394 | 0 | 0 | 0.29607 | 0 | 0 | 365.6574 | 16.82%
CZ 4B | 0.72751 | 0.21178 | 0.010239 | 0.20264 | 0 | 0.34534 | 0 | 1.3881 | 0 | 0 | 0.28747 | 0 | 0 | 0.0030062 | 0 | 0 | 3.1761 | 0.7787% | CZ 4B | 23.3514 | 6.7976 | 0.2826 | 20.6773 | 0 | 11.0847 | 0 | 44.5558 | 0 | 0 | 9.2272 | 0 | 0 | 0.096493 | 0 | 0 | 116.073 | 0.7787% | CZ 4B | 6.8439 | 1.9923 | 0.10252 | 0 | 0 | 3.2487 | 0 | 13.0586 | 0 | 0 | 2.7043 | 0 | 0 | 0.028281 | 0 | 0 | 27.9786 | 0.7787% | CZ 4B | 0 | 0 | -0.00067184 | 0.20677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2061 | 0.7787% | CZ 4B | 71.6488 | 20.857 | 0.99982 | 22.6003 | 0 | 34.011 | 0 | 136.71 | 0 | 0 | 28.3116 | 0 | 0 | 0.29607 | 0 | 0 | 315.4346 | 0.7787%
CZ 4C | 0.72514 | 0.21065 | 0.0097435 | 0.3873 | 0 | 0.079611 | 0 | 1.2562 | 0 | 0 | 0.29091 | 0 | 0 | 0.0030062 | 0 | 0 | 2.9625 | 2.174% | CZ 4C | 23.2756 | 6.7614 | 0.23954 | 39.5199 | 0 | 2.5554 | 0 | 40.3204 | 0 | 0 | 9.3375 | 0 | 0 | 0.096493 | 0 | 0 | 122.1062 | 2.174% | CZ 4C | 6.8217 | 1.9817 | 0.10151 | 0 | 0 | 0.74893 | 0 | 11.8172 | 0 | 0 | 2.7367 | 0 | 0 | 0.028281 | 0 | 0 | 24.2359 | 2.174% | CZ 4C | 0 | 0 | -0.0010681 | 0.3952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39413 | 2.174% | CZ 4C | 71.4162 | 20.746 | 0.94594 | 43.1953 | 0 | 7.8406 | 0 | 123.7147 | 0 | 0 | 28.65 | 0 | 0 | 0.29607 | 0 | 0 | 296.8047 | 2.174%
CZ 5A | 0.72686 | 0.21146 | 0.0094673 | 0.46803 | 0 | 0.66545 | 0 | 1.2293 | 0 | 0 | 0.293 | 0 | 0 | 0.0030062 | 0 | 0 | 3.6066 | 20.06% | CZ 5A | 23.3307 | 6.7873 | 0.21886 | 47.7578 | 0 | 21.3595 | 0 | 39.4589 | 0 | 0 | 9.4047 | 0 | 0 | 0.096493 | 0 | 0 | 148.4141 | 20.06% | CZ 5A | 6.8378 | 1.9892 | 0.1005 | 0 | 0 | 6.2601 | 0 | 11.5647 | 0 | 0 | 2.7563 | 0 | 0 | 0.028281 | 0 | 0 | 29.537 | 20.06% | CZ 5A | 0 | 0 | -0.0012403 | 0.47758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47634 | 20.06% | CZ 5A | 71.5853 | 20.8253 | 0.91654 | 52.1993 | 0 | 65.5371 | 0 | 121.0712 | 0 | 0 | 28.8562 | 0 | 0 | 0.29607 | 0 | 0 | 361.287 | 20.06%
CZ 5B | 0.72665 | 0.21129 | 0.0096561 | 0.29608 | 0 | 0.77153 | 0 | 1.3239 | 0 | 0 | 0.29236 | 0 | 0 | 0.0030062 | 0 | 0 | 3.6344 | 4.626% | CZ 5B | 23.3238 | 6.7821 | 0.23437 | 30.2123 | 0 | 24.7643 | 0 | 42.4932 | 0 | 0 | 9.384 | 0 | 0 | 0.096493 | 0 | 0 | 137.2906 | 4.626% | CZ 5B | 6.8358 | 1.9877 | 0.101 | 0 | 0 | 7.258 | 0 | 12.4541 | 0 | 0 | 2.7503 | 0 | 0 | 0.028281 | 0 | 0 | 31.4152 | 4.626% | CZ 5B | 0 | 0 | -0.0011025 | 0.30212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30102 | 4.626% | CZ 5B | 71.5642 | 20.8094 | 0.93689 | 33.0221 | 0 | 75.9841 | 0 | 130.3815 | 0 | 0 | 28.7927 | 0 | 0 | 0.29607 | 0 | 0 | 361.787 | 4.626%
CZ 5C | 0.72525 | 0.2107 | 0.0091773 | 0.48197 | 0 | 0.015783 | 0 | 1.1791 | 0 | 0 | 0.29343 | 0 | 0 | 0.0030062 | 0 | 0 | 2.9185 | 0.066% | CZ 5C | 23.279 | 6.7631 | 0.19302 | 49.1807 | 0 | 0.50659 | 0 | 37.8478 | 0 | 0 | 9.4184 | 0 | 0 | 0.096493 | 0 | 0 | 127.2852 | 0.066% | CZ 5C | 6.8227 | 1.9822 | 0.099992 | 0 | 0 | 0.14847 | 0 | 11.0926 | 0 | 0 | 2.7604 | 0 | 0 | 0.028281 | 0 | 0 | 22.9345 | 0.066% | CZ 5C | 0 | 0 | -0.0014815 | 0.49181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49033 | 0.066% | CZ 5C | 71.4267 | 20.7513 | 0.88489 | 53.7545 | 0 | 1.5544 | 0 | 116.1279 | 0 | 0 | 28.8985 | 0 | 0 | 0.29607 | 0 | 0 | 293.6943 | 0.066%
CZ 6A | 0.72659 | 0.21119 | 0.0093829 | 0.50068 | 0 | 0.64832 | 0 | 1.2258 | 0 | 0 | 0.29359 | 0 | 0 | 0.0030062 | 0 | 0 | 3.6186 | 3.001% | CZ 6A | 23.3221 | 6.7787 | 0.21025 | 51.0894 | 0 | 20.8098 | 0 | 39.3469 | 0 | 0 | 9.4236 | 0 | 0 | 0.096493 | 0 | 0 | 151.0772 | 3.001% | CZ 6A | 6.8353 | 1.9867 | 0.1005 | 0 | 0 | 6.099 | 0 | 11.5319 | 0 | 0 | 2.7619 | 0 | 0 | 0.028281 | 0 | 0 | 29.3436 | 3.001% | CZ 6A | 0 | 0 | -0.0013265 | 0.51089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50957 | 3.001% | CZ 6A | 71.5589 | 20.7989 | 0.90712 | 55.8408 | 0 | 63.8505 | 0 | 120.7276 | 0 | 0 | 28.9143 | 0 | 0 | 0.29607 | 0 | 0 | 362.8942 | 3.001%
CZ 6B | 0.72756 | 0.21113 | 0.0092279 | 0.42999 | 0 | 0.62615 | 0 | 1.2221 | 0 | 0 | 0.2945 | 0 | 0 | 0.0030062 | 0 | 0 | 3.5237 | 0.4557% | CZ 6B | 23.3531 | 6.7769 | 0.19819 | 43.8766 | 0 | 20.0982 | 0 | 39.228 | 0 | 0 | 9.4529 | 0 | 0 | 0.096493 | 0 | 0 | 143.0804 | 0.4557% | CZ 6B | 6.8444 | 1.9862 | 0.099992 | 0 | 0 | 5.8904 | 0 | 11.4971 | 0 | 0 | 2.7705 | 0 | 0 | 0.028281 | 0 | 0 | 29.1169 | 0.4557% | CZ 6B | 0 | 0 | -0.0014298 | 0.43877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43734 | 0.4557% | CZ 6B | 71.6541 | 20.7936 | 0.89054 | 47.9571 | 0 | 61.667 | 0 | 120.3628 | 0 | 0 | 29.0042 | 0 | 0 | 0.29607 | 0 | 0 | 352.6254 | 0.4557%
CZ 7 | 0.72692 | 0.2106 | 0.009073 | 0.56336 | 0 | 0.58713 | 0 | 1.2242 | 0 | 0 | 0.29525 | 0 | 0 | 0.0030062 | 0 | 0 | 3.6196 | 0.4458% | CZ 7 | 23.3324 | 6.7597 | 0.18613 | 57.4857 | 0 | 18.8455 | 0 | 39.2952 | 0 | 0 | 9.477 | 0 | 0 | 0.096493 | 0 | 0 | 155.4782 | 0.4458% | CZ 7 | 6.8383 | 1.9812 | 0.099487 | 0 | 0 | 5.5233 | 0 | 11.5168 | 0 | 0 | 2.7776 | 0 | 0 | 0.028281 | 0 | 0 | 28.7649 | 0.4458% | CZ 7 | 0 | 0 | -0.0015332 | 0.57486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57332 | 0.4458% | CZ 7 | 71.5906 | 20.7407 | 0.87395 | 62.8319 | 0 | 57.8234 | 0 | 120.569 | 0 | 0 | 29.0782 | 0 | 0 | 0.29607 | 0 | 0 | 363.8039 | 0.4458%
CZ 8 | 0.72058 | 0.20716 | 0.0088197 | 0.71636 | 0 | 0.46908 | 0 | 1.186 | 0 | 0 | 0.29751 | 0 | 0 | 0.0030062 | 0 | 0 | 3.6085 | 0.08738% | CZ 8 | 23.1291 | 6.6494 | 0.16029 | 73.0984 | 0 | 15.0564 | 0 | 38.0666 | 0 | 0 | 9.5494 | 0 | 0 | 0.096493 | 0 | 0 | 165.8061 | 0.08738% | CZ 8 | 6.7788 | 1.9488 | 0.099487 | 0 | 0 | 4.4128 | 0 | 11.1567 | 0 | 0 | 2.7988 | 0 | 0 | 0.028281 | 0 | 0 | 27.2236 | 0.08738% | CZ 8 | 0 | 0 | -0.0017916 | 0.73098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72919 | 0.08738% | CZ 8 | 70.9668 | 20.4024 | 0.84571 | 79.8965 | 0 | 46.1974 | 0 | 116.7994 | 0 | 0 | 29.3003 | 0 | 0 | 0.29607 | 0 | 0 | 364.7045 | 0.08738%
US Weighted | 0.72687 | 0.21163 | 0.010446 | 0.25663 | 0 | 0.88102 | 0 | 1.2199 | 0 | 0 | 0.28797 | 0 | 0 | 0.0030062 | 0 | 0 | 3.5975 | 100% | US Weighted | 23.331 | 6.7927 | 0.30299 | 26.1869 | 0 | 28.2789 | 0 | 39.1564 | 0 | 0 | 9.2431 | 0 | 0 | 0.096493 | 0 | 0 | 133.3886 | 100% | US Weighted | 6.8379 | 1.9908 | 0.10262 | 0 | 0 | 8.2881 | 0 | 11.4761 | 0 | 0 | 2.709 | 0 | 0 | 0.028281 | 0 | 0 | 31.4328 | 100% | US Weighted | 0 | 0 | -0.00047148 | 0.26187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2614 | 100% | US Weighted | 71.5863 | 20.8421 | 1.0228 | 28.6223 | 0 | 86.7679 | 0 | 120.1431 | 0 | 0 | 28.3606 | 0 | 0 | 0.29607 | 0 | 0 | 357.6411 | 100%
Building Type: | Full-service Restaurant |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Full-service Restaurant |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Full-service Restaurant |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 5502 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 5502 | [17 empty] | Prototype Floor Area: | 5502 | Building Type: | Full-service Restaurant | [15 empty] | Prototype Floor Area: | 5502 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 72.88% | 67.94% | 1.662% |  |  | 34.23% |  | 52.71% |  | 0% | 46.84% |  |  | 0.09906% |  |  | 31.29% | 0% | CZ 0A | 72.88% | 67.94% | 1.029% |  |  | 34.23% |  | 52.71% |  | 0% | 46.84% |  |  | 0.06312% |  |  | 26.19% | 0% | CZ 0A | 72.88% | 67.94% | 2.762% |  |  | 34.23% |  | 52.71% |  | 0% | 46.84% |  |  | 0.1341% |  |  | 34.36% | 0% | CZ 0A |  |  | 0.4075% | [10 empty] | 0% |  |  | 0.1283% | 0% | CZ 0A | 72.88% | 67.94% | 1.589% |  |  | 34.23% |  | 52.71% |  | 0% | 46.84% |  |  | 0.09574% |  |  | 30.92% | 0%
CZ 0B | 72.95% | 67.97% | 1.574% | 93.88% |  | 35.05% |  | 58.58% |  | 0% | 47.32% |  |  | 0.09906% |  |  | 32.65% | 0% | CZ 0B | 72.95% | 67.97% | 0.9175% | 93.88% |  | 35.05% |  | 58.58% |  | 0% | 47.32% |  |  | 0.06312% |  |  | 27.09% | 0% | CZ 0B | 72.95% | 67.97% | 2.711% |  |  | 35.05% |  | 58.58% |  | 0% | 47.32% |  |  | 0.1341% |  |  | 36.05% | 0% | CZ 0B |  |  | 0.2702% | 93.88% | [9 empty] | 0% |  |  | 0.1518% | 0% | CZ 0B | 72.95% | 67.97% | 1.499% | 93.88% |  | 35.05% |  | 58.58% |  | 0% | 47.32% |  |  | 0.09574% |  |  | 32.25% | 0%
CZ 1A | 72.89% | 67.97% | 1.494% | 100% |  | 39.98% |  | 71.02% |  | 0% | 47.53% |  |  | 0.09906% |  |  | 35.22% | 3.201% | CZ 1A | 72.89% | 67.97% | 0.831% | 100% |  | 39.98% |  | 71.02% |  | 0% | 47.53% |  |  | 0.06312% |  |  | 28.53% | 3.201% | CZ 1A | 72.89% | 67.97% | 2.723% |  |  | 39.98% |  | 71.02% |  | 0% | 47.53% |  |  | 0.1341% |  |  | 39.47% | 3.201% | CZ 1A |  |  | 0.2081% | 100% | [9 empty] | 0% |  |  | 0.07232% | 3.201% | CZ 1A | 72.89% | 67.97% | 1.416% | 100% |  | 39.98% |  | 71.02% |  | 0% | 47.53% |  |  | 0.09574% |  |  | 34.73% | 3.201%
CZ 1B | 72.85% | 67.98% | 1.445% | 59.68% |  | 38.17% |  | 60.72% |  | 0% | 47.75% |  |  | 0.09906% |  |  | 33.85% | 0% | CZ 1B | 72.85% | 67.98% | 0.7759% | 59.68% |  | 38.17% |  | 60.72% |  | 0% | 47.75% |  |  | 0.06312% |  |  | 27.9% | 0% | CZ 1B | 72.85% | 67.98% | 2.685% |  |  | 38.17% |  | 60.72% |  | 0% | 47.75% |  |  | 0.1341% |  |  | 37.63% | 0% | CZ 1B |  |  | 0.1484% | 59.68% | [9 empty] | 0% |  |  | 2.313% | 0% | CZ 1B | 72.85% | 67.98% | 1.366% | 59.68% |  | 38.17% |  | 60.72% |  | 0% | 47.75% |  |  | 0.09574% |  |  | 33.41% | 0%
CZ 2A | 73.04% | 67.99% | 1.388% | 56.72% |  | 41.48% |  | 62.08% |  | 0% | 47.81% |  |  | 0.09906% |  |  | 34.37% | 18.21% | CZ 2A | 73.04% | 67.99% | 0.7282% | 56.72% |  | 41.48% |  | 62.08% |  | 0% | 47.81% |  |  | 0.06312% |  |  | 28.1% | 18.21% | CZ 2A | 73.04% | 67.99% | 2.697% |  |  | 41.48% |  | 62.08% |  | 0% | 47.81% |  |  | 0.1341% |  |  | 38.52% | 18.21% | CZ 2A |  |  | 0.1358% | 56.72% | [9 empty] | 0% |  |  | 4.708% | 18.21% | CZ 2A | 73.04% | 67.99% | 1.309% | 56.72% |  | 41.48% |  | 62.08% |  | 0% | 47.81% |  |  | 0.09574% |  |  | 33.89% | 18.21%
CZ 2B | 73.04% | 67.98% | 1.286% | 56.53% |  | 49.19% |  | 66.42% |  | 0% | 48.58% |  |  | 0.09906% |  |  | 37.19% | 2.812% | CZ 2B | 73.04% | 67.98% | 0.6096% | 56.53% |  | 49.19% |  | 66.42% |  | 0% | 48.58% |  |  | 0.06312% |  |  | 29.99% | 2.812% | CZ 2B | 73.04% | 67.98% | 2.634% |  |  | 49.19% |  | 66.42% |  | 0% | 48.58% |  |  | 0.1341% |  |  | 42.03% | 2.812% | CZ 2B |  |  | 0.003863% | 56.53% | [9 empty] | 0% |  |  | 4.053% | 2.812% | CZ 2B | 73.04% | 67.98% | 1.205% | 56.53% |  | 49.19% |  | 66.42% |  | 0% | 48.58% |  |  | 0.09574% |  |  | 36.64% | 2.812%
CZ 3A | 73% | 67.97% | 1.178% | 37.83% |  | 50.22% |  | 64.73% |  | 0% | 48.77% |  |  | 0.09906% |  |  | 35.43% | 17.3% | CZ 3A | 73% | 67.97% | 0.5145% | 37.83% |  | 50.22% |  | 64.73% |  | 0% | 48.77% |  |  | 0.06312% |  |  | 28.45% | 17.3% | CZ 3A | 73% | 67.97% | 2.645% |  |  | 50.22% |  | 64.73% |  | 0% | 48.77% |  |  | 0.1341% |  |  | 40.78% | 17.3% | CZ 3A |  |  | -0.04395% | 37.83% | [9 empty] | 0% |  |  | 10.05% | 17.3% | CZ 3A | 73% | 67.97% | 1.096% | 37.83% |  | 50.22% |  | 64.73% |  | 0% | 48.77% |  |  | 0.09574% |  |  | 34.86% | 17.3%
CZ 3B | 72.92% | 67.97% | 1.166% | 40.86% |  | 39.29% |  | 66.65% |  | 0% | 48.88% |  |  | 0.09906% |  |  | 34.08% | 8.647% | CZ 3B | 72.92% | 67.97% | 0.4955% | 40.86% |  | 39.29% |  | 66.65% |  | 0% | 48.88% |  |  | 0.06312% |  |  | 27.01% | 8.647% | CZ 3B | 72.92% | 67.97% | 2.608% |  |  | 39.29% |  | 66.65% |  | 0% | 48.88% |  |  | 0.1341% |  |  | 39.27% | 8.647% | CZ 3B |  |  | -0.07696% | 40.86% | [9 empty] | 0% |  |  | 6.51% | 8.647% | CZ 3B | 72.92% | 67.97% | 1.083% | 40.86% |  | 39.29% |  | 66.65% |  | 0% | 48.88% |  |  | 0.09574% |  |  | 33.51% | 8.647%
CZ 3C | 72.76% | 67.86% | 1.236% | 55.37% |  | 37.43% |  | 75.77% |  | 0% | 48.32% |  |  | 0.09906% |  |  | 34.3% | 1.321% | CZ 3C | 72.76% | 67.86% | 0.588% | 55.37% |  | 37.43% |  | 75.77% |  | 0% | 48.32% |  |  | 0.06312% |  |  | 26.34% | 1.321% | CZ 3C | 72.76% | 67.86% | 2.684% |  |  | 37.43% |  | 75.77% |  | 0% | 48.32% |  |  | 0.1341% |  |  | 40.35% | 1.321% | CZ 3C |  |  | 0.04664% | 55.37% | [9 empty] | 0% |  |  | 5.052% | 1.321% | CZ 3C | 72.76% | 67.86% | 1.155% | 55.37% |  | 37.43% |  | 75.77% |  | 0% | 48.32% |  |  | 0.09574% |  |  | 33.65% | 1.321%
CZ 4A | 72.8% | 67.77% | 1.023% | 38.97% |  | 55.53% |  | 73.5% |  | 0% | 49.57% |  |  | 0.09906% |  |  | 36.59% | 16.82% | CZ 4A | 72.8% | 67.77% | 0.3646% | 38.97% |  | 55.53% |  | 73.5% |  | 0% | 49.57% |  |  | 0.06312% |  |  | 29.83% | 16.82% | CZ 4A | 72.8% | 67.77% | 2.594% |  |  | 55.53% |  | 73.5% |  | 0% | 49.57% |  |  | 0.1341% |  |  | 42.7% | 16.82% | CZ 4A |  |  | -0.1658% | 38.97% | [9 empty] | 0% |  |  | 16.59% | 16.82% | CZ 4A | 72.8% | 67.77% | 0.9393% | 38.97% |  | 55.53% |  | 73.5% |  | 0% | 49.57% |  |  | 0.09574% |  |  | 35.98% | 16.82%
CZ 4B | 73% | 67.95% | 1.076% | 40.26% |  | 38.16% |  | 68.21% |  | 0% | 49.27% |  |  | 0.09906% |  |  | 34.06% | 0.7787% | CZ 4B | 73% | 67.95% | 0.4155% | 40.26% |  | 38.16% |  | 68.21% |  | 0% | 49.27% |  |  | 0.06312% |  |  | 27.16% | 0.7787% | CZ 4B | 73% | 67.95% | 2.619% |  |  | 38.16% |  | 68.21% |  | 0% | 49.27% |  |  | 0.1341% |  |  | 39.7% | 0.7787% | CZ 4B |  |  | -0.1229% | 40.26% | [9 empty] | 0% |  |  | 11.02% | 0.7787% | CZ 4B | 73% | 67.95% | 0.9927% | 40.26% |  | 38.16% |  | 68.21% |  | 0% | 49.27% |  |  | 0.09574% |  |  | 33.48% | 0.7787%
CZ 4C | 72.76% | 67.71% | 0.9929% | 48.44% |  | 32.23% |  | 74.97% |  | 0% | 49.66% |  |  | 0.09906% |  |  | 34.31% | 2.174% | CZ 4C | 72.76% | 67.71% | 0.3372% | 48.44% |  | 32.23% |  | 74.97% |  | 0% | 49.66% |  |  | 0.06312% |  |  | 28.53% | 2.174% | CZ 4C | 72.76% | 67.71% | 2.594% |  |  | 32.23% |  | 74.97% |  | 0% | 49.66% |  |  | 0.1341% |  |  | 39.78% | 2.174% | CZ 4C |  |  | -0.1852% | 48.44% | [9 empty] | 0% |  |  | 17.9% | 2.174% | CZ 4C | 72.76% | 67.71% | 0.9094% | 48.44% |  | 32.23% |  | 74.97% |  | 0% | 49.66% |  |  | 0.09574% |  |  | 33.79% | 2.174%
CZ 5A | 72.93% | 67.88% | 0.9384% | 32.67% |  | 65.09% |  | 73.48% |  | 0% | 49.99% |  |  | 0.09906% |  |  | 35.82% | 20.06% | CZ 5A | 72.93% | 67.88% | 0.2964% | 32.67% |  | 65.09% |  | 73.48% |  | 0% | 49.99% |  |  | 0.06312% |  |  | 28.53% | 20.06% | CZ 5A | 72.93% | 67.88% | 2.568% |  |  | 65.09% |  | 73.48% |  | 0% | 49.99% |  |  | 0.1341% |  |  | 43.31% | 20.06% | CZ 5A |  |  | -0.205% | 32.67% | [9 empty] | 0% |  |  | 16.56% | 20.06% | CZ 5A | 72.93% | 67.88% | 0.8558% | 32.67% |  | 65.09% |  | 73.48% |  | 0% | 49.99% |  |  | 0.09574% |  |  | 35.13% | 20.06%
CZ 5B | 72.91% | 67.82% | 0.9687% | 32.47% |  | 67.82% |  | 66.91% |  | 0% | 49.93% |  |  | 0.09906% |  |  | 36.51% | 4.626% | CZ 5B | 72.91% | 67.82% | 0.3227% | 32.47% |  | 67.82% |  | 66.91% |  | 0% | 49.93% |  |  | 0.06312% |  |  | 28.64% | 4.626% | CZ 5B | 72.91% | 67.82% | 2.581% |  |  | 67.82% |  | 66.91% |  | 0% | 49.93% |  |  | 0.1341% |  |  | 43.54% | 4.626% | CZ 5B |  |  | -0.186% | 32.47% | [9 empty] | 0% |  |  | 12.91% | 4.626% | CZ 5B | 72.91% | 67.82% | 0.8859% | 32.47% |  | 67.82% |  | 66.91% |  | 0% | 49.93% |  |  | 0.09574% |  |  | 35.81% | 4.626%
CZ 5C | 72.77% | 67.73% | 0.9126% | 46.93% |  | 17.82% |  | 74.11% |  | 0% | 50.08% |  |  | 0.09906% |  |  | 33.77% | 0.066% | CZ 5C | 72.77% | 67.73% | 0.2626% | 46.93% |  | 17.82% |  | 74.11% |  | 0% | 50.08% |  |  | 0.06312% |  |  | 28.54% | 0.066% | CZ 5C | 72.77% | 67.73% | 2.555% |  |  | 17.82% |  | 74.11% |  | 0% | 50.08% |  |  | 0.1341% |  |  | 39.11% | 0.066% | CZ 5C |  |  | -0.2463% | 46.93% | [9 empty] | 0% |  |  | 19.94% | 0.066% | CZ 5C | 72.77% | 67.73% | 0.8291% | 46.93% |  | 17.82% |  | 74.11% |  | 0% | 50.08% |  |  | 0.09574% |  |  | 33.27% | 0.066%
CZ 6A | 72.91% | 67.82% | 0.9016% | 26.21% |  | 62.57% |  | 72.46% |  | 0% | 50.14% |  |  | 0.09906% |  |  | 34.11% | 3.001% | CZ 6A | 72.91% | 67.82% | 0.2727% | 26.21% |  | 62.57% |  | 72.46% |  | 0% | 50.14% |  |  | 0.06312% |  |  | 26.35% | 3.001% | CZ 6A | 72.91% | 67.82% | 2.568% |  |  | 62.57% |  | 72.46% |  | 0% | 50.14% |  |  | 0.1341% |  |  | 42.84% | 3.001% | CZ 6A |  |  | -0.2081% | 26.21% | [9 empty] | 0% |  |  | 15.01% | 3.001% | CZ 6A | 72.91% | 67.82% | 0.8199% | 26.21% |  | 62.57% |  | 72.46% |  | 0% | 50.14% |  |  | 0.09574% |  |  | 33.35% | 3.001%
CZ 6B | 73% | 67.85% | 0.8937% | 30.1% |  | 71.36% |  | 66.05% |  | 0% | 50.32% |  |  | 0.09906% |  |  | 34.82% | 0.4557% | CZ 6B | 73% | 67.85% | 0.2599% | 30.1% |  | 71.36% |  | 66.05% |  | 0% | 50.32% |  |  | 0.06312% |  |  | 27.34% | 0.4557% | CZ 6B | 73% | 67.85% | 2.555% |  |  | 71.36% |  | 66.05% |  | 0% | 50.32% |  |  | 0.1341% |  |  | 42.51% | 0.4557% | CZ 6B |  |  | -0.2273% | 30.1% | [9 empty] | 0% |  |  | 15.1% | 0.4557% | CZ 6B | 73% | 67.85% | 0.8115% | 30.1% |  | 71.36% |  | 66.05% |  | 0% | 50.32% |  |  | 0.09574% |  |  | 34.12% | 0.4557%
CZ 7 | 72.94% | 67.72% | 0.8413% | 23.73% |  | 68.17% |  | 72.5% |  | 0% | 50.43% |  |  | 0.09906% |  |  | 33.11% | 0.4458% | CZ 7 | 72.94% | 67.72% | 0.2299% | 23.73% |  | 68.17% |  | 72.5% |  | 0% | 50.43% |  |  | 0.06312% |  |  | 25.13% | 0.4458% | CZ 7 | 72.94% | 67.72% | 2.542% |  |  | 68.17% |  | 72.5% |  | 0% | 50.43% |  |  | 0.1341% |  |  | 43.05% | 0.4458% | CZ 7 |  |  | -0.2268% | 23.73% | [9 empty] | 0% |  |  | 14.67% | 0.4458% | CZ 7 | 72.94% | 67.72% | 0.7609% | 23.73% |  | 68.17% |  | 72.5% |  | 0% | 50.43% |  |  | 0.09574% |  |  | 32.29% | 0.4458%
CZ 8 | 72.3% | 66.98% | 0.7809% | 21.82% |  | 84% |  | 71.86% |  | 0% | 50.85% |  |  | 0.09906% |  |  | 31.24% | 0.08738% | CZ 8 | 72.3% | 66.98% | 0.1861% | 21.82% |  | 84% |  | 71.86% |  | 0% | 50.85% |  |  | 0.06312% |  |  | 23.49% | 0.08738% | CZ 8 | 72.3% | 66.98% | 2.542% |  |  | 84% |  | 71.86% |  | 0% | 50.85% |  |  | 0.1341% |  |  | 42.81% | 0.08738% | CZ 8 |  |  | -0.2462% | 21.82% | [9 empty] | 0% |  |  | 14.92% | 0.08738% | CZ 8 | 72.3% | 66.98% | 0.7017% | 21.82% |  | 84% |  | 71.86% |  | 0% | 50.85% |  |  | 0.09574% |  |  | 30.39% | 0.08738%
US Weighted | 72.93% | 67.9% | 1.129% | 42.98% | 0% | 51.92% | 0% | 68.67% | 0% | 0% | 49.07% | 0% | 0% | 0.09906% | 0% | 0% | 35.38% | 100% | US Weighted | 72.93% | 67.9% | 0.4729% | 42.98% | 0% | 51.92% | 0% | 68.67% | 0% | 0% | 49.07% | 0% | 0% | 0.06312% | 0% | 0% | 28.44% | 100% | US Weighted | 72.93% | 67.9% | 2.622% | 0% | 0% | 51.92% | 0% | 68.67% | 0% | 0% | 49.07% | 0% | 0% | 0.1341% | 0% | 0% | 41.23% | 100% | US Weighted | 0% | 0% | -0.07341% | 42.98% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 11.14% | 100% | US Weighted | 72.93% | 67.9% | 1.047% | 42.98% | 0% | 51.92% | 0% | 68.67% | 0% | 0% | 49.07% | 0% | 0% | 0.09574% | 0% | 0% | 34.79% | 100%

## AptMR
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 33741 |  | Building Type: | Mid-rise Apartment |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 |  | Building Type: | Mid-rise Apartment |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | Mid-rise Apartment |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | Mid-rise Apartment | [14 empty] | Prototype Floor Area: | 33741 |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [18 empty] | End Use by 90.1 edition:
STD2019 | 0.073032 | 0.022706 | 0.33122 | 0.027212 | 0 | 0.1076 | 0 | 0.069285 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0784 |  | STD2019 | 2.3442 | 0.7288 | 10.6314 | 2.7767 | 0 | 3.4537 | 0 | 2.2239 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 36.5187 |  | STD2019 | 0.68704 | 0.2136 | 3.1159 | 0 | 0 | 1.0122 | 0 | 0.65179 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.8892 |  | STD2019 | 0 | 0 | 0 | 0.027767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027767 |  | STD2019 | 7.1926 | 2.2362 | 32.6201 | 3.0349 | 0 | 10.5969 | 0 | 6.8235 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 106.5651
STD2016 | 0.089384 | 0.022706 | 0.33135 | 0.032266 | 0 | 0.11434 | 0 | 0.071086 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1085 |  | STD2016 | 2.869 | 0.7288 | 10.6356 | 3.2925 | 0 | 3.6702 | 0 | 2.2817 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 37.8379 |  | STD2016 | 0.84087 | 0.2136 | 3.1171 | 0 | 0 | 1.0757 | 0 | 0.66873 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.1247 |  | STD2016 | 0 | 0 | 0 | 0.032925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032925 |  | STD2016 | 8.803 | 2.2362 | 32.6331 | 3.5987 | 0 | 11.2612 | 0 | 7.001 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 109.5939
STD2013 | 0.1139 | 0.034495 | 0.33132 | 0.031332 | 0 | 0.11881 | 0 | 0.073144 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1504 |  | STD2013 | 3.656 | 1.1072 | 10.6345 | 3.1972 | 0 | 3.8136 | 0 | 2.3478 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 39.1163 |  | STD2013 | 1.0715 | 0.32451 | 3.1168 | 0 | 0 | 1.1177 | 0 | 0.68809 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.5273 |  | STD2013 | 0 | 0 | 0 | 0.031972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031972 |  | STD2013 | 11.2178 | 3.3973 | 32.6297 | 3.4945 | 0 | 11.7012 | 0 | 7.2036 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 113.7049
STD2010 | 0.13482 | 0.034495 | 0.33193 | 0.067148 | 0 | 0.1446 | 0 | 0.081396 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.2421 |  | STD2010 | 4.3276 | 1.1072 | 10.6543 | 6.8518 | 0 | 4.6414 | 0 | 2.6126 | 0 | 0 | 0 | 3.5203 | 0 | 0 | 0 | 10.849 | 44.5643 |  | STD2010 | 1.2683 | 0.32451 | 3.1226 | 0 | 0 | 1.3603 | 0 | 0.76572 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 11.0529 |  | STD2010 | 0 | 0 | 0 | 0.068518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068518 |  | STD2010 | 13.2783 | 3.3973 | 32.6904 | 7.489 | 0 | 14.2411 | 0 | 8.0164 | 0 | 0 | 0 | 10.8014 | 0 | 0 | 0 | 33.2879 | 123.2017
STD2007 | 0.12208 | 0.06384 | 0.33206 | 0.089143 | 0 | 0.14384 | 0 | 0.084313 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2884 |  | STD2007 | 3.9185 | 2.0491 | 10.6583 | 9.0962 | 0 | 4.6168 | 0 | 2.7063 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9035 | 47.5896 |  | STD2007 | 1.1484 | 0.60057 | 3.1238 | 0 | 0 | 1.3531 | 0 | 0.79316 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1956 | 11.2818 |  | STD2007 | 0 | 0 | 0 | 0.090962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090962 |  | STD2007 | 12.023 | 6.2873 | 32.7028 | 9.9421 | 0 | 14.1658 | 0 | 8.3036 | 0 | 0 | 0 | 11.1712 | 0 | 0 | 0 | 33.4551 | 128.0511
STD2004 | 0.12208 | 0.06384 | 0.33212 | 0.10226 | 0 | 0.18221 | 0 | 0.08798 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3436 |  | STD2004 | 3.9185 | 2.0491 | 10.6602 | 10.4345 | 0 | 5.8486 | 0 | 2.824 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9035 | 50.2793 |  | STD2004 | 1.1484 | 0.60057 | 3.1243 | 0 | 0 | 1.7141 | 0 | 0.82766 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1956 | 11.6778 |  | STD2004 | 0 | 0 | 0 | 0.10435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10435 |  | STD2004 | 12.023 | 6.2873 | 32.7087 | 11.4049 | 0 | 17.9452 | 0 | 8.6648 | 0 | 0 | 0 | 11.1712 | 0 | 0 | 0 | 33.4551 | 133.6603
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions:
2004-2007 | 0 | 0 | 5.9784e-05 | 0.013116 | 0 | 0.038375 | 0 | 0.0036674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.055218 |  | 2004-2007 | 0 | 0 | 0.001919 | 1.3383 | 0 | 1.2318 | 0 | 0.11772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6897 |  | 2004-2007 | 0 | 0 | 0.00056241 | 0 | 0 | 0.36101 | 0 | 0.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39607 |  | 2004-2007 | 0 | 0 | 0 | 0.013383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013383 |  | 2004-2007 | 0 | 0 | 0.0058879 | 1.4628 | 0 | 3.7794 | 0 | 0.36119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6093
2007-2010 | -0.012745 | 0.029345 | 0.00012555 | 0.021995 | 0 | -0.00076472 | 0 | 0.0029166 | 0 | 0 | 0 | 0.0037553 | 0 | 0 | 0 | 0.0016982 | 0.046326 |  | 2007-2010 | -0.4091 | 0.94192 | 0.0040299 | 2.2444 | 0 | -0.024546 | 0 | 0.093616 | 0 | 0 | 0 | 0.12054 | 0 | 0 | 0 | 0.054509 | 3.0253 |  | 2007-2010 | -0.1199 | 0.27606 | 0.0011811 | 0 | 0 | -0.007194 | 0 | 0.027437 | 0 | 0 | 0 | 0.035328 | 0 | 0 | 0 | 0.015976 | 0.22889 |  | 2007-2010 | 0 | 0 | 0 | 0.022444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022444 |  | 2007-2010 | -1.2552 | 2.8901 | 0.012365 | 2.4531 | 0 | -0.075314 | 0 | 0.28724 | 0 | 0 | 0 | 0.36985 | 0 | 0 | 0 | 0.16725 | 4.8493
2010-2013 | 0.020921 | 0 | 0.00061657 | 0.035816 | 0 | 0.02579 | 0 | 0.0082522 | 0 | 0 | 0 | 0.00028887 | 0 | 0 | 0 | 0 | 0.091685 |  | 2010-2013 | 0.67153 | 0 | 0.019791 | 3.6546 | 0 | 0.8278 | 0 | 0.26488 | 0 | 0 | 0 | 0.0092722 | 0 | 0 | 0 | 0 | 5.4479 |  | 2010-2013 | 0.19681 | 0 | 0.0058003 | 0 | 0 | 0.24262 | 0 | 0.077632 | 0 | 0 | 0 | 0.0027175 | 0 | 0 | 0 | 0 | 0.52558 |  | 2010-2013 | 0 | 0 | 0 | 0.036546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036546 |  | 2010-2013 | 2.0604 | 0 | 0.060723 | 3.9945 | 0 | 2.5399 | 0 | 0.81273 | 0 | 0 | 0 | 0.02845 | 0 | 0 | 0 | 0 | 9.4968
2013-2016 | 0.024519 | 0.01179 | -3.3803e-05 | -0.00093395 | 0 | 0.0044672 | 0 | 0.0020578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041866 |  | 2013-2016 | 0.78701 | 0.37842 | -0.001085 | -0.095301 | 0 | 0.14339 | 0 | 0.066052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2785 |  | 2013-2016 | 0.23066 | 0.11091 | -0.000318 | 0 | 0 | 0.042025 | 0 | 0.019359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40263 |  | 2013-2016 | 0 | 0 | 0 | -0.00095301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.00095301 |  | 2013-2016 | 2.4148 | 1.1611 | -0.0033291 | -0.10416 | 0 | 0.43996 | 0 | 0.20267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.111
2016-2019 | 0.016352 | 0 | 0.0001312 | 0.0050545 | 0 | 0.0067452 | 0 | 0.0018015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030084 |  | 2016-2019 | 0.52486 | 0 | 0.0042113 | 0.51577 | 0 | 0.21651 | 0 | 0.057824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3192 |  | 2016-2019 | 0.15383 | 0 | 0.0012343 | 0 | 0 | 0.063454 | 0 | 0.016947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23546 |  | 2016-2019 | 0 | 0 | 0 | 0.0051577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0051577 |  | 2016-2019 | 1.6104 | 0 | 0.012922 | 0.56374 | 0 | 0.66431 | 0 | 0.17742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0288
2004-2019 | 0.049047 | 0.041135 | 0.00089931 | 0.075047 | 0 | 0.074613 | 0 | 0.018696 | 0 | 0 | 0 | 0.0040442 | 0 | 0 | 0 | 0.0016982 | 0.26518 |  | 2004-2019 | 1.5743 | 1.3203 | 0.028866 | 7.6578 | 0 | 2.3949 | 0 | 0.60009 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 13.7606 |  | 2004-2019 | 0.4614 | 0.38697 | 0.0084601 | 0 | 0 | 0.70191 | 0 | 0.17588 | 0 | 0 | 0 | 0.038045 | 0 | 0 | 0 | 0.015976 | 1.7886 |  | 2004-2019 | 0 | 0 | 0 | 0.076578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076578 |  | 2004-2019 | 4.8304 | 4.0512 | 0.088568 | 8.37 | 0 | 7.3483 | 0 | 1.8412 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 27.0952
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | 0.018% | 12.83% |  | 21.06% |  | 4.168% |  |  |  | 0% |  |  |  | 0% | 4.11% |  | 2004-2007 | 0% | 0% | 0.018% | 12.83% |  | 21.06% |  | 4.168% |  |  |  | 0% |  |  |  | 0% | 5.35% |  | 2004-2007 | 0% | 0% | 0.018% |  |  | 21.06% |  | 4.168% |  |  |  | 0% |  |  |  | 0% | 3.392% |  | 2004-2007 |  |  |  | 12.83% | [12 empty] | 12.83% |  | 2004-2007 | 0% | 0% | 0.018% | 12.83% |  | 21.06% |  | 4.168% |  |  |  | 0% |  |  |  | 0% | 4.197%
2007-2010 | -10.44% | 45.97% | 0.03781% | 24.67% |  | -0.5317% |  | 3.459% |  |  |  | 3.311% |  |  |  | 0.4999% | 3.596% |  | 2007-2010 | -10.44% | 45.97% | 0.03781% | 24.67% |  | -0.5317% |  | 3.459% |  |  |  | 3.311% |  |  |  | 0.4999% | 6.357% |  | 2007-2010 | -10.44% | 45.97% | 0.03781% |  |  | -0.5317% |  | 3.459% |  |  |  | 3.311% |  |  |  | 0.4999% | 2.029% |  | 2007-2010 |  |  |  | 24.67% | [12 empty] | 24.67% |  | 2007-2010 | -10.44% | 45.97% | 0.03781% | 24.67% |  | -0.5317% |  | 3.459% |  |  |  | 3.311% |  |  |  | 0.4999% | 3.787%
2010-2013 | 15.52% | 0% | 0.1858% | 53.34% |  | 17.84% |  | 10.14% |  |  |  | 0.2634% |  |  |  | 0% | 7.382% |  | 2010-2013 | 15.52% | 0% | 0.1858% | 53.34% |  | 17.84% |  | 10.14% |  |  |  | 0.2634% |  |  |  | 0% | 12.22% |  | 2010-2013 | 15.52% | 0% | 0.1858% |  |  | 17.84% |  | 10.14% |  |  |  | 0.2634% |  |  |  | 0% | 4.755% |  | 2010-2013 |  |  |  | 53.34% | [12 empty] | 53.34% |  | 2010-2013 | 15.52% | 0% | 0.1858% | 53.34% |  | 17.84% |  | 10.14% |  |  |  | 0.2634% |  |  |  | 0% | 7.708%
2013-2016 | 21.53% | 34.18% | -0.0102% | -2.981% |  | 3.76% |  | 2.813% |  |  |  | 0% |  |  |  | 0% | 3.639% |  | 2013-2016 | 21.53% | 34.18% | -0.0102% | -2.981% |  | 3.76% |  | 2.813% |  |  |  | 0% |  |  |  | 0% | 3.268% |  | 2013-2016 | 21.53% | 34.18% | -0.0102% |  |  | 3.76% |  | 2.813% |  |  |  | 0% |  |  |  | 0% | 3.825% |  | 2013-2016 |  |  |  | -2.981% | [12 empty] | -2.981% |  | 2013-2016 | 21.53% | 34.18% | -0.0102% | -2.981% |  | 3.76% |  | 2.813% |  |  |  | 0% |  |  |  | 0% | 3.616%
2016-2019 | 18.29% | 0% | 0.0396% | 15.67% |  | 5.899% |  | 2.534% |  |  |  | 0% |  |  |  | 0% | 2.714% |  | 2016-2019 | 18.29% | 0% | 0.0396% | 15.67% |  | 5.899% |  | 2.534% |  |  |  | 0% |  |  |  | 0% | 3.486% |  | 2016-2019 | 18.29% | 0% | 0.0396% |  |  | 5.899% |  | 2.534% |  |  |  | 0% |  |  |  | 0% | 2.326% |  | 2016-2019 |  |  |  | 15.67% | [12 empty] | 15.67% |  | 2016-2019 | 18.29% | 0% | 0.0396% | 15.67% |  | 5.899% |  | 2.534% |  |  |  | 0% |  |  |  | 0% | 2.764%
2004-2019 | 40.18% | 64.43% | 0.2708% | 73.39% |  | 40.95% |  | 21.25% |  |  |  | 3.565% |  |  |  | 0.4999% | 19.74% |  | 2004-2019 | 40.18% | 64.43% | 0.2708% | 73.39% |  | 40.95% |  | 21.25% |  |  |  | 3.565% |  |  |  | 0.4999% | 27.37% |  | 2004-2019 | 40.18% | 64.43% | 0.2708% |  |  | 40.95% |  | 21.25% |  |  |  | 3.565% |  |  |  | 0.4999% | 15.32% |  | 2004-2019 |  |  |  | 73.39% | [12 empty] | 73.39% |  | 2004-2019 | 40.18% | 64.43% | 0.2708% | 73.39% |  | 40.95% |  | 21.25% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.27%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail:
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.073033 | 0.022742 | 0.24083 | 0 | 0 | 0.34774 | 0 | 0.1131 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2448 | 0% | CZ 0A | 2.3442 | 0.72998 | 7.73 | 0 | 0 | 11.1618 | 0 | 3.6302 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 39.9564 | 0% | CZ 0A | 0.68704 | 0.21394 | 2.2655 | 0 | 0 | 3.2713 | 0 | 1.064 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 11.7106 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 7.1927 | 2.2398 | 23.7178 | 0 | 0 | 34.2477 | 0 | 11.1386 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 122.5979 | 0%
CZ 0B | 0.073033 | 0.022751 | 0.23975 | 0 | 0 | 0.33386 | 0 | 0.11581 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2326 | 0% | CZ 0B | 2.3442 | 0.73026 | 7.6954 | 0 | 0 | 10.7162 | 0 | 3.7173 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 39.5636 | 0% | CZ 0B | 0.68704 | 0.21403 | 2.2554 | 0 | 0 | 3.1407 | 0 | 1.0895 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 11.5954 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 7.1927 | 2.2407 | 23.6118 | 0 | 0 | 32.8804 | 0 | 11.4059 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 121.3926 | 0%
CZ 1A | 0.073033 | 0.022751 | 0.259 | 0 | 0 | 0.24346 | 0 | 0.096204 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1418 | 2.646% | CZ 1A | 2.3442 | 0.73026 | 8.3133 | 0 | 0 | 7.8146 | 0 | 3.0879 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 36.6505 | 2.646% | CZ 1A | 0.68704 | 0.21403 | 2.4365 | 0 | 0 | 2.2903 | 0 | 0.90502 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.7416 | 2.646% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.646% | CZ 1A | 7.1927 | 2.2407 | 25.5076 | 0 | 0 | 23.9773 | 0 | 9.4747 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 112.4542 | 2.646%
CZ 1B | 0.073033 | 0.022725 | 0.25989 | 0.00039091 | 0 | 0.25902 | 0 | 0.10395 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1664 | 0% | CZ 1B | 2.3442 | 0.72942 | 8.3419 | 0.039889 | 0 | 8.3138 | 0 | 3.3366 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 37.4661 | 0% | CZ 1B | 0.68704 | 0.21378 | 2.4449 | 0 | 0 | 2.4367 | 0 | 0.9779 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.969 | 0% | CZ 1B | 0 | 0 | 0 | 0.00039889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00039889 | 0% | CZ 1B | 7.1927 | 2.2381 | 25.5955 | 0.043599 | 0 | 25.5093 | 0 | 10.2377 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 114.8781 | 0%
CZ 2A | 0.073033 | 0.022716 | 0.28034 | 0.00054232 | 0 | 0.19597 | 0 | 0.082338 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1023 | 16.39% | CZ 2A | 2.3442 | 0.72914 | 8.9983 | 0.055339 | 0 | 6.2902 | 0 | 2.6429 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 35.4203 | 16.39% | CZ 2A | 0.68704 | 0.2137 | 2.6373 | 0 | 0 | 1.8436 | 0 | 0.77458 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.3649 | 16.39% | CZ 2A | 0 | 0 | 0 | 0.00055339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00055339 | 16.39% | CZ 2A | 7.1927 | 2.2372 | 27.6094 | 0.060486 | 0 | 19.3003 | 0 | 8.1091 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 108.5704 | 16.39%
CZ 2B | 0.073033 | 0.022734 | 0.28183 | 0.00080385 | 0 | 0.17783 | 0 | 0.090996 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0946 | 1.974% | CZ 2B | 2.3442 | 0.7297 | 9.0461 | 0.082026 | 0 | 5.7081 | 0 | 2.9208 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 35.191 | 1.974% | CZ 2B | 0.68704 | 0.21386 | 2.6513 | 0 | 0 | 1.6729 | 0 | 0.85603 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.2899 | 1.974% | CZ 2B | 0 | 0 | 0 | 0.00082026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00082026 | 1.974% | CZ 2B | 7.1927 | 2.2389 | 27.756 | 0.089654 | 0 | 17.514 | 0 | 8.9617 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 107.8142 | 1.974%
CZ 3A | 0.073033 | 0.022725 | 0.3171 | 0.011626 | 0 | 0.11656 | 0 | 0.068752 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0572 | 12.99% | CZ 3A | 2.3442 | 0.72942 | 10.1781 | 1.1863 | 0 | 3.7412 | 0 | 2.2068 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 34.7463 | 12.99% | CZ 3A | 0.68704 | 0.21378 | 2.983 | 0 | 0 | 1.0965 | 0 | 0.64678 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.8359 | 12.99% | CZ 3A | 0 | 0 | 0 | 0.011863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011863 | 12.99% | CZ 3A | 7.1927 | 2.2381 | 31.2295 | 1.2966 | 0 | 11.4791 | 0 | 6.7711 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 104.2683 | 12.99%
CZ 3B | 0.073033 | 0.022725 | 0.30762 | 0.0029319 | 0 | 0.13313 | 0 | 0.08176 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0686 | 8.593% | CZ 3B | 2.3442 | 0.72942 | 9.8738 | 0.29917 | 0 | 4.2731 | 0 | 2.6243 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 34.5043 | 8.593% | CZ 3B | 0.68704 | 0.21378 | 2.8939 | 0 | 0 | 1.2524 | 0 | 0.76915 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.0249 | 8.593% | CZ 3B | 0 | 0 | 0 | 0.0029917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029917 | 8.593% | CZ 3B | 7.1927 | 2.2381 | 30.2958 | 0.32699 | 0 | 13.1111 | 0 | 8.0522 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 105.2781 | 8.593%
CZ 3C | 0.073033 | 0.022725 | 0.32091 | 0.0017977 | 0 | 0.058992 | 0 | 0.052847 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 0.97769 | 3.597% | CZ 3C | 2.3442 | 0.72942 | 10.3004 | 0.18343 | 0 | 1.8935 | 0 | 1.6963 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 31.5074 | 3.597% | CZ 3C | 0.68704 | 0.21378 | 3.0189 | 0 | 0 | 0.55496 | 0 | 0.49715 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.1805 | 3.597% | CZ 3C | 0 | 0 | 0 | 0.0018343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018343 | 3.597% | CZ 3C | 7.1927 | 2.2381 | 31.6045 | 0.20049 | 0 | 5.8098 | 0 | 5.2046 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 96.3114 | 3.597%
CZ 4A | 0.073033 | 0.02269 | 0.34618 | 0.034808 | 0 | 0.083529 | 0 | 0.063054 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0707 | 22.03% | CZ 4A | 2.3442 | 0.72829 | 11.1115 | 3.5518 | 0 | 2.6811 | 0 | 2.0239 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 36.801 | 22.03% | CZ 4A | 0.68704 | 0.21345 | 3.2566 | 0 | 0 | 0.78578 | 0 | 0.59317 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.7448 | 22.03% | CZ 4A | 0 | 0 | 0 | 0.035518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035518 | 22.03% | CZ 4A | 7.1927 | 2.2346 | 34.0934 | 3.8821 | 0 | 8.2264 | 0 | 6.2099 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 105.9003 | 22.03%
CZ 4B | 0.073033 | 0.022707 | 0.33758 | 0.0098554 | 0 | 0.10314 | 0 | 0.075125 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0688 | 0.1893% | CZ 4B | 2.3442 | 0.72886 | 10.8356 | 1.0057 | 0 | 3.3105 | 0 | 2.4114 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 34.9964 | 0.189% | CZ 4B | 0.68704 | 0.21362 | 3.1757 | 0 | 0 | 0.97025 | 0 | 0.70673 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.9621 | 0.189% | CZ 4B | 0 | 0 | 0 | 0.010057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010057 | 0.1893% | CZ 4B | 7.1927 | 2.2363 | 33.2468 | 1.0992 | 0 | 10.1575 | 0 | 7.3987 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 105.3925 | 0.1893%
CZ 4C | 0.073033 | 0.022664 | 0.3547 | 0.014067 | 0 | 0.047192 | 0 | 0.055902 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0149 | 5.156% | CZ 4C | 2.3442 | 0.72745 | 11.3852 | 1.4354 | 0 | 1.5148 | 0 | 1.7943 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 33.5616 | 5.156% | CZ 4C | 0.68704 | 0.2132 | 3.3368 | 0 | 0 | 0.44395 | 0 | 0.52589 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.4156 | 5.156% | CZ 4C | 0 | 0 | 0 | 0.014354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014354 | 5.156% | CZ 4C | 7.1927 | 2.232 | 34.9331 | 1.5689 | 0 | 4.6477 | 0 | 5.5055 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 100.1412 | 5.156%
CZ 5A | 0.073033 | 0.022699 | 0.3706 | 0.064336 | 0 | 0.054265 | 0 | 0.060638 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.093 | 16.2% | CZ 5A | 2.3442 | 0.72858 | 11.8955 | 6.5649 | 0 | 1.7418 | 0 | 1.9463 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 39.5814 | 16.2% | CZ 5A | 0.68704 | 0.21353 | 3.4864 | 0 | 0 | 0.51049 | 0 | 0.57044 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.6766 | 16.2% | CZ 5A | 0 | 0 | 0 | 0.065649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065649 | 16.2% | CZ 5A | 7.1927 | 2.2355 | 36.4987 | 7.1754 | 0 | 5.3443 | 0 | 5.9719 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 108.4797 | 16.2%
CZ 5B | 0.073033 | 0.022699 | 0.3634 | 0.028864 | 0 | 0.078574 | 0 | 0.06975 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0837 | 5.323% | CZ 5B | 2.3442 | 0.72858 | 11.6645 | 2.9453 | 0 | 2.5221 | 0 | 2.2388 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 36.8037 | 5.323% | CZ 5B | 0.68704 | 0.21353 | 3.4187 | 0 | 0 | 0.73917 | 0 | 0.65616 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.9233 | 5.323% | CZ 5B | 0 | 0 | 0 | 0.029453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029453 | 5.323% | CZ 5B | 7.1927 | 2.2355 | 35.7901 | 3.2193 | 0 | 7.7384 | 0 | 6.8694 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 107.1065 | 5.323%
CZ 5C | 0.073033 | 0.022664 | 0.36837 | 0.011171 | 0 | 0.04643 | 0 | 0.05472 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0238 | 0.04828% | CZ 5C | 2.3442 | 0.72745 | 11.8238 | 1.1399 | 0 | 1.4903 | 0 | 1.7564 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 33.6423 | 0.048% | CZ 5C | 0.68704 | 0.2132 | 3.4654 | 0 | 0 | 0.43678 | 0 | 0.51477 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.5259 | 0.048% | CZ 5C | 0 | 0 | 0 | 0.011399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011399 | 0.04828% | CZ 5C | 7.1927 | 2.232 | 36.2789 | 1.2459 | 0 | 4.5727 | 0 | 5.3891 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 100.9726 | 0.04828%
CZ 6A | 0.073033 | 0.02269 | 0.38857 | 0.10432 | 0 | 0.0583 | 0 | 0.063973 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1583 | 4.174% | CZ 6A | 2.3442 | 0.72829 | 12.4723 | 10.6448 | 0 | 1.8713 | 0 | 2.0534 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 44.4745 | 4.174% | CZ 6A | 0.68704 | 0.21345 | 3.6554 | 0 | 0 | 0.54845 | 0 | 0.60181 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.9149 | 4.174% | CZ 6A | 0 | 0 | 0 | 0.10645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10645 | 4.174% | CZ 6A | 7.1927 | 2.2346 | 38.2687 | 11.6348 | 0 | 5.7417 | 0 | 6.3004 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 115.4341 | 4.174%
CZ 6B | 0.073033 | 0.022672 | 0.38397 | 0.062208 | 0 | 0.053171 | 0 | 0.064577 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.107 | 0.3776% | CZ 6B | 2.3442 | 0.72773 | 12.3245 | 6.3477 | 0 | 1.7067 | 0 | 2.0728 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 39.8838 | 0.378% | CZ 6B | 0.68704 | 0.21329 | 3.6121 | 0 | 0 | 0.50019 | 0 | 0.60749 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.8289 | 0.378% | CZ 6B | 0 | 0 | 0 | 0.063477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063477 | 0.3776% | CZ 6B | 7.1927 | 2.2329 | 37.8152 | 6.9381 | 0 | 5.2365 | 0 | 6.3599 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 109.8365 | 0.3776%
CZ 7 | 0.073033 | 0.022655 | 0.40982 | 0.10293 | 0 | 0.051866 | 0 | 0.063815 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1715 | 0.3013% | CZ 7 | 2.3442 | 0.72717 | 13.1543 | 10.5032 | 0 | 1.6648 | 0 | 2.0483 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 44.8022 | 0.301% | CZ 7 | 0.68704 | 0.21312 | 3.8553 | 0 | 0 | 0.48792 | 0 | 0.60033 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.0524 | 0.301% | CZ 7 | 0 | 0 | 0 | 0.10503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10503 | 0.3013% | CZ 7 | 7.1927 | 2.2312 | 40.361 | 11.48 | 0 | 5.1081 | 0 | 6.2849 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 116.7191 | 0.3013%
CZ 8 | 0.073033 | 0.022532 | 0.43865 | 0.13201 | 0 | 0.043585 | 0 | 0.067002 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2242 | 8.036e-05% | CZ 8 | 2.3442 | 0.72324 | 14.0798 | 13.4702 | 0 | 1.399 | 0 | 2.1506 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 48.5272 | 0% | CZ 8 | 0.68704 | 0.21197 | 4.1266 | 0 | 0 | 0.41002 | 0 | 0.63031 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.2746 | 0% | CZ 8 | 0 | 0 | 0 | 0.1347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1347 | 8.036e-05% | CZ 8 | 7.1927 | 2.2191 | 43.2009 | 14.7229 | 0 | 4.2925 | 0 | 6.5987 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 122.288 | 8.036e-05%
US Weighted | 0.073032 | 0.022706 | 0.33122 | 0.027212 | 0 | 0.1076 | 0 | 0.069285 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0784 | 100% | US Weighted | 2.3442 | 0.7288 | 10.6314 | 2.7767 | 0 | 3.4537 | 0 | 2.2239 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 36.5187 | 100% | US Weighted | 0.68704 | 0.2136 | 3.1159 | 0 | 0 | 1.0122 | 0 | 0.65179 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.8892 | 100% | US Weighted | 0 | 0 | 0 | 0.027767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027767 | 100% | US Weighted | 7.1926 | 2.2362 | 32.6201 | 3.0349 | 0 | 10.5969 | 0 | 6.8235 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 106.5651 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.089385 | 0.022742 | 0.24072 | 0 | 0 | 0.44242 | 0 | 0.12844 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.3711 | 0% | CZ 0A | 2.8691 | 0.72998 | 7.7266 | 0 | 0 | 14.2006 | 0 | 4.1228 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 44.0093 | 0% | CZ 0A | 0.84087 | 0.21394 | 2.2645 | 0 | 0 | 4.162 | 0 | 1.2083 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 12.8984 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 8.8031 | 2.2398 | 23.7075 | 0 | 0 | 43.5716 | 0 | 12.6499 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 135.0331 | 0%
CZ 0B | 0.089385 | 0.022751 | 0.2397 | 0 | 0 | 0.3962 | 0 | 0.12544 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.3209 | 0% | CZ 0B | 2.8691 | 0.73026 | 7.6937 | 0 | 0 | 12.7171 | 0 | 4.0264 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 42.3967 | 0% | CZ 0B | 0.84087 | 0.21403 | 2.2549 | 0 | 0 | 3.7272 | 0 | 1.1801 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 12.4258 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 8.8031 | 2.2407 | 23.6066 | 0 | 0 | 39.0196 | 0 | 12.3542 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 130.0854 | 0%
CZ 1A | 0.089385 | 0.022751 | 0.25898 | 0 | 0 | 0.27625 | 0 | 0.101 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1958 | 2.646% | CZ 1A | 2.8691 | 0.73026 | 8.3127 | 0 | 0 | 8.8671 | 0 | 3.2419 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 38.3813 | 2.646% | CZ 1A | 0.84087 | 0.21403 | 2.4363 | 0 | 0 | 2.5988 | 0 | 0.95015 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 11.2489 | 2.646% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.646% | CZ 1A | 8.8031 | 2.2407 | 25.5058 | 0 | 0 | 27.2068 | 0 | 9.9471 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 117.7648 | 2.646%
CZ 1B | 0.089385 | 0.022725 | 0.25997 | 0.0010929 | 0 | 0.31226 | 0 | 0.11343 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2462 | 0% | CZ 1B | 2.8691 | 0.72942 | 8.3445 | 0.11152 | 0 | 10.0228 | 0 | 3.6409 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 40.0784 | 0% | CZ 1B | 0.84087 | 0.21378 | 2.4456 | 0 | 0 | 2.9375 | 0 | 1.0671 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 11.7136 | 0% | CZ 1B | 0 | 0 | 0 | 0.0011152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011152 | 0% | CZ 1B | 8.8031 | 2.2381 | 25.6033 | 0.12189 | 0 | 30.7527 | 0 | 11.1714 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 122.7517 | 0%
CZ 2A | 0.089385 | 0.022716 | 0.28051 | 0.0028493 | 0 | 0.22519 | 0 | 0.086059 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1541 | 16.39% | CZ 2A | 2.8691 | 0.72914 | 9.0037 | 0.29074 | 0 | 7.2282 | 0 | 2.7623 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 37.2432 | 16.39% | CZ 2A | 0.84087 | 0.2137 | 2.6388 | 0 | 0 | 2.1185 | 0 | 0.80958 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.8302 | 16.39% | CZ 2A | 0 | 0 | 0 | 0.0029074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0029074 | 16.39% | CZ 2A | 8.8031 | 2.2372 | 27.6258 | 0.31778 | 0 | 22.1781 | 0 | 8.4755 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 113.6987 | 16.39%
CZ 2B | 0.089385 | 0.022734 | 0.28204 | 0.0021363 | 0 | 0.18726 | 0 | 0.090899 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1218 | 1.974% | CZ 2B | 2.8691 | 0.7297 | 9.0528 | 0.21799 | 0 | 6.0107 | 0 | 2.9177 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 36.1581 | 1.974% | CZ 2B | 0.84087 | 0.21386 | 2.6532 | 0 | 0 | 1.7616 | 0 | 0.85512 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.5335 | 1.974% | CZ 2B | 0 | 0 | 0 | 0.0021799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021799 | 1.974% | CZ 2B | 8.8031 | 2.2389 | 27.7767 | 0.23826 | 0 | 18.4425 | 0 | 8.9523 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 110.513 | 1.974%
CZ 3A | 0.089385 | 0.022725 | 0.31753 | 0.034034 | 0 | 0.12177 | 0 | 0.071212 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.104 | 12.99% | CZ 3A | 2.8691 | 0.72942 | 10.1919 | 3.4729 | 0 | 3.9084 | 0 | 2.2858 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 37.8176 | 12.99% | CZ 3A | 0.84087 | 0.21378 | 2.9871 | 0 | 0 | 1.1455 | 0 | 0.66992 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.0659 | 12.99% | CZ 3A | 0 | 0 | 0 | 0.034729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034729 | 12.99% | CZ 3A | 8.8031 | 2.2381 | 31.2717 | 3.7959 | 0 | 11.9921 | 0 | 7.0134 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 109.1755 | 12.99%
CZ 3B | 0.089385 | 0.022725 | 0.308 | 0.010626 | 0 | 0.13216 | 0 | 0.079983 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0903 | 8.593% | CZ 3B | 2.8691 | 0.72942 | 9.8862 | 1.0843 | 0 | 4.2419 | 0 | 2.5673 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 35.7384 | 8.593% | CZ 3B | 0.84087 | 0.21378 | 2.8975 | 0 | 0 | 1.2432 | 0 | 0.75243 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.1565 | 8.593% | CZ 3B | 0 | 0 | 0 | 0.010843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010843 | 8.593% | CZ 3B | 8.8031 | 2.2381 | 30.3337 | 1.1852 | 0 | 13.0154 | 0 | 7.8772 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 107.5139 | 8.593%
CZ 3C | 0.089385 | 0.022725 | 0.3209 | 0.0017866 | 0 | 0.060594 | 0 | 0.05458 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 0.99736 | 3.597% | CZ 3C | 2.8691 | 0.72942 | 10.3001 | 0.18231 | 0 | 1.9449 | 0 | 1.7519 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 32.1379 | 3.597% | CZ 3C | 0.84087 | 0.21378 | 3.0188 | 0 | 0 | 0.57003 | 0 | 0.51345 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.3656 | 3.597% | CZ 3C | 0 | 0 | 0 | 0.0018231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018231 | 3.597% | CZ 3C | 8.8031 | 2.2381 | 31.6036 | 0.19927 | 0 | 5.9676 | 0 | 5.3753 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 98.2483 | 3.597%
CZ 4A | 0.089385 | 0.02269 | 0.34608 | 0.03042 | 0 | 0.086164 | 0 | 0.064612 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0867 | 22.03% | CZ 4A | 2.8691 | 0.72829 | 11.1085 | 3.1041 | 0 | 2.7657 | 0 | 2.0739 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 37.0096 | 22.03% | CZ 4A | 0.84087 | 0.21345 | 3.2557 | 0 | 0 | 0.81057 | 0 | 0.60782 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.9372 | 22.03% | CZ 4A | 0 | 0 | 0 | 0.031041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031041 | 22.03% | CZ 4A | 8.8031 | 2.2346 | 34.0839 | 3.3927 | 0 | 8.4859 | 0 | 6.3633 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 107.4248 | 22.03%
CZ 4B | 0.089385 | 0.022707 | 0.33798 | 0.024286 | 0 | 0.096222 | 0 | 0.074644 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0926 | 0.1893% | CZ 4B | 2.8691 | 0.72886 | 10.8486 | 2.4782 | 0 | 3.0885 | 0 | 2.3959 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 36.7693 | 0.189% | CZ 4B | 0.84087 | 0.21362 | 3.1795 | 0 | 0 | 0.90519 | 0 | 0.7022 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.0501 | 0.189% | CZ 4B | 0 | 0 | 0 | 0.024782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024782 | 0.1893% | CZ 4B | 8.8031 | 2.2363 | 33.2865 | 2.7087 | 0 | 9.4764 | 0 | 7.3513 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 107.9236 | 0.1893%
CZ 4C | 0.089385 | 0.022664 | 0.35532 | 0.043166 | 0 | 0.033816 | 0 | 0.055508 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0472 | 5.156% | CZ 4C | 2.8691 | 0.72745 | 11.4049 | 4.4047 | 0 | 1.0854 | 0 | 1.7817 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 36.6334 | 5.156% | CZ 4C | 0.84087 | 0.2132 | 3.3426 | 0 | 0 | 0.31812 | 0 | 0.52218 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.4457 | 5.156% | CZ 4C | 0 | 0 | 0 | 0.044047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044047 | 5.156% | CZ 4C | 8.8031 | 2.232 | 34.9935 | 4.8143 | 0 | 3.3304 | 0 | 5.4667 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 103.7013 | 5.156%
CZ 5A | 0.089385 | 0.022699 | 0.37049 | 0.058455 | 0 | 0.057722 | 0 | 0.062283 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1084 | 16.2% | CZ 5A | 2.8691 | 0.72858 | 11.8918 | 5.9648 | 0 | 1.8528 | 0 | 1.9992 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 39.6664 | 16.2% | CZ 5A | 0.84087 | 0.21353 | 3.4853 | 0 | 0 | 0.54301 | 0 | 0.58592 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.8774 | 16.2% | CZ 5A | 0 | 0 | 0 | 0.059648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059648 | 16.2% | CZ 5A | 8.8031 | 2.2355 | 36.4875 | 6.5196 | 0 | 5.6848 | 0 | 6.134 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 109.9258 | 16.2%
CZ 5B | 0.089385 | 0.022699 | 0.36384 | 0.062067 | 0 | 0.070862 | 0 | 0.072035 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1283 | 5.323% | CZ 5B | 2.8691 | 0.72858 | 11.6786 | 6.3334 | 0 | 2.2745 | 0 | 2.3122 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 40.5565 | 5.323% | CZ 5B | 0.84087 | 0.21353 | 3.4228 | 0 | 0 | 0.66662 | 0 | 0.67766 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.0302 | 5.323% | CZ 5B | 0 | 0 | 0 | 0.063334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063334 | 5.323% | CZ 5B | 8.8031 | 2.2355 | 35.8332 | 6.9224 | 0 | 6.9789 | 0 | 7.0944 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 111.9287 | 5.323%
CZ 5C | 0.089385 | 0.022664 | 0.36912 | 0.043133 | 0 | 0.027732 | 0 | 0.053424 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0528 | 0.04828% | CZ 5C | 2.8691 | 0.72745 | 11.848 | 4.4013 | 0 | 0.89014 | 0 | 1.7148 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 36.8109 | 0.048% | CZ 5C | 0.84087 | 0.2132 | 3.4724 | 0 | 0 | 0.26088 | 0 | 0.50258 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.4987 | 0.048% | CZ 5C | 0 | 0 | 0 | 0.044013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044013 | 0.04828% | CZ 5C | 8.8031 | 2.232 | 36.353 | 4.8106 | 0 | 2.7312 | 0 | 5.2615 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 104.2528 | 0.04828%
CZ 6A | 0.089385 | 0.02269 | 0.38846 | 0.096085 | 0 | 0.063255 | 0 | 0.066345 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1736 | 4.174% | CZ 6A | 2.8691 | 0.72829 | 12.4687 | 9.8046 | 0 | 2.0303 | 0 | 2.1295 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 44.3907 | 4.174% | CZ 6A | 0.84087 | 0.21345 | 3.6544 | 0 | 0 | 0.59506 | 0 | 0.62413 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.1366 | 4.174% | CZ 6A | 0 | 0 | 0 | 0.098046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.098046 | 4.174% | CZ 6A | 8.8031 | 2.2346 | 38.2575 | 10.7164 | 0 | 6.2297 | 0 | 6.534 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 116.8366 | 4.174%
CZ 6B | 0.089385 | 0.022672 | 0.38399 | 0.066615 | 0 | 0.056339 | 0 | 0.06828 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1347 | 0.3776% | CZ 6B | 2.8691 | 0.72773 | 12.3254 | 6.7975 | 0 | 1.8084 | 0 | 2.1916 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 41.0798 | 0.378% | CZ 6B | 0.84087 | 0.21329 | 3.6124 | 0 | 0 | 0.53 | 0 | 0.64233 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.0476 | 0.378% | CZ 6B | 0 | 0 | 0 | 0.067975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.067975 | 0.3776% | CZ 6B | 8.8031 | 2.2329 | 37.8178 | 7.4296 | 0 | 5.5486 | 0 | 6.7245 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 112.6178 | 0.3776%
CZ 7 | 0.089385 | 0.022655 | 0.40983 | 0.10795 | 0 | 0.056366 | 0 | 0.068691 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2023 | 0.3013% | CZ 7 | 2.8691 | 0.72717 | 13.1548 | 11.0156 | 0 | 1.8092 | 0 | 2.2048 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 46.1409 | 0.301% | CZ 7 | 0.84087 | 0.21312 | 3.8555 | 0 | 0 | 0.53025 | 0 | 0.6462 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.2946 | 0.301% | CZ 7 | 0 | 0 | 0 | 0.11016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11016 | 0.3013% | CZ 7 | 8.8031 | 2.2312 | 40.3628 | 12.04 | 0 | 5.5512 | 0 | 6.7651 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 119.8146 | 0.3013%
CZ 8 | 0.089385 | 0.022532 | 0.4387 | 0.14512 | 0 | 0.047104 | 0 | 0.072744 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.263 | 8.036e-05% | CZ 8 | 2.8691 | 0.72324 | 14.0815 | 14.8079 | 0 | 1.5119 | 0 | 2.3349 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 50.6887 | 0% | CZ 8 | 0.84087 | 0.21197 | 4.127 | 0 | 0 | 0.44312 | 0 | 0.68433 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.5161 | 0% | CZ 8 | 0 | 0 | 0 | 0.14808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14808 | 8.036e-05% | CZ 8 | 8.8031 | 2.2191 | 43.206 | 16.185 | 0 | 4.6391 | 0 | 7.1642 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 126.2778 | 8.036e-05%
US Weighted | 0.089384 | 0.022706 | 0.33135 | 0.032266 | 0 | 0.11434 | 0 | 0.071086 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1085 | 100% | US Weighted | 2.869 | 0.7288 | 10.6356 | 3.2925 | 0 | 3.6702 | 0 | 2.2817 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 37.8379 | 100% | US Weighted | 0.84087 | 0.2136 | 3.1171 | 0 | 0 | 1.0757 | 0 | 0.66873 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.1247 | 100% | US Weighted | 0 | 0 | 0 | 0.032925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032925 | 100% | US Weighted | 8.803 | 2.2362 | 32.6331 | 3.5987 | 0 | 11.2612 | 0 | 7.001 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 109.5939 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.1139 | 0.034551 | 0.24072 | 0 | 0 | 0.45586 | 0 | 0.13315 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.4256 | 0% | CZ 0A | 3.6561 | 1.109 | 7.7266 | 0 | 0 | 14.6322 | 0 | 4.2737 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 45.7578 | 0% | CZ 0A | 1.0715 | 0.32503 | 2.2645 | 0 | 0 | 4.2885 | 0 | 1.2525 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 13.4108 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 11.2179 | 3.4028 | 23.7075 | 0 | 0 | 44.8958 | 0 | 13.1129 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 140.3981 | 0%
CZ 0B | 0.1139 | 0.03456 | 0.2397 | 0 | 0 | 0.40948 | 0 | 0.12984 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.3749 | 0% | CZ 0B | 3.6561 | 1.1093 | 7.6937 | 0 | 0 | 13.1436 | 0 | 4.1675 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 44.1304 | 0% | CZ 0B | 1.0715 | 0.32512 | 2.2549 | 0 | 0 | 3.8522 | 0 | 1.2214 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 12.9339 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 11.2179 | 3.4037 | 23.6066 | 0 | 0 | 40.3283 | 0 | 12.787 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 135.4047 | 0%
CZ 1A | 0.1139 | 0.034569 | 0.25898 | 0 | 0 | 0.28193 | 0 | 0.10317 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2399 | 2.646% | CZ 1A | 3.6561 | 1.1096 | 8.3127 | 0 | 0 | 9.0494 | 0 | 3.3116 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 39.7997 | 2.646% | CZ 1A | 1.0715 | 0.3252 | 2.4363 | 0 | 0 | 2.6522 | 0 | 0.97058 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 11.6646 | 2.646% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.646% | CZ 1A | 11.2179 | 3.4045 | 25.5058 | 0 | 0 | 27.7663 | 0 | 10.161 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 122.1168 | 2.646%
CZ 1B | 0.1139 | 0.034525 | 0.25995 | 0.00094976 | 0 | 0.31794 | 0 | 0.11552 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2902 | 0% | CZ 1B | 3.6561 | 1.1082 | 8.3439 | 0.096914 | 0 | 10.2051 | 0 | 3.7081 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 41.4785 | 0% | CZ 1B | 1.0715 | 0.32479 | 2.4455 | 0 | 0 | 2.9909 | 0 | 1.0868 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 12.1282 | 0% | CZ 1B | 0 | 0 | 0 | 0.00096914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00096914 | 0% | CZ 1B | 11.2179 | 3.4002 | 25.6015 | 0.10593 | 0 | 31.3122 | 0 | 11.3774 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 127.0765 | 0%
CZ 2A | 0.1139 | 0.034507 | 0.2805 | 0.0026841 | 0 | 0.23032 | 0 | 0.088019 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1973 | 16.39% | CZ 2A | 3.6561 | 1.1076 | 9.0034 | 0.27389 | 0 | 7.3928 | 0 | 2.8252 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 38.6192 | 16.39% | CZ 2A | 1.0715 | 0.32462 | 2.6387 | 0 | 0 | 2.1667 | 0 | 0.82803 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 11.2384 | 16.39% | CZ 2A | 0 | 0 | 0 | 0.0027389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027389 | 16.39% | CZ 2A | 11.2179 | 3.3985 | 27.6249 | 0.29936 | 0 | 22.6833 | 0 | 8.6686 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 117.9538 | 16.39%
CZ 2B | 0.1139 | 0.034534 | 0.28202 | 0.0019656 | 0 | 0.19222 | 0 | 0.09307 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1651 | 1.974% | CZ 2B | 3.6561 | 1.1085 | 9.0523 | 0.20057 | 0 | 6.17 | 0 | 2.9874 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 37.5349 | 1.974% | CZ 2B | 1.0715 | 0.32487 | 2.6531 | 0 | 0 | 1.8083 | 0 | 0.87554 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.9421 | 1.974% | CZ 2B | 0 | 0 | 0 | 0.0020057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020057 | 1.974% | CZ 2B | 11.2179 | 3.4011 | 27.7749 | 0.21922 | 0 | 18.9313 | 0 | 9.1661 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 114.7718 | 1.974%
CZ 3A | 0.1139 | 0.034525 | 0.31749 | 0.032372 | 0 | 0.12542 | 0 | 0.072508 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1436 | 12.99% | CZ 3A | 3.6561 | 1.1082 | 10.1908 | 3.3032 | 0 | 4.0256 | 0 | 2.3273 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 38.9714 | 12.99% | CZ 3A | 1.0715 | 0.32479 | 2.9867 | 0 | 0 | 1.1798 | 0 | 0.6821 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.4537 | 12.99% | CZ 3A | 0 | 0 | 0 | 0.033032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033032 | 12.99% | CZ 3A | 11.2179 | 3.4002 | 31.2683 | 3.6104 | 0 | 12.3516 | 0 | 7.1409 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 113.0506 | 12.99%
CZ 3B | 0.1139 | 0.034525 | 0.30797 | 0.0098279 | 0 | 0.13638 | 0 | 0.081839 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1318 | 8.593% | CZ 3B | 3.6561 | 1.1082 | 9.8851 | 1.0028 | 0 | 4.3774 | 0 | 2.6269 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 37.0166 | 8.593% | CZ 3B | 1.0715 | 0.32479 | 2.8972 | 0 | 0 | 1.2829 | 0 | 0.76989 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.555 | 8.593% | CZ 3B | 0 | 0 | 0 | 0.010028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010028 | 8.593% | CZ 3B | 11.2179 | 3.4002 | 30.3303 | 1.0961 | 0 | 13.431 | 0 | 8.06 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 111.5967 | 8.593%
CZ 3C | 0.1139 | 0.034525 | 0.32085 | 0.0015389 | 0 | 0.064437 | 0 | 0.056532 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0392 | 3.597% | CZ 3C | 3.6561 | 1.1082 | 10.2987 | 0.15703 | 0 | 2.0683 | 0 | 1.8146 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 33.463 | 3.597% | CZ 3C | 1.0715 | 0.32479 | 3.0184 | 0 | 0 | 0.60618 | 0 | 0.53182 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.7614 | 3.597% | CZ 3C | 0 | 0 | 0 | 0.0015703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015703 | 3.597% | CZ 3C | 11.2179 | 3.4002 | 31.5993 | 0.17163 | 0 | 6.3461 | 0 | 5.5676 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 102.364 | 3.597%
CZ 4A | 0.1139 | 0.034472 | 0.34603 | 0.029021 | 0 | 0.092107 | 0 | 0.067247 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1302 | 22.03% | CZ 4A | 3.6561 | 1.1065 | 11.1068 | 2.9613 | 0 | 2.9564 | 0 | 2.1585 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 38.3058 | 22.03% | CZ 4A | 1.0715 | 0.32429 | 3.2552 | 0 | 0 | 0.86649 | 0 | 0.63261 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.3589 | 22.03% | CZ 4A | 0 | 0 | 0 | 0.029613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029613 | 22.03% | CZ 4A | 11.2179 | 3.395 | 34.0788 | 3.2368 | 0 | 9.0712 | 0 | 6.6228 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 111.6838 | 22.03%
CZ 4B | 0.1139 | 0.034499 | 0.33791 | 0.022365 | 0 | 0.10441 | 0 | 0.077917 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1384 | 0.1893% | CZ 4B | 3.6561 | 1.1073 | 10.8463 | 2.2821 | 0 | 3.3512 | 0 | 2.501 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 38.1042 | 0.189% | CZ 4B | 1.0715 | 0.32454 | 3.1789 | 0 | 0 | 0.98219 | 0 | 0.733 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.4989 | 0.189% | CZ 4B | 0 | 0 | 0 | 0.022821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022821 | 0.1893% | CZ 4B | 11.2179 | 3.3976 | 33.2796 | 2.4943 | 0 | 10.2825 | 0 | 7.6737 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 112.407 | 0.1893%
CZ 4C | 0.1139 | 0.034437 | 0.35525 | 0.040523 | 0 | 0.038403 | 0 | 0.05788 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0878 | 5.156% | CZ 4C | 3.6561 | 1.1054 | 11.4026 | 4.135 | 0 | 1.2326 | 0 | 1.8578 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 37.7498 | 5.156% | CZ 4C | 1.0715 | 0.32396 | 3.3419 | 0 | 0 | 0.36127 | 0 | 0.5445 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.8519 | 5.156% | CZ 4C | 0 | 0 | 0 | 0.04135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04135 | 5.156% | CZ 4C | 11.2179 | 3.3916 | 34.9866 | 4.5195 | 0 | 3.7821 | 0 | 5.7003 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 107.6594 | 5.156%
CZ 5A | 0.1139 | 0.034481 | 0.37045 | 0.057164 | 0 | 0.061154 | 0 | 0.06434 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1489 | 16.2% | CZ 5A | 3.6561 | 1.1068 | 11.8907 | 5.8331 | 0 | 1.9629 | 0 | 2.0652 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 40.8749 | 16.2% | CZ 5A | 1.0715 | 0.32438 | 3.485 | 0 | 0 | 0.5753 | 0 | 0.60527 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.2702 | 16.2% | CZ 5A | 0 | 0 | 0 | 0.058331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.058331 | 16.2% | CZ 5A | 11.2179 | 3.3959 | 36.4841 | 6.3756 | 0 | 6.0228 | 0 | 6.3366 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 113.8941 | 16.2%
CZ 5B | 0.1139 | 0.03449 | 0.3638 | 0.059992 | 0 | 0.0753 | 0 | 0.074355 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1692 | 5.323% | CZ 5B | 3.6561 | 1.1071 | 11.6772 | 6.1216 | 0 | 2.417 | 0 | 2.3866 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 41.7257 | 5.323% | CZ 5B | 1.0715 | 0.32446 | 3.4224 | 0 | 0 | 0.70837 | 0 | 0.69948 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.435 | 5.323% | CZ 5B | 0 | 0 | 0 | 0.061216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061216 | 5.323% | CZ 5B | 11.2179 | 3.3968 | 35.8289 | 6.6909 | 0 | 7.416 | 0 | 7.3229 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 115.9345 | 5.323%
CZ 5C | 0.1139 | 0.034429 | 0.36906 | 0.040594 | 0 | 0.030778 | 0 | 0.055114 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.0913 | 0.04828% | CZ 5C | 3.6561 | 1.1051 | 11.846 | 4.1423 | 0 | 0.98792 | 0 | 1.769 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 37.8666 | 0.048% | CZ 5C | 1.0715 | 0.32388 | 3.4719 | 0 | 0 | 0.28954 | 0 | 0.51847 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 9.884 | 0.048% | CZ 5C | 0 | 0 | 0 | 0.041423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041423 | 0.04828% | CZ 5C | 11.2179 | 3.3907 | 36.347 | 4.5275 | 0 | 3.0312 | 0 | 5.4279 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 108.0036 | 0.04828%
CZ 6A | 0.1139 | 0.034472 | 0.38847 | 0.099479 | 0 | 0.064262 | 0 | 0.067833 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2158 | 4.174% | CZ 6A | 3.6561 | 1.1065 | 12.4689 | 10.1509 | 0 | 2.0627 | 0 | 2.1773 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 45.9826 | 4.174% | CZ 6A | 1.0715 | 0.32429 | 3.6544 | 0 | 0 | 0.60453 | 0 | 0.63813 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.5017 | 4.174% | CZ 6A | 0 | 0 | 0 | 0.10151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10151 | 4.174% | CZ 6A | 11.2179 | 3.395 | 38.2583 | 11.095 | 0 | 6.3288 | 0 | 6.6806 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 121.0369 | 4.174%
CZ 6B | 0.1139 | 0.034446 | 0.38401 | 0.068911 | 0 | 0.057013 | 0 | 0.069584 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1753 | 0.3776% | CZ 6B | 3.6561 | 1.1056 | 12.3259 | 7.0317 | 0 | 1.83 | 0 | 2.2335 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 42.5431 | 0.378% | CZ 6B | 1.0715 | 0.32405 | 3.6125 | 0 | 0 | 0.53634 | 0 | 0.6546 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.4078 | 0.378% | CZ 6B | 0 | 0 | 0 | 0.070317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.070317 | 0.3776% | CZ 6B | 11.2179 | 3.3924 | 37.8195 | 7.6857 | 0 | 5.615 | 0 | 6.853 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 116.6448 | 0.3776%
CZ 7 | 0.1139 | 0.03442 | 0.40984 | 0.11081 | 0 | 0.057416 | 0 | 0.070144 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.2439 | 0.3013% | CZ 7 | 3.6561 | 1.1048 | 13.1551 | 11.3069 | 0 | 1.8429 | 0 | 2.2515 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 47.6775 | 0.301% | CZ 7 | 1.0715 | 0.3238 | 3.8555 | 0 | 0 | 0.54013 | 0 | 0.65987 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.6596 | 0.301% | CZ 7 | 0 | 0 | 0 | 0.11307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11307 | 0.3013% | CZ 7 | 11.2179 | 3.3899 | 40.3636 | 12.3584 | 0 | 5.6546 | 0 | 6.9082 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 123.9539 | 0.3013%
CZ 8 | 0.1139 | 0.034236 | 0.43877 | 0.16358 | 0 | 0.045756 | 0 | 0.074565 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.3182 | 8.036e-05% | CZ 8 | 3.6561 | 1.0989 | 14.0834 | 16.6922 | 0 | 1.4687 | 0 | 2.3934 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.8491 | 53.7529 | 0% | CZ 8 | 1.0715 | 0.32207 | 4.1276 | 0 | 0 | 0.43044 | 0 | 0.70146 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.8619 | 0% | CZ 8 | 0 | 0 | 0 | 0.16692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16692 | 8.036e-05% | CZ 8 | 11.2179 | 3.3718 | 43.2121 | 18.2446 | 0 | 4.5063 | 0 | 7.3435 | 0 | 0 | 0 | 10.7731 | 0 | 0 | 0 | 33.2882 | 131.9574 | 8.036e-05%
US Weighted | 0.1139 | 0.034495 | 0.33132 | 0.031332 | 0 | 0.11881 | 0 | 0.073144 | 0 | 0 | 0 | 0.10939 | 0 | 0 | 0 | 0.338 | 1.1504 | 100% | US Weighted | 3.656 | 1.1072 | 10.6345 | 3.1972 | 0 | 3.8136 | 0 | 2.3478 | 0 | 0 | 0 | 3.5111 | 0 | 0 | 0 | 10.849 | 39.1163 | 100% | US Weighted | 1.0715 | 0.32451 | 3.1168 | 0 | 0 | 1.1177 | 0 | 0.68809 | 0 | 0 | 0 | 1.029 | 0 | 0 | 0 | 3.1797 | 10.5273 | 100% | US Weighted | 0 | 0 | 0 | 0.031972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031972 | 100% | US Weighted | 11.2178 | 3.3973 | 32.6297 | 3.4945 | 0 | 11.7012 | 0 | 7.2036 | 0 | 0 | 0 | 10.773 | 0 | 0 | 0 | 33.2879 | 113.7049 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.13483 | 0.034551 | 0.24101 | 0 | 0 | 0.53611 | 0 | 0.14727 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.5414 | 0% | CZ 0A | 4.3276 | 1.109 | 7.7359 | 0 | 0 | 17.2079 | 0 | 4.7272 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 49.4771 | 0% | CZ 0A | 1.2684 | 0.32503 | 2.2673 | 0 | 0 | 5.0434 | 0 | 1.3855 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 14.5009 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 13.2784 | 3.4028 | 23.7359 | 0 | 0 | 52.7989 | 0 | 14.5043 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 151.81 | 0%
CZ 0B | 0.13483 | 0.03456 | 0.24002 | 0 | 0 | 0.47879 | 0 | 0.14222 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.4781 | 0% | CZ 0B | 4.3276 | 1.1093 | 7.7041 | 0 | 0 | 15.3681 | 0 | 4.565 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 47.4437 | 0% | CZ 0B | 1.2684 | 0.32512 | 2.258 | 0 | 0 | 4.5041 | 0 | 1.3379 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 13.9049 | 0% | CZ 0B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0B | 13.2784 | 3.4037 | 23.6385 | 0 | 0 | 47.1537 | 0 | 14.0069 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 145.5708 | 0%
CZ 1A | 0.13483 | 0.034569 | 0.25952 | 0 | 0 | 0.36059 | 0 | 0.1192 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.3564 | 2.646% | CZ 1A | 4.3276 | 1.1096 | 8.3301 | 0 | 0 | 11.5743 | 0 | 3.8261 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 43.5372 | 2.646% | CZ 1A | 1.2684 | 0.3252 | 2.4414 | 0 | 0 | 3.3922 | 0 | 1.1214 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 12.76 | 2.646% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.646% | CZ 1A | 13.2784 | 3.4045 | 25.5593 | 0 | 0 | 35.5133 | 0 | 11.7395 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 133.5847 | 2.646%
CZ 1B | 0.13483 | 0.034525 | 0.26028 | 0.0020757 | 0 | 0.37014 | 0 | 0.12617 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.3757 | 0% | CZ 1B | 4.3276 | 1.1082 | 8.3543 | 0.21181 | 0 | 11.8806 | 0 | 4.0497 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 44.3017 | 0% | CZ 1B | 1.2684 | 0.32479 | 2.4485 | 0 | 0 | 3.482 | 0 | 1.1869 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 12.922 | 0% | CZ 1B | 0 | 0 | 0 | 0.0021181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021181 | 0% | CZ 1B | 13.2784 | 3.4002 | 25.6334 | 0.2315 | 0 | 36.453 | 0 | 12.4257 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 135.512 | 0%
CZ 2A | 0.13483 | 0.034507 | 0.28094 | 0.0037495 | 0 | 0.28322 | 0 | 0.098051 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.283 | 16.39% | CZ 2A | 4.3276 | 1.1076 | 9.0177 | 0.3826 | 0 | 9.0908 | 0 | 3.1472 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 41.443 | 16.39% | CZ 2A | 1.2684 | 0.32462 | 2.6429 | 0 | 0 | 2.6643 | 0 | 0.9224 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 12.0341 | 16.39% | CZ 2A | 0 | 0 | 0 | 0.003826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003826 | 16.39% | CZ 2A | 13.2784 | 3.3985 | 27.6689 | 0.41818 | 0 | 27.8931 | 0 | 9.6566 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 126.4033 | 16.39%
CZ 2B | 0.13483 | 0.034534 | 0.28235 | 0.0033503 | 0 | 0.2242 | 0 | 0.10019 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.2271 | 1.974% | CZ 2B | 4.3276 | 1.1085 | 9.0629 | 0.34187 | 0 | 7.1964 | 0 | 3.2158 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 39.6226 | 1.974% | CZ 2B | 1.2684 | 0.32487 | 2.6562 | 0 | 0 | 2.1091 | 0 | 0.94249 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 11.5125 | 1.974% | CZ 2B | 0 | 0 | 0 | 0.0034187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034187 | 1.974% | CZ 2B | 13.2784 | 3.4011 | 27.8077 | 0.37366 | 0 | 22.0806 | 0 | 9.867 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 120.8981 | 1.974%
CZ 3A | 0.13483 | 0.034525 | 0.31789 | 0.038874 | 0 | 0.15317 | 0 | 0.078767 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.2057 | 12.99% | CZ 3A | 4.3276 | 1.1082 | 10.2034 | 3.9667 | 0 | 4.9163 | 0 | 2.5282 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 41.4199 | 12.99% | CZ 3A | 1.2684 | 0.32479 | 2.9905 | 0 | 0 | 1.4409 | 0 | 0.74098 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.9769 | 12.99% | CZ 3A | 0 | 0 | 0 | 0.039667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039667 | 12.99% | CZ 3A | 13.2784 | 3.4002 | 31.3071 | 4.3356 | 0 | 15.0845 | 0 | 7.7574 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 119.2529 | 12.99%
CZ 3B | 0.13483 | 0.034525 | 0.30835 | 0.013638 | 0 | 0.15876 | 0 | 0.087494 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.1853 | 8.593% | CZ 3B | 4.3276 | 1.1082 | 9.8974 | 1.3916 | 0 | 5.0958 | 0 | 2.8084 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 38.9985 | 8.593% | CZ 3B | 1.2684 | 0.32479 | 2.9008 | 0 | 0 | 1.4935 | 0 | 0.82309 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 11.022 | 8.593% | CZ 3B | 0 | 0 | 0 | 0.013916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013916 | 8.593% | CZ 3B | 13.2784 | 3.4002 | 30.3682 | 1.521 | 0 | 15.6354 | 0 | 8.6169 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 116.9099 | 8.593%
CZ 3C | 0.13483 | 0.034525 | 0.32149 | 0.0027777 | 0 | 0.08675 | 0 | 0.062169 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.0902 | 3.597% | CZ 3C | 4.3276 | 1.1082 | 10.3192 | 0.28344 | 0 | 2.7845 | 0 | 1.9955 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 35.1879 | 3.597% | CZ 3C | 1.2684 | 0.32479 | 3.0244 | 0 | 0 | 0.81609 | 0 | 0.58485 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.2299 | 3.597% | CZ 3C | 0 | 0 | 0 | 0.0028344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028344 | 3.597% | CZ 3C | 13.2784 | 3.4002 | 31.6622 | 0.3098 | 0 | 8.5436 | 0 | 6.1228 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 107.4067 | 3.597%
CZ 4A | 0.13483 | 0.034472 | 0.3469 | 0.08613 | 0 | 0.11477 | 0 | 0.076184 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.241 | 22.03% | CZ 4A | 4.3276 | 1.1065 | 11.1349 | 8.7888 | 0 | 3.6839 | 0 | 2.4453 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 45.8565 | 22.03% | CZ 4A | 1.2684 | 0.32429 | 3.2634 | 0 | 0 | 1.0797 | 0 | 0.71669 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.8639 | 22.03% | CZ 4A | 0 | 0 | 0 | 0.087888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087888 | 22.03% | CZ 4A | 13.2784 | 3.395 | 34.165 | 9.6062 | 0 | 11.3033 | 0 | 7.503 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 123.3406 | 22.03%
CZ 4B | 0.13483 | 0.034499 | 0.33831 | 0.029258 | 0 | 0.12592 | 0 | 0.084343 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.1948 | 0.1893% | CZ 4B | 4.3276 | 1.1073 | 10.8589 | 2.9855 | 0 | 4.0419 | 0 | 2.7072 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 40.398 | 0.189% | CZ 4B | 1.2684 | 0.32454 | 3.1826 | 0 | 0 | 1.1846 | 0 | 0.79344 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.965 | 0.189% | CZ 4B | 0 | 0 | 0 | 0.029855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029855 | 0.1893% | CZ 4B | 13.2784 | 3.3976 | 33.3184 | 3.2632 | 0 | 12.4016 | 0 | 8.3065 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 118.0554 | 0.1893%
CZ 4C | 0.13483 | 0.034437 | 0.35558 | 0.049005 | 0 | 0.049074 | 0 | 0.062073 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.1327 | 5.156% | CZ 4C | 4.3276 | 1.1054 | 11.4133 | 5.0005 | 0 | 1.5752 | 0 | 1.9924 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 39.7838 | 5.156% | CZ 4C | 1.2684 | 0.32396 | 3.3451 | 0 | 0 | 0.46165 | 0 | 0.58394 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.1944 | 5.156% | CZ 4C | 0 | 0 | 0 | 0.050005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.050005 | 5.156% | CZ 4C | 13.2784 | 3.3916 | 35.0193 | 5.4655 | 0 | 4.833 | 0 | 6.1133 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 112.1909 | 5.156%
CZ 5A | 0.13483 | 0.034481 | 0.37134 | 0.14824 | 0 | 0.068884 | 0 | 0.073891 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.2793 | 16.2% | CZ 5A | 4.3276 | 1.1068 | 11.9194 | 15.1261 | 0 | 2.211 | 0 | 2.3717 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 51.4321 | 16.2% | CZ 5A | 1.2684 | 0.32438 | 3.4934 | 0 | 0 | 0.64801 | 0 | 0.69512 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.6407 | 16.2% | CZ 5A | 0 | 0 | 0 | 0.15126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15126 | 16.2% | CZ 5A | 13.2784 | 3.3959 | 36.572 | 16.5329 | 0 | 6.784 | 0 | 7.2772 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 127.9301 | 16.2%
CZ 5B | 0.13483 | 0.03449 | 0.36414 | 0.074414 | 0 | 0.091556 | 0 | 0.080202 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.2273 | 5.323% | CZ 5B | 4.3276 | 1.1071 | 11.6881 | 7.5933 | 0 | 2.9387 | 0 | 2.5743 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 44.5986 | 5.323% | CZ 5B | 1.2684 | 0.32446 | 3.4256 | 0 | 0 | 0.8613 | 0 | 0.75449 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.8456 | 5.323% | CZ 5B | 0 | 0 | 0 | 0.075933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075933 | 5.323% | CZ 5B | 13.2784 | 3.3968 | 35.8625 | 8.2994 | 0 | 9.0169 | 0 | 7.8987 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 121.8425 | 5.323%
CZ 5C | 0.13483 | 0.034429 | 0.36939 | 0.052226 | 0 | 0.035838 | 0 | 0.058195 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.1326 | 0.04828% | CZ 5C | 4.3276 | 1.1051 | 11.8567 | 5.3291 | 0 | 1.1503 | 0 | 1.8679 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 40.0063 | 0.048% | CZ 5C | 1.2684 | 0.32388 | 3.475 | 0 | 0 | 0.33714 | 0 | 0.54746 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.1633 | 0.048% | CZ 5C | 0 | 0 | 0 | 0.053291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053291 | 0.04828% | CZ 5C | 13.2784 | 3.3907 | 36.3798 | 5.8247 | 0 | 3.5295 | 0 | 5.7314 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 112.2242 | 0.04828%
CZ 6A | 0.13483 | 0.034472 | 0.38934 | 0.22345 | 0 | 0.0727 | 0 | 0.078206 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.3807 | 4.174% | CZ 6A | 4.3276 | 1.1065 | 12.497 | 22.8014 | 0 | 2.3335 | 0 | 2.5103 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 59.9458 | 4.174% | CZ 6A | 1.2684 | 0.32429 | 3.6627 | 0 | 0 | 0.68392 | 0 | 0.73571 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.8864 | 4.174% | CZ 6A | 0 | 0 | 0 | 0.22801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22801 | 4.174% | CZ 6A | 13.2784 | 3.395 | 38.3445 | 24.922 | 0 | 7.1599 | 0 | 7.7022 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 138.8917 | 4.174%
CZ 6B | 0.13483 | 0.034446 | 0.38473 | 0.14634 | 0 | 0.058108 | 0 | 0.07502 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.2811 | 0.3776% | CZ 6B | 4.3276 | 1.1056 | 12.349 | 14.9323 | 0 | 1.8651 | 0 | 2.408 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 51.3571 | 0.378% | CZ 6B | 1.2684 | 0.32405 | 3.6193 | 0 | 0 | 0.54664 | 0 | 0.70574 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 10.6755 | 0.378% | CZ 6B | 0 | 0 | 0 | 0.14932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14932 | 0.3776% | CZ 6B | 13.2784 | 3.3924 | 37.8902 | 16.321 | 0 | 5.7228 | 0 | 7.3884 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 128.0829 | 0.3776%
CZ 7 | 0.13483 | 0.03442 | 0.41056 | 0.23186 | 0 | 0.062248 | 0 | 0.080106 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.4017 | 0.3013% | CZ 7 | 4.3276 | 1.1048 | 13.1781 | 23.6588 | 0 | 1.998 | 0 | 2.5712 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 61.2081 | 0.301% | CZ 7 | 1.2684 | 0.3238 | 3.8623 | 0 | 0 | 0.58559 | 0 | 0.75358 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 11.0051 | 0.301% | CZ 7 | 0 | 0 | 0 | 0.23659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23659 | 0.3013% | CZ 7 | 13.2784 | 3.3899 | 40.4343 | 25.859 | 0 | 6.1305 | 0 | 7.8893 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 141.0711 | 0.3013%
CZ 8 | 0.13483 | 0.034236 | 0.43939 | 0.31694 | 0 | 0.042141 | 0 | 0.085463 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.5007 | 8.036e-05% | CZ 8 | 4.3276 | 1.0989 | 14.1034 | 32.3411 | 0 | 1.3526 | 0 | 2.7432 | 0 | 0 | 0 | 3.5204 | 0 | 0 | 0 | 10.8491 | 70.3363 | 0% | CZ 8 | 1.2684 | 0.32207 | 4.1335 | 0 | 0 | 0.39643 | 0 | 0.80398 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 11.1358 | 0% | CZ 8 | 0 | 0 | 0 | 0.32341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32341 | 8.036e-05% | CZ 8 | 13.2784 | 3.3718 | 43.2733 | 35.3488 | 0 | 4.1502 | 0 | 8.4169 | 0 | 0 | 0 | 10.8015 | 0 | 0 | 0 | 33.2882 | 151.9291 | 8.036e-05%
US Weighted | 0.13482 | 0.034495 | 0.33193 | 0.067148 | 0 | 0.1446 | 0 | 0.081396 | 0 | 0 | 0 | 0.10968 | 0 | 0 | 0 | 0.338 | 1.2421 | 100% | US Weighted | 4.3276 | 1.1072 | 10.6543 | 6.8518 | 0 | 4.6414 | 0 | 2.6126 | 0 | 0 | 0 | 3.5203 | 0 | 0 | 0 | 10.849 | 44.5643 | 100% | US Weighted | 1.2683 | 0.32451 | 3.1226 | 0 | 0 | 1.3603 | 0 | 0.76572 | 0 | 0 | 0 | 1.0318 | 0 | 0 | 0 | 3.1797 | 11.0529 | 100% | US Weighted | 0 | 0 | 0 | 0.068518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.068518 | 100% | US Weighted | 13.2783 | 3.3973 | 32.6904 | 7.489 | 0 | 14.2411 | 0 | 8.0164 | 0 | 0 | 0 | 10.8014 | 0 | 0 | 0 | 33.2879 | 123.2017 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.12208 | 0.063946 | 0.24102 | 0 | 0 | 0.55641 | 0 | 0.15354 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.5901 | 0% | CZ 0A | 3.9185 | 2.0525 | 7.7362 | 0 | 0 | 17.8595 | 0 | 4.9283 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 51.0396 | 0% | CZ 0A | 1.1485 | 0.60157 | 2.2673 | 0 | 0 | 5.2343 | 0 | 1.4444 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 14.9589 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 12.0231 | 6.2978 | 23.7368 | 0 | 0 | 54.7981 | 0 | 15.1216 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 156.6042 | 0%
CZ 0B | 0.12208 | 0.063955 | 0.24003 | 2.7529e-06 | 0 | 0.49985 | 0 | 0.15076 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.5298 | 0% | CZ 0B | 3.9185 | 2.0528 | 7.7044 | 0.00028091 | 0 | 16.0441 | 0 | 4.839 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 49.1037 | 0% | CZ 0B | 1.1485 | 0.60165 | 2.258 | 0 | 0 | 4.7023 | 0 | 1.4182 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 14.3914 | 0% | CZ 0B | 0 | 0 | 0 | 2.8091e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8091e-06 | 0% | CZ 0B | 12.0231 | 6.2987 | 23.6393 | 0.00030703 | 0 | 49.228 | 0 | 14.8474 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 150.6637 | 0%
CZ 1A | 0.12208 | 0.063964 | 0.25953 | 0 | 0 | 0.37551 | 0 | 0.12366 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3979 | 2.646% | CZ 1A | 3.9185 | 2.0531 | 8.3304 | 0 | 0 | 12.0531 | 0 | 3.9694 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 44.8691 | 2.646% | CZ 1A | 1.1485 | 0.60173 | 2.4415 | 0 | 0 | 3.5326 | 0 | 1.1634 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 13.1504 | 2.646% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.646% | CZ 1A | 12.0231 | 6.2995 | 25.5602 | 0 | 0 | 36.9824 | 0 | 12.1792 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 137.6712 | 2.646%
CZ 1B | 0.12208 | 0.063885 | 0.26029 | 0.0020014 | 0 | 0.3789 | 0 | 0.13182 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.4121 | 0% | CZ 1B | 3.9185 | 2.0506 | 8.3549 | 0.20422 | 0 | 12.1618 | 0 | 4.2312 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 45.4658 | 0% | CZ 1B | 1.1485 | 0.60099 | 2.4487 | 0 | 0 | 3.5644 | 0 | 1.2401 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 13.2654 | 0% | CZ 1B | 0 | 0 | 0 | 0.0020422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020422 | 0% | CZ 1B | 12.0231 | 6.2918 | 25.6352 | 0.22321 | 0 | 37.316 | 0 | 12.9827 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 139.0988 | 0%
CZ 2A | 0.12208 | 0.063868 | 0.28101 | 0.0048699 | 0 | 0.28934 | 0 | 0.10125 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3155 | 16.39% | CZ 2A | 3.9185 | 2.05 | 9.0197 | 0.49693 | 0 | 9.2872 | 0 | 3.2498 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 42.5666 | 16.39% | CZ 2A | 1.1485 | 0.60082 | 2.6435 | 0 | 0 | 2.7219 | 0 | 0.95246 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 12.3299 | 16.39% | CZ 2A | 0 | 0 | 0 | 0.0049693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049693 | 16.39% | CZ 2A | 12.0231 | 6.29 | 27.6749 | 0.54314 | 0 | 28.4957 | 0 | 9.9713 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 129.625 | 16.39%
CZ 2B | 0.12208 | 0.063911 | 0.28241 | 0.0042147 | 0 | 0.229 | 0 | 0.10456 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2593 | 1.974% | CZ 2B | 3.9185 | 2.0514 | 9.0646 | 0.43007 | 0 | 7.3504 | 0 | 3.3563 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 40.7158 | 1.974% | CZ 2B | 1.1485 | 0.60124 | 2.6567 | 0 | 0 | 2.1543 | 0 | 0.98367 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.8071 | 1.974% | CZ 2B | 0 | 0 | 0 | 0.0043007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043007 | 1.974% | CZ 2B | 12.0231 | 6.2943 | 27.8129 | 0.47007 | 0 | 22.5531 | 0 | 10.298 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 124.0783 | 1.974%
CZ 3A | 0.12208 | 0.063894 | 0.31801 | 0.05225 | 0 | 0.15414 | 0 | 0.082076 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2456 | 12.99% | CZ 3A | 3.9185 | 2.0509 | 10.2074 | 5.3317 | 0 | 4.9475 | 0 | 2.6344 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 43.6348 | 12.99% | CZ 3A | 1.1485 | 0.60107 | 2.9916 | 0 | 0 | 1.45 | 0 | 0.77211 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.226 | 12.99% | CZ 3A | 0 | 0 | 0 | 0.053317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053317 | 12.99% | CZ 3A | 12.0231 | 6.2926 | 31.3191 | 5.8275 | 0 | 15.1802 | 0 | 8.0832 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 123.3527 | 12.99%
CZ 3B | 0.12208 | 0.063894 | 0.30846 | 0.017313 | 0 | 0.15981 | 0 | 0.091127 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2158 | 8.593% | CZ 3B | 3.9185 | 2.0509 | 9.9008 | 1.7666 | 0 | 5.1295 | 0 | 2.925 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 40.2359 | 8.593% | CZ 3B | 1.1485 | 0.60107 | 2.9018 | 0 | 0 | 1.5034 | 0 | 0.85726 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.2747 | 8.593% | CZ 3B | 0 | 0 | 0 | 0.017666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017666 | 8.593% | CZ 3B | 12.0231 | 6.2926 | 30.3785 | 1.9309 | 0 | 15.7389 | 0 | 8.9747 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 119.9656 | 8.593%
CZ 3C | 0.12208 | 0.063885 | 0.32156 | 0.0037192 | 0 | 0.083152 | 0 | 0.062388 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.1099 | 3.597% | CZ 3C | 3.9185 | 2.0506 | 10.3214 | 0.37951 | 0 | 2.669 | 0 | 2.0025 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 35.8861 | 3.597% | CZ 3C | 1.1485 | 0.60099 | 3.025 | 0 | 0 | 0.78224 | 0 | 0.58691 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.4064 | 3.597% | CZ 3C | 0 | 0 | 0 | 0.0037951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037951 | 3.597% | CZ 3C | 12.0231 | 6.2918 | 31.6691 | 0.4148 | 0 | 8.1893 | 0 | 6.1443 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 109.3593 | 3.597%
CZ 4A | 0.12208 | 0.063798 | 0.34706 | 0.11872 | 0 | 0.11165 | 0 | 0.078679 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2951 | 22.03% | CZ 4A | 3.9185 | 2.0478 | 11.1399 | 12.1145 | 0 | 3.5839 | 0 | 2.5254 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 49.8745 | 22.03% | CZ 4A | 1.1485 | 0.60017 | 3.2649 | 0 | 0 | 1.0504 | 0 | 0.74016 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.0668 | 22.03% | CZ 4A | 0 | 0 | 0 | 0.12115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12115 | 22.03% | CZ 4A | 12.0231 | 6.2831 | 34.1805 | 13.2412 | 0 | 10.9963 | 0 | 7.7487 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 129.0998 | 22.03%
CZ 4B | 0.12208 | 0.06385 | 0.33847 | 0.039559 | 0 | 0.11973 | 0 | 0.086566 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2234 | 0.1893% | CZ 4B | 3.9185 | 2.0495 | 10.864 | 4.0367 | 0 | 3.8432 | 0 | 2.7786 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 42.035 | 0.189% | CZ 4B | 1.1485 | 0.60066 | 3.1841 | 0 | 0 | 1.1264 | 0 | 0.81436 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.1367 | 0.189% | CZ 4B | 0 | 0 | 0 | 0.040367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040367 | 0.189% | CZ 4B | 12.0231 | 6.2883 | 33.3339 | 4.4121 | 0 | 11.7921 | 0 | 8.5255 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 121.0018 | 0.1893%
CZ 4C | 0.12208 | 0.063728 | 0.35581 | 0.066777 | 0 | 0.041519 | 0 | 0.06315 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.1662 | 5.156% | CZ 4C | 3.9185 | 2.0455 | 11.4206 | 6.814 | 0 | 1.3327 | 0 | 2.027 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 42.1029 | 5.156% | CZ 4C | 1.1485 | 0.59951 | 3.3472 | 0 | 0 | 0.39059 | 0 | 0.59407 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.3426 | 5.156% | CZ 4C | 0 | 0 | 0 | 0.06814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06814 | 5.156% | CZ 4C | 12.0231 | 6.2762 | 35.0418 | 7.4477 | 0 | 4.089 | 0 | 6.2193 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 115.7241 | 5.156%
CZ 5A | 0.12208 | 0.063824 | 0.37149 | 0.19525 | 0 | 0.06427 | 0 | 0.076744 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3468 | 16.2% | CZ 5A | 3.9185 | 2.0486 | 11.9241 | 19.9235 | 0 | 2.0629 | 0 | 2.4633 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 56.8856 | 16.2% | CZ 5A | 1.1485 | 0.60041 | 3.4948 | 0 | 0 | 0.60461 | 0 | 0.72196 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.833 | 16.2% | CZ 5A | 0 | 0 | 0 | 0.19924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19924 | 16.2% | CZ 5A | 12.0231 | 6.2857 | 36.5867 | 21.7764 | 0 | 6.3297 | 0 | 7.5582 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 135.1867 | 16.2%
CZ 5B | 0.12208 | 0.063824 | 0.36431 | 0.095578 | 0 | 0.085761 | 0 | 0.08338 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2681 | 5.323% | CZ 5B | 3.9185 | 2.0486 | 11.6935 | 9.7529 | 0 | 2.7527 | 0 | 2.6763 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 47.3871 | 5.323% | CZ 5B | 1.1485 | 0.60041 | 3.4272 | 0 | 0 | 0.80678 | 0 | 0.78438 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.0299 | 5.323% | CZ 5B | 0 | 0 | 0 | 0.097529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097529 | 5.323% | CZ 5B | 12.0231 | 6.2857 | 35.8789 | 10.6599 | 0 | 8.4462 | 0 | 8.2117 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 126.1324 | 5.323%
CZ 5C | 0.12208 | 0.063719 | 0.36957 | 0.062863 | 0 | 0.029071 | 0 | 0.05886 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.1593 | 0.04828% | CZ 5C | 3.9185 | 2.0452 | 11.8623 | 6.4146 | 0 | 0.93313 | 0 | 1.8893 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 41.6076 | 0.048% | CZ 5C | 1.1485 | 0.59942 | 3.4766 | 0 | 0 | 0.27348 | 0 | 0.55372 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.3145 | 0.048% | CZ 5C | 0 | 0 | 0 | 0.064146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064146 | 0.048% | CZ 5C | 12.0231 | 6.2754 | 36.397 | 7.0111 | 0 | 2.8631 | 0 | 5.7969 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 114.9935 | 0.04828%
CZ 6A | 0.12208 | 0.063789 | 0.38948 | 0.28424 | 0 | 0.068849 | 0 | 0.082321 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.4639 | 4.174% | CZ 6A | 3.9185 | 2.0475 | 12.5015 | 29.0042 | 0 | 2.2099 | 0 | 2.6423 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 66.8685 | 4.174% | CZ 6A | 1.1485 | 0.60008 | 3.664 | 0 | 0 | 0.64768 | 0 | 0.77442 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.0974 | 4.174% | CZ 6A | 0 | 0 | 0 | 0.29004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29004 | 4.174% | CZ 6A | 12.0231 | 6.2823 | 38.3583 | 31.7016 | 0 | 6.7806 | 0 | 8.1074 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 147.8801 | 4.174%
CZ 6B | 0.12208 | 0.063745 | 0.38492 | 0.18759 | 0 | 0.052531 | 0 | 0.079134 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3431 | 0.3776% | CZ 6B | 3.9185 | 2.0461 | 12.3552 | 19.142 | 0 | 1.6861 | 0 | 2.54 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 56.2325 | 0.378% | CZ 6B | 1.1485 | 0.59967 | 3.6211 | 0 | 0 | 0.49418 | 0 | 0.74444 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.8706 | 0.378% | CZ 6B | 0 | 0 | 0 | 0.19142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19142 | 0.378% | CZ 6B | 12.0231 | 6.278 | 37.9092 | 20.9222 | 0 | 5.1736 | 0 | 7.7936 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 134.7265 | 0.3776%
CZ 7 | 0.12208 | 0.063701 | 0.41069 | 0.28048 | 0 | 0.057206 | 0 | 0.08338 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.4707 | 0.3013% | CZ 7 | 3.9185 | 2.0447 | 13.1824 | 28.6205 | 0 | 1.8362 | 0 | 2.6763 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 66.8231 | 0.301% | CZ 7 | 1.1485 | 0.59926 | 3.8635 | 0 | 0 | 0.53816 | 0 | 0.78438 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.1965 | 0.301% | CZ 7 | 0 | 0 | 0 | 0.2862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2862 | 0.301% | CZ 7 | 12.0231 | 6.2737 | 40.4473 | 31.2822 | 0 | 5.634 | 0 | 8.2117 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 148.4987 | 0.3013%
CZ 8 | 0.12208 | 0.063351 | 0.4395 | 0.35023 | 0 | 0.036678 | 0 | 0.089131 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.5541 | 8.036e-05% | CZ 8 | 3.9185 | 2.0334 | 14.107 | 35.7376 | 0 | 1.1773 | 0 | 2.8609 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 74.3793 | 0% | CZ 8 | 1.1485 | 0.59597 | 4.1345 | 0 | 0 | 0.34505 | 0 | 0.83849 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.3252 | 0% | CZ 8 | 0 | 0 | 0 | 0.35738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35738 | 0% | CZ 8 | 12.0231 | 6.2392 | 43.2845 | 39.0612 | 0 | 3.6123 | 0 | 8.7781 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 157.6252 | 8.036e-05%
US Weighted | 0.12208 | 0.06384 | 0.33206 | 0.089143 | 0 | 0.14384 | 0 | 0.084313 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2884 | 100% | US Weighted | 3.9185 | 2.0491 | 10.6583 | 9.0962 | 0 | 4.6168 | 0 | 2.7063 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9035 | 47.5896 | 100% | US Weighted | 1.1484 | 0.60057 | 3.1238 | 0 | 0 | 1.3531 | 0 | 0.79316 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1956 | 11.2818 | 100% | US Weighted | 0 | 0 | 0 | 0.090962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.090962 | 100% | US Weighted | 12.023 | 6.2873 | 32.7028 | 9.9421 | 0 | 14.1658 | 0 | 8.3036 | 0 | 0 | 0 | 11.1712 | 0 | 0 | 0 | 33.4551 | 128.0511 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 33741 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.12208 | 0.063946 | 0.24103 | 0 | 0 | 0.68087 | 0 | 0.15499 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.716 | 0% | CZ 0A | 3.9185 | 2.0525 | 7.7364 | 0 | 0 | 21.8544 | 0 | 4.975 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 55.0815 | 0% | CZ 0A | 1.1485 | 0.60157 | 2.2674 | 0 | 0 | 6.4052 | 0 | 1.4581 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 16.1435 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 12.0231 | 6.2978 | 23.7376 | 0 | 0 | 67.0557 | 0 | 15.2647 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 169.0058 | 0%
CZ 0B | 0.12208 | 0.063955 | 0.24004 | 8.2587e-06 | 0 | 0.61081 | 0 | 0.15172 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.6417 | 0% | CZ 0B | 3.9185 | 2.0528 | 7.7047 | 0.00084273 | 0 | 19.6058 | 0 | 4.8699 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 52.6971 | 0% | CZ 0B | 1.1485 | 0.60165 | 2.2581 | 0 | 0 | 5.7461 | 0 | 1.4273 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 15.4444 | 0% | CZ 0B | 0 | 0 | 0 | 8.4273e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4273e-06 | 0% | CZ 0B | 12.0231 | 6.2987 | 23.6402 | 0.0009211 | 0 | 60.1562 | 0 | 14.9423 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 161.6882 | 0%
CZ 1A | 0.12208 | 0.063964 | 0.25953 | 0 | 0 | 0.45872 | 0 | 0.12456 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.482 | 2.646% | CZ 1A | 3.9185 | 2.0531 | 8.3304 | 0 | 0 | 14.7238 | 0 | 3.998 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 47.5684 | 2.646% | CZ 1A | 1.1485 | 0.60173 | 2.4415 | 0 | 0 | 4.3153 | 0 | 1.1718 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 13.9415 | 2.646% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.646% | CZ 1A | 12.0231 | 6.2995 | 25.5602 | 0 | 0 | 45.1768 | 0 | 12.2671 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 145.9536 | 2.646%
CZ 1B | 0.12208 | 0.063885 | 0.26031 | 0.0027336 | 0 | 0.46347 | 0 | 0.13302 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.4986 | 0% | CZ 1B | 3.9185 | 2.0506 | 8.3554 | 0.27894 | 0 | 14.8764 | 0 | 4.2697 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 48.2941 | 0% | CZ 1B | 1.1485 | 0.60099 | 2.4488 | 0 | 0 | 4.36 | 0 | 1.2514 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 14.0724 | 0% | CZ 1B | 0 | 0 | 0 | 0.0027894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027894 | 0% | CZ 1B | 12.0231 | 6.2918 | 25.6369 | 0.30488 | 0 | 45.645 | 0 | 13.1008 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 147.6292 | 0%
CZ 2A | 0.12208 | 0.063868 | 0.28113 | 0.0096022 | 0 | 0.36748 | 0 | 0.10885 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.4061 | 16.39% | CZ 2A | 3.9185 | 2.05 | 9.0236 | 0.97981 | 0 | 11.7952 | 0 | 3.494 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 45.8056 | 16.39% | CZ 2A | 1.1485 | 0.60082 | 2.6447 | 0 | 0 | 3.457 | 0 | 1.024 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 13.1377 | 16.39% | CZ 2A | 0 | 0 | 0 | 0.0097981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097981 | 16.39% | CZ 2A | 12.0231 | 6.29 | 27.687 | 1.0709 | 0 | 36.191 | 0 | 10.7205 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 138.6094 | 16.39%
CZ 2B | 0.12208 | 0.063911 | 0.2826 | 0.0099215 | 0 | 0.29996 | 0 | 0.11308 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3447 | 1.974% | CZ 2B | 3.9185 | 2.0514 | 9.0708 | 1.0124 | 0 | 9.628 | 0 | 3.6297 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 43.8553 | 1.974% | CZ 2B | 1.1485 | 0.60124 | 2.6585 | 0 | 0 | 2.8218 | 0 | 1.0638 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 12.5565 | 1.974% | CZ 2B | 0 | 0 | 0 | 0.010124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010124 | 1.974% | CZ 2B | 12.0231 | 6.2943 | 27.8318 | 1.1066 | 0 | 29.5414 | 0 | 11.1369 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 132.561 | 1.974%
CZ 3A | 0.12208 | 0.063894 | 0.31796 | 0.052465 | 0 | 0.20498 | 0 | 0.08766 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3022 | 12.99% | CZ 3A | 3.9185 | 2.0509 | 10.2057 | 5.3536 | 0 | 6.5794 | 0 | 2.8137 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 45.4662 | 12.99% | CZ 3A | 1.1485 | 0.60107 | 2.9911 | 0 | 0 | 1.9283 | 0 | 0.82465 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.7563 | 12.99% | CZ 3A | 0 | 0 | 0 | 0.053536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053536 | 12.99% | CZ 3A | 12.0231 | 6.2926 | 31.3139 | 5.8515 | 0 | 20.1874 | 0 | 8.6333 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 128.9287 | 12.99%
CZ 3B | 0.12208 | 0.063894 | 0.3084 | 0.018343 | 0 | 0.21792 | 0 | 0.098384 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2822 | 8.593% | CZ 3B | 3.9185 | 2.0509 | 9.8991 | 1.8717 | 0 | 6.9947 | 0 | 3.1579 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 42.4373 | 8.593% | CZ 3B | 1.1485 | 0.60107 | 2.9013 | 0 | 0 | 2.05 | 0 | 0.92553 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.8891 | 8.593% | CZ 3B | 0 | 0 | 0 | 0.018717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018717 | 8.593% | CZ 3B | 12.0231 | 6.2926 | 30.3734 | 2.0458 | 0 | 21.4616 | 0 | 9.6894 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 126.5127 | 8.593%
CZ 3C | 0.12208 | 0.063885 | 0.32148 | 0.0046965 | 0 | 0.17605 | 0 | 0.085078 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2264 | 3.597% | CZ 3C | 3.9185 | 2.0506 | 10.3189 | 0.47923 | 0 | 5.6507 | 0 | 2.7308 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 39.6933 | 3.597% | CZ 3C | 1.1485 | 0.60099 | 3.0243 | 0 | 0 | 1.6561 | 0 | 0.80036 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.493 | 3.597% | CZ 3C | 0 | 0 | 0 | 0.0047923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047923 | 3.597% | CZ 3C | 12.0231 | 6.2918 | 31.6614 | 0.5238 | 0 | 17.3381 | 0 | 8.379 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 120.844 | 3.597%
CZ 4A | 0.12208 | 0.063798 | 0.34713 | 0.13636 | 0 | 0.1312 | 0 | 0.07881 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3325 | 22.03% | CZ 4A | 3.9185 | 2.0478 | 11.1422 | 13.914 | 0 | 4.2113 | 0 | 2.5296 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 52.3079 | 22.03% | CZ 4A | 1.1485 | 0.60017 | 3.2656 | 0 | 0 | 1.2343 | 0 | 0.7414 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.2526 | 22.03% | CZ 4A | 0 | 0 | 0 | 0.13914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13914 | 22.03% | CZ 4A | 12.0231 | 6.2831 | 34.1874 | 15.208 | 0 | 12.9215 | 0 | 7.7617 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 133.0116 | 22.03%
CZ 4B | 0.12208 | 0.06385 | 0.3386 | 0.05143 | 0 | 0.13953 | 0 | 0.086838 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.2555 | 0.1893% | CZ 4B | 3.9185 | 2.0495 | 10.8682 | 5.248 | 0 | 4.4785 | 0 | 2.7873 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 43.8945 | 0.189% | CZ 4B | 1.1485 | 0.60066 | 3.1853 | 0 | 0 | 1.3126 | 0 | 0.81691 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.3266 | 0.189% | CZ 4B | 0 | 0 | 0 | 0.05248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05248 | 0.189% | CZ 4B | 12.0231 | 6.2883 | 33.3468 | 5.736 | 0 | 13.7413 | 0 | 8.5522 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 124.3147 | 0.1893%
CZ 4C | 0.12208 | 0.063728 | 0.35596 | 0.082549 | 0 | 0.045196 | 0 | 0.063036 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.1857 | 5.156% | CZ 4C | 3.9185 | 2.0455 | 11.4257 | 8.4234 | 0 | 1.4507 | 0 | 2.0233 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 43.8316 | 5.156% | CZ 4C | 1.1485 | 0.59951 | 3.3487 | 0 | 0 | 0.42517 | 0 | 0.593 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.3776 | 5.156% | CZ 4C | 0 | 0 | 0 | 0.084234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084234 | 5.156% | CZ 4C | 12.0231 | 6.2762 | 35.0573 | 9.2067 | 0 | 4.4511 | 0 | 6.2081 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 117.8495 | 5.156%
CZ 5A | 0.12208 | 0.063824 | 0.37159 | 0.22225 | 0 | 0.072945 | 0 | 0.076508 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3823 | 16.2% | CZ 5A | 3.9185 | 2.0486 | 11.9272 | 22.6787 | 0 | 2.3414 | 0 | 2.4557 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 59.9147 | 16.2% | CZ 5A | 1.1485 | 0.60041 | 3.4957 | 0 | 0 | 0.68622 | 0 | 0.71974 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.9133 | 16.2% | CZ 5A | 0 | 0 | 0 | 0.22679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22679 | 16.2% | CZ 5A | 12.0231 | 6.2857 | 36.5962 | 24.7878 | 0 | 7.1841 | 0 | 7.5349 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 139.0386 | 16.2%
CZ 5B | 0.12208 | 0.063824 | 0.36443 | 0.11867 | 0 | 0.097561 | 0 | 0.082872 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3026 | 5.323% | CZ 5B | 3.9185 | 2.0486 | 11.6974 | 12.1089 | 0 | 3.1315 | 0 | 2.66 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 50.1094 | 5.323% | CZ 5B | 1.1485 | 0.60041 | 3.4283 | 0 | 0 | 0.91779 | 0 | 0.77961 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.1373 | 5.323% | CZ 5B | 0 | 0 | 0 | 0.12109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12109 | 5.323% | CZ 5B | 12.0231 | 6.2857 | 35.8909 | 13.235 | 0 | 9.6083 | 0 | 8.1617 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 129.8317 | 5.323%
CZ 5C | 0.12208 | 0.063719 | 0.36981 | 0.084336 | 0 | 0.029089 | 0 | 0.05872 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.1809 | 0.04828% | CZ 5C | 3.9185 | 2.0452 | 11.8702 | 8.6057 | 0 | 0.93369 | 0 | 1.8848 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 43.8026 | 0.048% | CZ 5C | 1.1485 | 0.59942 | 3.479 | 0 | 0 | 0.27365 | 0 | 0.5524 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.3156 | 0.048% | CZ 5C | 0 | 0 | 0 | 0.086057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086057 | 0.048% | CZ 5C | 12.0231 | 6.2754 | 36.4212 | 9.406 | 0 | 2.8648 | 0 | 5.7831 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 117.4004 | 0.04828%
CZ 6A | 0.12208 | 0.063789 | 0.38956 | 0.31867 | 0 | 0.078486 | 0 | 0.084474 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.5102 | 4.174% | CZ 6A | 3.9185 | 2.0475 | 12.5041 | 32.5173 | 0 | 2.5192 | 0 | 2.7114 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 70.7625 | 4.174% | CZ 6A | 1.1485 | 0.60008 | 3.6647 | 0 | 0 | 0.73835 | 0 | 0.79468 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.2091 | 4.174% | CZ 6A | 0 | 0 | 0 | 0.32517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32517 | 4.174% | CZ 6A | 12.0231 | 6.2823 | 38.3661 | 35.5414 | 0 | 7.7298 | 0 | 8.3195 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 152.8889 | 4.174%
CZ 6B | 0.12208 | 0.063745 | 0.38504 | 0.21932 | 0 | 0.058878 | 0 | 0.079126 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3813 | 0.3776% | CZ 6B | 3.9185 | 2.0461 | 12.3591 | 22.3801 | 0 | 1.8899 | 0 | 2.5398 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 59.6779 | 0.378% | CZ 6B | 1.1485 | 0.59967 | 3.6222 | 0 | 0 | 0.55389 | 0 | 0.74436 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 10.9314 | 0.378% | CZ 6B | 0 | 0 | 0 | 0.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2238 | 0.378% | CZ 6B | 12.0231 | 6.278 | 37.9212 | 24.4614 | 0 | 5.7986 | 0 | 7.7927 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 138.9019 | 0.3776%
CZ 7 | 0.12208 | 0.063701 | 0.41078 | 0.34117 | 0 | 0.067816 | 0 | 0.088527 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.5472 | 0.3013% | CZ 7 | 3.9185 | 2.0447 | 13.1852 | 34.8131 | 0 | 2.1767 | 0 | 2.8415 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 73.5243 | 0.301% | CZ 7 | 1.1485 | 0.59926 | 3.8643 | 0 | 0 | 0.63796 | 0 | 0.8328 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.3456 | 0.301% | CZ 7 | 0 | 0 | 0 | 0.34813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34813 | 0.301% | CZ 7 | 12.0231 | 6.2737 | 40.4559 | 38.0507 | 0 | 6.6788 | 0 | 8.7186 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 156.8277 | 0.3013%
CZ 8 | 0.12208 | 0.063351 | 0.43955 | 0.38907 | 0 | 0.041502 | 0 | 0.090488 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.5992 | 8.036e-05% | CZ 8 | 3.9185 | 2.0334 | 14.1087 | 39.7012 | 0 | 1.3321 | 0 | 2.9045 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9036 | 78.543 | 0% | CZ 8 | 1.1485 | 0.59597 | 4.135 | 0 | 0 | 0.39042 | 0 | 0.85125 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1957 | 11.3839 | 0% | CZ 8 | 0 | 0 | 0 | 0.39701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39701 | 0% | CZ 8 | 12.0231 | 6.2392 | 43.2897 | 43.3935 | 0 | 4.0873 | 0 | 8.9117 | 0 | 0 | 0 | 11.1714 | 0 | 0 | 0 | 33.4555 | 162.5713 | 8.036e-05%
US Weighted | 0.12208 | 0.06384 | 0.33212 | 0.10226 | 0 | 0.18221 | 0 | 0.08798 | 0 | 0 | 0 | 0.11343 | 0 | 0 | 0 | 0.3397 | 1.3436 | 100% | US Weighted | 3.9185 | 2.0491 | 10.6602 | 10.4345 | 0 | 5.8486 | 0 | 2.824 | 0 | 0 | 0 | 3.6409 | 0 | 0 | 0 | 10.9035 | 50.2793 | 100% | US Weighted | 1.1484 | 0.60057 | 3.1243 | 0 | 0 | 1.7141 | 0 | 0.82766 | 0 | 0 | 0 | 1.0671 | 0 | 0 | 0 | 3.1956 | 11.6778 | 100% | US Weighted | 0 | 0 | 0 | 0.10435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10435 | 100% | US Weighted | 12.023 | 6.2873 | 32.7087 | 11.4049 | 0 | 17.9452 | 0 | 8.6648 | 0 | 0 | 0 | 11.1712 | 0 | 0 | 0 | 33.4551 | 133.6603 | 100%
Building Type: | Mid-rise Apartment |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 33741 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 33741 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.049047 | 0.041204 | 0.00020134 | 0 | 0 | 0.33313 | 0 | 0.041896 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.47122 | 0% | CZ 0A | 1.5743 | 1.3226 | 0.0064625 | 0 | 0 | 10.6926 | 0 | 1.3448 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 15.125 | 0% | CZ 0A | 0.46141 | 0.38762 | 0.001894 | 0 | 0 | 3.1338 | 0 | 0.39413 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 4.4329 | 0% | CZ 0A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | CZ 0A | 4.8305 | 4.058 | 0.019829 | 0 | 0 | 32.808 | 0 | 4.1261 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 46.408 | 0%
CZ 0B | 0.049047 | 0.041204 | 0.00028888 | 8.2587e-06 | 0 | 0.27695 | 0 | 0.035908 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.40915 | 0% | CZ 0B | 1.5743 | 1.3226 | 0.0092723 | 0.00084273 | 0 | 8.8896 | 0 | 1.1526 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 13.1335 | 0% | CZ 0B | 0.46141 | 0.38762 | 0.0027175 | 0 | 0 | 2.6054 | 0 | 0.3378 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 3.849 | 0% | CZ 0B | 0 | 0 | 0 | 8.4273e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4273e-06 | 0% | CZ 0B | 4.8305 | 4.058 | 0.02845 | 0.0009211 | 0 | 27.2758 | 0 | 3.5364 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 40.2956 | 0%
CZ 1A | 0.049047 | 0.041213 | 0.00053398 | 0 | 0 | 0.21526 | 0 | 0.028354 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.34015 | 2.646% | CZ 1A | 1.5743 | 1.3228 | 0.01714 | 0 | 0 | 6.9092 | 0 | 0.91009 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 10.918 | 2.646% | CZ 1A | 0.46141 | 0.3877 | 0.0050233 | 0 | 0 | 2.025 | 0 | 0.26673 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 3.1999 | 2.646% | CZ 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.646% | CZ 1A | 4.8305 | 4.0589 | 0.052589 | 0 | 0 | 21.1995 | 0 | 2.7924 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 33.4994 | 2.646%
CZ 1B | 0.049047 | 0.04116 | 0.00042018 | 0.0023427 | 0 | 0.20445 | 0 | 0.029071 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.33224 | 0% | CZ 1B | 1.5743 | 1.3212 | 0.013487 | 0.23905 | 0 | 6.5625 | 0 | 0.93313 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 10.828 | 0% | CZ 1B | 0.46141 | 0.38721 | 0.0039528 | 0 | 0 | 1.9234 | 0 | 0.27348 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 3.1034 | 0% | CZ 1B | 0 | 0 | 0 | 0.0023905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023905 | 0% | CZ 1B | 4.8305 | 4.0537 | 0.041382 | 0.26129 | 0 | 20.1357 | 0 | 2.8631 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 32.7512 | 0%
CZ 2A | 0.049047 | 0.041152 | 0.00078784 | 0.0090598 | 0 | 0.1715 | 0 | 0.026515 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.30381 | 16.39% | CZ 2A | 1.5743 | 1.3209 | 0.025288 | 0.92447 | 0 | 5.5049 | 0 | 0.85108 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 10.3853 | 16.39% | CZ 2A | 0.46141 | 0.38713 | 0.0074115 | 0 | 0 | 1.6134 | 0 | 0.24944 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 2.7728 | 16.39% | CZ 2A | 0 | 0 | 0 | 0.0092447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092447 | 16.39% | CZ 2A | 4.8305 | 4.0528 | 0.077591 | 1.0104 | 0 | 16.8907 | 0 | 2.6114 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 30.0389 | 16.39%
CZ 2B | 0.049047 | 0.041178 | 0.00077033 | 0.0091177 | 0 | 0.12212 | 0 | 0.022086 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.25007 | 1.974% | CZ 2B | 1.5743 | 1.3217 | 0.024726 | 0.93037 | 0 | 3.9199 | 0 | 0.70891 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 8.6643 | 1.974% | CZ 2B | 0.46141 | 0.38737 | 0.0072468 | 0 | 0 | 1.1489 | 0 | 0.20777 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 2.2667 | 1.974% | CZ 2B | 0 | 0 | 0 | 0.0093037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0093037 | 1.974% | CZ 2B | 4.8305 | 4.0554 | 0.075867 | 1.0169 | 0 | 12.0274 | 0 | 2.1751 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 24.7468 | 1.974%
CZ 3A | 0.049047 | 0.041169 | 0.00085787 | 0.040839 | 0 | 0.088422 | 0 | 0.018908 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.24499 | 12.99% | CZ 3A | 1.5743 | 1.3214 | 0.027536 | 4.1673 | 0 | 2.8382 | 0 | 0.60691 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 10.72 | 12.99% | CZ 3A | 0.46141 | 0.38729 | 0.0080703 | 0 | 0 | 0.83182 | 0 | 0.17788 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.9205 | 12.99% | CZ 3A | 0 | 0 | 0 | 0.041673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041673 | 12.99% | CZ 3A | 4.8305 | 4.0546 | 0.084488 | 4.5549 | 0 | 8.7083 | 0 | 1.8622 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 24.6604 | 12.99%
CZ 3B | 0.049047 | 0.041169 | 0.00078784 | 0.015411 | 0 | 0.084789 | 0 | 0.016623 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.21357 | 8.593% | CZ 3B | 1.5743 | 1.3214 | 0.025288 | 1.5725 | 0 | 2.7216 | 0 | 0.53358 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 7.933 | 8.593% | CZ 3B | 0.46141 | 0.38729 | 0.0074115 | 0 | 0 | 0.79764 | 0 | 0.15638 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.8642 | 8.593% | CZ 3B | 0 | 0 | 0 | 0.015725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015725 | 8.593% | CZ 3B | 4.8305 | 4.0546 | 0.077591 | 1.7188 | 0 | 8.3505 | 0 | 1.6372 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 21.2346 | 8.593%
CZ 3C | 0.049047 | 0.04116 | 0.00057775 | 0.0028988 | 0 | 0.11706 | 0 | 0.032231 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.24871 | 3.597% | CZ 3C | 1.5743 | 1.3212 | 0.018545 | 0.2958 | 0 | 3.7572 | 0 | 1.0346 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 8.1859 | 3.597% | CZ 3C | 0.46141 | 0.38721 | 0.0054351 | 0 | 0 | 1.1012 | 0 | 0.30321 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 2.3125 | 3.597% | CZ 3C | 0 | 0 | 0 | 0.002958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002958 | 3.597% | CZ 3C | 4.8305 | 4.0537 | 0.0569 | 0.32331 | 0 | 11.5283 | 0 | 3.1743 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 24.5325 | 3.597%
CZ 4A | 0.049047 | 0.041108 | 0.00095416 | 0.10155 | 0 | 0.047673 | 0 | 0.015757 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.26183 | 22.03% | CZ 4A | 1.5743 | 1.3195 | 0.030627 | 10.3622 | 0 | 1.5302 | 0 | 0.50576 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 15.5069 | 22.03% | CZ 4A | 0.46141 | 0.38671 | 0.0089761 | 0 | 0 | 0.44848 | 0 | 0.14823 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.5078 | 22.03% | CZ 4A | 0 | 0 | 0 | 0.10362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10362 | 22.03% | CZ 4A | 4.8305 | 4.0485 | 0.093971 | 11.3259 | 0 | 4.6951 | 0 | 1.5518 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 27.1113 | 22.03%
CZ 4B | 0.049047 | 0.041143 | 0.0010154 | 0.041575 | 0 | 0.03639 | 0 | 0.011713 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.18662 | 0.1893% | CZ 4B | 1.5743 | 1.3206 | 0.032593 | 4.2423 | 0 | 1.168 | 0 | 0.37595 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 8.8981 | 0.189% | CZ 4B | 0.46141 | 0.38704 | 0.0095526 | 0 | 0 | 0.34233 | 0 | 0.11018 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.3645 | 0.189% | CZ 4B | 0 | 0 | 0 | 0.042423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042423 | 0.189% | CZ 4B | 4.8305 | 4.052 | 0.10001 | 4.6368 | 0 | 3.5838 | 0 | 1.1535 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 18.9222 | 0.1893%
CZ 4C | 0.049047 | 0.041064 | 0.0012605 | 0.068481 | 0 | -0.0019959 | 0 | 0.0071343 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.17073 | 5.156% | CZ 4C | 1.5743 | 1.3181 | 0.040461 | 6.9879 | 0 | -0.064063 | 0 | 0.229 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 10.27 | 5.156% | CZ 4C | 0.46141 | 0.3863 | 0.011858 | 0 | 0 | -0.018776 | 0 | 0.067115 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 0.96193 | 5.156% | CZ 4C | 0 | 0 | 0 | 0.069879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069879 | 5.156% | CZ 4C | 4.8305 | 4.0442 | 0.12415 | 7.6378 | 0 | -0.19656 | 0 | 0.70263 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 17.7082 | 5.156%
CZ 5A | 0.049047 | 0.041125 | 0.00098918 | 0.15792 | 0 | 0.018681 | 0 | 0.015871 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.28937 | 16.2% | CZ 5A | 1.5743 | 1.32 | 0.03175 | 16.1138 | 0 | 0.59961 | 0 | 0.50941 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 20.3333 | 16.2% | CZ 5A | 0.46141 | 0.38688 | 0.0093055 | 0 | 0 | 0.17573 | 0 | 0.1493 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.2366 | 16.2% | CZ 5A | 0 | 0 | 0 | 0.16114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16114 | 16.2% | CZ 5A | 4.8305 | 4.0502 | 0.09742 | 17.6124 | 0 | 1.8398 | 0 | 1.563 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 30.5589 | 16.2%
CZ 5B | 0.049047 | 0.041125 | 0.0010242 | 0.089803 | 0 | 0.018987 | 0 | 0.013122 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.21885 | 5.323% | CZ 5B | 1.5743 | 1.32 | 0.032874 | 9.1636 | 0 | 0.60944 | 0 | 0.42119 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 13.3057 | 5.323% | CZ 5B | 0.46141 | 0.38688 | 0.0096349 | 0 | 0 | 0.17862 | 0 | 0.12344 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.214 | 5.323% | CZ 5B | 0 | 0 | 0 | 0.091636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091636 | 5.323% | CZ 5B | 4.8305 | 4.0502 | 0.10087 | 10.0158 | 0 | 1.8699 | 0 | 1.2923 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 22.7251 | 5.323%
CZ 5C | 0.049047 | 0.041055 | 0.0014444 | 0.073164 | 0 | -0.017341 | 0 | 0.0040005 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.15711 | 0.04828% | CZ 5C | 1.5743 | 1.3178 | 0.046361 | 7.4657 | 0 | -0.55662 | 0 | 0.12841 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 10.1603 | 0.048% | CZ 5C | 0.46141 | 0.38622 | 0.013588 | 0 | 0 | -0.16314 | 0 | 0.037634 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 0.78974 | 0.048% | CZ 5C | 0 | 0 | 0 | 0.074657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074657 | 0.048% | CZ 5C | 4.8305 | 4.0433 | 0.14225 | 8.16 | 0 | -1.7079 | 0 | 0.39399 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 16.4278 | 0.04828%
CZ 6A | 0.049047 | 0.041099 | 0.00098918 | 0.21435 | 0 | 0.020186 | 0 | 0.020501 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.35192 | 4.174% | CZ 6A | 1.5743 | 1.3192 | 0.03175 | 21.8725 | 0 | 0.64793 | 0 | 0.65805 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 26.288 | 4.174% | CZ 6A | 0.46141 | 0.38663 | 0.0093055 | 0 | 0 | 0.1899 | 0 | 0.19286 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.2941 | 4.174% | CZ 6A | 0 | 0 | 0 | 0.21872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21872 | 4.174% | CZ 6A | 4.8305 | 4.0477 | 0.09742 | 23.9066 | 0 | 1.9881 | 0 | 2.0191 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 37.4548 | 4.174%
CZ 6B | 0.049047 | 0.041073 | 0.0010767 | 0.15712 | 0 | 0.0057075 | 0 | 0.014549 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.27431 | 0.3776% | CZ 6B | 1.5743 | 1.3183 | 0.03456 | 16.0324 | 0 | 0.1832 | 0 | 0.46698 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 19.7941 | 0.378% | CZ 6B | 0.46141 | 0.38639 | 0.010129 | 0 | 0 | 0.053692 | 0 | 0.13687 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.1025 | 0.378% | CZ 6B | 0 | 0 | 0 | 0.16032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16032 | 0.378% | CZ 6B | 4.8305 | 4.0451 | 0.10604 | 17.5234 | 0 | 0.5621 | 0 | 1.4328 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 29.0654 | 0.3776%
CZ 7 | 0.049047 | 0.041047 | 0.00096292 | 0.23824 | 0 | 0.015949 | 0 | 0.024712 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.3757 | 0.3013% | CZ 7 | 1.5743 | 1.3175 | 0.030908 | 24.3099 | 0 | 0.51194 | 0 | 0.7932 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 28.7221 | 0.301% | CZ 7 | 0.46141 | 0.38614 | 0.0090585 | 0 | 0 | 0.15004 | 0 | 0.23247 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.2931 | 0.301% | CZ 7 | 0 | 0 | 0 | 0.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2431 | 0.301% | CZ 7 | 4.8305 | 4.0425 | 0.094833 | 26.5707 | 0 | 1.5708 | 0 | 2.4338 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 40.1086 | 0.3013%
CZ 8 | 0.049047 | 0.040819 | 0.00090164 | 0.25706 | 0 | -0.0020834 | 0 | 0.023486 | 0 | 0 | 0 | 0.0040443 | 0 | 0 | 0 | 0.0016982 | 0.37498 | 8.036e-05% | CZ 8 | 1.5743 | 1.3102 | 0.028941 | 26.2311 | 0 | -0.066873 | 0 | 0.75386 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.05451 | 30.0158 | 0% | CZ 8 | 0.46141 | 0.384 | 0.008482 | 0 | 0 | -0.019599 | 0 | 0.22094 | 0 | 0 | 0 | 0.038046 | 0 | 0 | 0 | 0.015976 | 1.1093 | 0% | CZ 8 | 0 | 0 | 0 | 0.26231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26231 | 0% | CZ 8 | 4.8305 | 4.0201 | 0.088798 | 28.6705 | 0 | -0.20518 | 0 | 2.3131 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 40.2833 | 8.036e-05%
US Weighted | 0.049047 | 0.041135 | 0.00089931 | 0.075047 | 0 | 0.074613 | 0 | 0.018696 | 0 | 0 | 0 | 0.0040442 | 0 | 0 | 0 | 0.0016982 | 0.26518 | 100% | US Weighted | 1.5743 | 1.3203 | 0.028866 | 7.6578 | 0 | 2.3949 | 0 | 0.60009 | 0 | 0 | 0 | 0.12981 | 0 | 0 | 0 | 0.054509 | 13.7606 | 100% | US Weighted | 0.4614 | 0.38697 | 0.0084601 | 0 | 0 | 0.70191 | 0 | 0.17588 | 0 | 0 | 0 | 0.038045 | 0 | 0 | 0 | 0.015976 | 1.7886 | 100% | US Weighted | 0 | 0 | 0 | 0.076578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076578 | 100% | US Weighted | 4.8304 | 4.0512 | 0.088568 | 8.37 | 0 | 7.3483 | 0 | 1.8412 | 0 | 0 | 0 | 0.3983 | 0 | 0 | 0 | 0.16725 | 27.0952 | 100%
Building Type: | Mid-rise Apartment |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | Mid-rise Apartment |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr | Building Type: | Mid-rise Apartment |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 33741 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 33741 | [17 empty] | Prototype Floor Area: | 33741 | Building Type: | Mid-rise Apartment | [15 empty] | Prototype Floor Area: | 33741 | [6 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 40.18% | 64.44% | 0.08353% |  |  | 48.93% |  | 27.03% |  |  |  | 3.565% |  |  |  | 0.4999% | 27.46% | 0% | CZ 0A | 40.18% | 64.44% | 0.08353% |  |  | 48.93% |  | 27.03% |  |  |  | 3.565% |  |  |  | 0.4999% | 27.46% | 0% | CZ 0A | 40.18% | 64.44% | 0.08353% |  |  | 48.93% |  | 27.03% |  |  |  | 3.565% |  |  |  | 0.4999% | 27.46% | 0% | CZ 0A | [16 empty] | 0% | 0% | CZ 0A | 40.18% | 64.44% | 0.08353% |  |  | 48.93% |  | 27.03% |  |  |  | 3.565% |  |  |  | 0.4999% | 27.46% | 0%
CZ 0B | 40.18% | 64.43% | 0.1203% | 100% |  | 45.34% |  | 23.67% |  |  |  | 3.565% |  |  |  | 0.4999% | 24.92% | 0% | CZ 0B | 40.18% | 64.43% | 0.1203% | 100% |  | 45.34% |  | 23.67% |  |  |  | 3.565% |  |  |  | 0.4999% | 24.92% | 0% | CZ 0B | 40.18% | 64.43% | 0.1203% |  |  | 45.34% |  | 23.67% |  |  |  | 3.565% |  |  |  | 0.4999% | 24.92% | 0% | CZ 0B |  |  |  | 100% | [12 empty] | 100% | 0% | CZ 0B | 40.18% | 64.43% | 0.1203% | 100% |  | 45.34% |  | 23.67% |  |  |  | 3.565% |  |  |  | 0.4999% | 24.92% | 0%
CZ 1A | 40.18% | 64.43% | 0.2057% |  |  | 46.93% |  | 22.76% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.95% | 2.646% | CZ 1A | 40.18% | 64.43% | 0.2057% |  |  | 46.93% |  | 22.76% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.95% | 2.646% | CZ 1A | 40.18% | 64.43% | 0.2057% |  |  | 46.93% |  | 22.76% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.95% | 2.646% | CZ 1A | [16 empty] | 0% | 2.646% | CZ 1A | 40.18% | 64.43% | 0.2057% |  |  | 46.93% |  | 22.76% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.95% | 2.646%
CZ 1B | 40.18% | 64.43% | 0.1614% | 85.7% |  | 44.11% |  | 21.85% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.17% | 0% | CZ 1B | 40.18% | 64.43% | 0.1614% | 85.7% |  | 44.11% |  | 21.85% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.42% | 0% | CZ 1B | 40.18% | 64.43% | 0.1614% |  |  | 44.11% |  | 21.85% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.05% | 0% | CZ 1B |  |  |  | 85.7% | [12 empty] | 85.7% | 0% | CZ 1B | 40.18% | 64.43% | 0.1614% | 85.7% |  | 44.11% |  | 21.85% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.18% | 0%
CZ 2A | 40.18% | 64.43% | 0.2802% | 94.35% |  | 46.67% |  | 24.36% |  |  |  | 3.565% |  |  |  | 0.4999% | 21.61% | 16.39% | CZ 2A | 40.18% | 64.43% | 0.2802% | 94.35% |  | 46.67% |  | 24.36% |  |  |  | 3.565% |  |  |  | 0.4999% | 22.67% | 16.39% | CZ 2A | 40.18% | 64.43% | 0.2802% |  |  | 46.67% |  | 24.36% |  |  |  | 3.565% |  |  |  | 0.4999% | 21.11% | 16.39% | CZ 2A |  |  |  | 94.35% | [12 empty] | 94.35% | 16.39% | CZ 2A | 40.18% | 64.43% | 0.2802% | 94.35% |  | 46.67% |  | 24.36% |  |  |  | 3.565% |  |  |  | 0.4999% | 21.67% | 16.39%
CZ 2B | 40.18% | 64.43% | 0.2726% | 91.9% |  | 40.71% |  | 19.53% |  |  |  | 3.565% |  |  |  | 0.4999% | 18.6% | 1.974% | CZ 2B | 40.18% | 64.43% | 0.2726% | 91.9% |  | 40.71% |  | 19.53% |  |  |  | 3.565% |  |  |  | 0.4999% | 19.76% | 1.974% | CZ 2B | 40.18% | 64.43% | 0.2726% |  |  | 40.71% |  | 19.53% |  |  |  | 3.565% |  |  |  | 0.4999% | 18.05% | 1.974% | CZ 2B |  |  |  | 91.9% | [12 empty] | 91.9% | 1.974% | CZ 2B | 40.18% | 64.43% | 0.2726% | 91.9% |  | 40.71% |  | 19.53% |  |  |  | 3.565% |  |  |  | 0.4999% | 18.67% | 1.974%
CZ 3A | 40.18% | 64.43% | 0.2698% | 77.84% |  | 43.14% |  | 21.57% |  |  |  | 3.565% |  |  |  | 0.4999% | 18.81% | 12.99% | CZ 3A | 40.18% | 64.43% | 0.2698% | 77.84% |  | 43.14% |  | 21.57% |  |  |  | 3.565% |  |  |  | 0.4999% | 23.58% | 12.99% | CZ 3A | 40.18% | 64.43% | 0.2698% |  |  | 43.14% |  | 21.57% |  |  |  | 3.565% |  |  |  | 0.4999% | 16.34% | 12.99% | CZ 3A |  |  |  | 77.84% | [12 empty] | 77.84% | 12.99% | CZ 3A | 40.18% | 64.43% | 0.2698% | 77.84% |  | 43.14% |  | 21.57% |  |  |  | 3.565% |  |  |  | 0.4999% | 19.13% | 12.99%
CZ 3B | 40.18% | 64.43% | 0.2555% | 84.02% |  | 38.91% |  | 16.9% |  |  |  | 3.565% |  |  |  | 0.4999% | 16.66% | 8.593% | CZ 3B | 40.18% | 64.43% | 0.2555% | 84.02% |  | 38.91% |  | 16.9% |  |  |  | 3.565% |  |  |  | 0.4999% | 18.69% | 8.593% | CZ 3B | 40.18% | 64.43% | 0.2555% |  |  | 38.91% |  | 16.9% |  |  |  | 3.565% |  |  |  | 0.4999% | 15.68% | 8.593% | CZ 3B |  |  |  | 84.02% | [12 empty] | 84.02% | 8.593% | CZ 3B | 40.18% | 64.43% | 0.2555% | 84.02% |  | 38.91% |  | 16.9% |  |  |  | 3.565% |  |  |  | 0.4999% | 16.78% | 8.593%
CZ 3C | 40.18% | 64.43% | 0.1797% | 61.72% |  | 66.49% |  | 37.88% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.28% | 3.597% | CZ 3C | 40.18% | 64.43% | 0.1797% | 61.72% |  | 66.49% |  | 37.88% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.62% | 3.597% | CZ 3C | 40.18% | 64.43% | 0.1797% |  |  | 66.49% |  | 37.88% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.12% | 3.597% | CZ 3C |  |  |  | 61.72% | [12 empty] | 61.72% | 3.597% | CZ 3C | 40.18% | 64.43% | 0.1797% | 61.72% |  | 66.49% |  | 37.88% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.3% | 3.597%
CZ 4A | 40.18% | 64.43% | 0.2749% | 74.47% |  | 36.34% |  | 19.99% |  |  |  | 3.565% |  |  |  | 0.4999% | 19.65% | 22.03% | CZ 4A | 40.18% | 64.43% | 0.2749% | 74.47% |  | 36.34% |  | 19.99% |  |  |  | 3.565% |  |  |  | 0.4999% | 29.65% | 22.03% | CZ 4A | 40.18% | 64.43% | 0.2749% |  |  | 36.34% |  | 19.99% |  |  |  | 3.565% |  |  |  | 0.4999% | 13.4% | 22.03% | CZ 4A |  |  |  | 74.47% | [12 empty] | 74.47% | 22.03% | CZ 4A | 40.18% | 64.43% | 0.2749% | 74.47% |  | 36.34% |  | 19.99% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.38% | 22.03%
CZ 4B | 40.18% | 64.44% | 0.2999% | 80.84% |  | 26.08% |  | 13.49% |  |  |  | 3.565% |  |  |  | 0.4999% | 14.87% | 0.1893% | CZ 4B | 40.18% | 64.44% | 0.2999% | 80.84% |  | 26.08% |  | 13.49% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.27% | 0.1893% | CZ 4B | 40.18% | 64.44% | 0.2999% |  |  | 26.08% |  | 13.49% |  |  |  | 3.565% |  |  |  | 0.4999% | 12.05% | 0.1893% | CZ 4B |  |  |  | 80.84% | [12 empty] | 80.84% | 0.1893% | CZ 4B | 40.18% | 64.44% | 0.2999% | 80.84% |  | 26.08% |  | 13.49% |  |  |  | 3.565% |  |  |  | 0.4999% | 15.22% | 0.1893%
CZ 4C | 40.18% | 64.44% | 0.3541% | 82.96% |  | -4.416% |  | 11.32% |  |  |  | 3.565% |  |  |  | 0.4999% | 14.4% | 5.156% | CZ 4C | 40.18% | 64.44% | 0.3541% | 82.96% |  | -4.416% |  | 11.32% |  |  |  | 3.565% |  |  |  | 0.4999% | 23.43% | 5.156% | CZ 4C | 40.18% | 64.44% | 0.3541% |  |  | -4.416% |  | 11.32% |  |  |  | 3.565% |  |  |  | 0.4999% | 9.269% | 5.156% | CZ 4C |  |  |  | 82.96% | [12 empty] | 82.96% | 5.156% | CZ 4C | 40.18% | 64.44% | 0.3541% | 82.96% |  | -4.416% |  | 11.32% |  |  |  | 3.565% |  |  |  | 0.4999% | 15.03% | 5.156%
CZ 5A | 40.18% | 64.44% | 0.2662% | 71.05% |  | 25.61% |  | 20.74% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.93% | 16.2% | CZ 5A | 40.18% | 64.44% | 0.2662% | 71.05% |  | 25.61% |  | 20.74% |  |  |  | 3.565% |  |  |  | 0.4999% | 33.94% | 16.2% | CZ 5A | 40.18% | 64.44% | 0.2662% |  |  | 25.61% |  | 20.74% |  |  |  | 3.565% |  |  |  | 0.4999% | 11.33% | 16.2% | CZ 5A |  |  |  | 71.05% | [12 empty] | 71.05% | 16.2% | CZ 5A | 40.18% | 64.44% | 0.2662% | 71.05% |  | 25.61% |  | 20.74% |  |  |  | 3.565% |  |  |  | 0.4999% | 21.98% | 16.2%
CZ 5B | 40.18% | 64.44% | 0.281% | 75.68% |  | 19.46% |  | 15.83% |  |  |  | 3.565% |  |  |  | 0.4999% | 16.8% | 5.323% | CZ 5B | 40.18% | 64.44% | 0.281% | 75.68% |  | 19.46% |  | 15.83% |  |  |  | 3.565% |  |  |  | 0.4999% | 26.55% | 5.323% | CZ 5B | 40.18% | 64.44% | 0.281% |  |  | 19.46% |  | 15.83% |  |  |  | 3.565% |  |  |  | 0.4999% | 10.9% | 5.323% | CZ 5B |  |  |  | 75.68% | [12 empty] | 75.68% | 5.323% | CZ 5B | 40.18% | 64.44% | 0.281% | 75.68% |  | 19.46% |  | 15.83% |  |  |  | 3.565% |  |  |  | 0.4999% | 17.5% | 5.323%
CZ 5C | 40.18% | 64.43% | 0.3906% | 86.75% |  | -59.61% |  | 6.813% |  |  |  | 3.565% |  |  |  | 0.4999% | 13.3% | 0.04828% | CZ 5C | 40.18% | 64.43% | 0.3906% | 86.75% |  | -59.61% |  | 6.813% |  |  |  | 3.565% |  |  |  | 0.4999% | 23.2% | 0.04828% | CZ 5C | 40.18% | 64.43% | 0.3906% |  |  | -59.61% |  | 6.813% |  |  |  | 3.565% |  |  |  | 0.4999% | 7.656% | 0.04828% | CZ 5C |  |  |  | 86.75% | [12 empty] | 86.75% | 0.04828% | CZ 5C | 40.18% | 64.43% | 0.3906% | 86.75% |  | -59.61% |  | 6.813% |  |  |  | 3.565% |  |  |  | 0.4999% | 13.99% | 0.04828%
CZ 6A | 40.18% | 64.43% | 0.2539% | 67.26% |  | 25.72% |  | 24.27% |  |  |  | 3.565% |  |  |  | 0.4999% | 23.3% | 4.174% | CZ 6A | 40.18% | 64.43% | 0.2539% | 67.26% |  | 25.72% |  | 24.27% |  |  |  | 3.565% |  |  |  | 0.4999% | 37.15% | 4.174% | CZ 6A | 40.18% | 64.43% | 0.2539% |  |  | 25.72% |  | 24.27% |  |  |  | 3.565% |  |  |  | 0.4999% | 11.55% | 4.174% | CZ 6A |  |  |  | 67.26% | [12 empty] | 67.26% | 4.174% | CZ 6A | 40.18% | 64.43% | 0.2539% | 67.26% |  | 25.72% |  | 24.27% |  |  |  | 3.565% |  |  |  | 0.4999% | 24.5% | 4.174%
CZ 6B | 40.18% | 64.43% | 0.2796% | 71.64% |  | 9.694% |  | 18.39% |  |  |  | 3.565% |  |  |  | 0.4999% | 19.86% | 0.3776% | CZ 6B | 40.18% | 64.43% | 0.2796% | 71.64% |  | 9.694% |  | 18.39% |  |  |  | 3.565% |  |  |  | 0.4999% | 33.17% | 0.3776% | CZ 6B | 40.18% | 64.43% | 0.2796% |  |  | 9.694% |  | 18.39% |  |  |  | 3.565% |  |  |  | 0.4999% | 10.09% | 0.3776% | CZ 6B |  |  |  | 71.64% | [12 empty] | 71.64% | 0.3776% | CZ 6B | 40.18% | 64.43% | 0.2796% | 71.64% |  | 9.694% |  | 18.39% |  |  |  | 3.565% |  |  |  | 0.4999% | 20.93% | 0.3776%
CZ 7 | 40.18% | 64.44% | 0.2344% | 69.83% |  | 23.52% |  | 27.91% |  |  |  | 3.565% |  |  |  | 0.4999% | 24.28% | 0.3013% | CZ 7 | 40.18% | 64.44% | 0.2344% | 69.83% |  | 23.52% |  | 27.91% |  |  |  | 3.565% |  |  |  | 0.4999% | 39.06% | 0.3013% | CZ 7 | 40.18% | 64.44% | 0.2344% |  |  | 23.52% |  | 27.91% |  |  |  | 3.565% |  |  |  | 0.4999% | 11.4% | 0.3013% | CZ 7 |  |  |  | 69.83% | [12 empty] | 69.83% | 0.3013% | CZ 7 | 40.18% | 64.44% | 0.2344% | 69.83% |  | 23.52% |  | 27.91% |  |  |  | 3.565% |  |  |  | 0.4999% | 25.57% | 0.3013%
CZ 8 | 40.18% | 64.43% | 0.2051% | 66.07% |  | -5.02% |  | 25.96% |  |  |  | 3.565% |  |  |  | 0.4999% | 23.45% | 8.036e-05% | CZ 8 | 40.18% | 64.43% | 0.2051% | 66.07% |  | -5.02% |  | 25.96% |  |  |  | 3.565% |  |  |  | 0.4999% | 38.22% | 8.036e-05% | CZ 8 | 40.18% | 64.43% | 0.2051% |  |  | -5.02% |  | 25.96% |  |  |  | 3.565% |  |  |  | 0.4999% | 9.744% | 8.036e-05% | CZ 8 |  |  |  | 66.07% | [12 empty] | 66.07% | 8.036e-05% | CZ 8 | 40.18% | 64.43% | 0.2051% | 66.07% |  | -5.02% |  | 25.96% |  |  |  | 3.565% |  |  |  | 0.4999% | 24.78% | 8.036e-05%
US Weighted | 40.18% | 64.43% | 0.2703% | 76.54% | 0% | 35.2% | 0% | 20.99% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 19.63% | 100% | US Weighted | 40.18% | 64.43% | 0.2703% | 76.54% | 0% | 35.2% | 0% | 20.99% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 26.62% | 100% | US Weighted | 40.18% | 64.43% | 0.2703% | 0% | 0% | 35.2% | 0% | 20.99% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 15.04% | 100% | US Weighted | 0% | 0% | 0% | 76.54% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 76.54% | 100% | US Weighted | 40.18% | 64.43% | 0.2703% | 76.54% | 0% | 35.2% | 0% | 20.99% | 0% | 0% | 0% | 3.565% | 0% | 0% | 0% | 0.4999% | 20.16% | 100%

## AptHR
Note: for printout, pagination is set for landscape legal size. For letter size, reduce scale further.
Building Type: | High-rise Apartment |  |  |  | End Use Cost Summary for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr |  |  |  |  | Prototype Floor Area: | 84352 |  | Building Type: | High-rise Apartment |  |  |  | End Use Summary for Standard 90.1 |  |  |  |  | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 |  | Building Type: | High-rise Apartment |  |  |  | Electric Summary for Standard 90.1 |  |  |  |  | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 |  | Gas Summary for Standard 90.1 | [16 empty] | Gas Use Intensity therms/sq ft/yr |  |  | Building Type: | High-rise Apartment |  |  |  | End Use Summary for Standard 90.1 | [11 empty] | Energy Use Index Source kBtus/sq ft/yr
US Average Weighted Results | [5 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [5 empty] | US Average Weighted Results | [10 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  | US Average Weighted Results | [18 empty] | Building Type: | High-rise Apartment | [14 empty] | Prototype Floor Area: | 84352 |  |  | US Average Weighted Results | [5 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
| Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  | US Weighted |  |  | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total |  |  |  | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total
End Cost by 90.1 edition: | [18 empty] | End Use by 90.1 edition: | [18 empty] | End Electric Use by 90.1 edition: | [18 empty] | End Gas Use by 90.1 edition: | [19 empty] | End Use by 90.1 edition:
STD2019 | 0.0721 | 0.041287 | 0.11595 | 0.066847 | 0 | 0.14132 | 0.0034834 | 0.079609 | 0 | 0.012059 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.93367 |  | STD2019 | 2.3143 | 1.3252 | 11.8315 | 4.582 | 0 | 4.5362 | 0.11181 | 2.5553 | 0 | 0.38706 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 40.5149 |  | STD2019 | 0.67827 | 0.3884 | 0 | 0.30116 | 0 | 1.3295 | 0.03277 | 0.74891 | 0 | 0.11344 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.3649 |  | STD2019 | 0 | 0 | 0.11832 | 0.035545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15386 |  |  | STD2019 | 7.1008 | 4.0661 | 12.9318 | 7.0379 | 0 | 13.9184 | 0.34306 | 7.8403 | 0 | 1.1876 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 93.9197
STD2016 | 0.088732 | 0.041287 | 0.11595 | 0.069226 | 0 | 0.14387 | 0.0036305 | 0.078486 | 0 | 0.012409 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.95459 |  | STD2016 | 2.8481 | 1.3252 | 11.8316 | 4.7473 | 0 | 4.6178 | 0.11653 | 2.5192 | 0 | 0.39829 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.2756 |  | STD2016 | 0.83474 | 0.3884 | 0 | 0.31157 | 0 | 1.3534 | 0.034154 | 0.73834 | 0 | 0.11673 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.5498 |  | STD2016 | 0 | 0 | 0.11832 | 0.036843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15516 |  |  | STD2016 | 8.7389 | 4.0661 | 12.9319 | 7.2888 | 0 | 14.1686 | 0.35755 | 7.7297 | 0 | 1.2221 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 95.9972
STD2013 | 0.11277 | 0.058979 | 0.1163 | 0.068507 | 0 | 0.15007 | 0.0072494 | 0.080327 | 0 | 0.01305 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.0105 |  | STD2013 | 3.6196 | 1.8931 | 11.8678 | 4.694 | 0 | 4.8171 | 0.23269 | 2.5783 | 0 | 0.41888 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 43.0641 |  | STD2013 | 1.0608 | 0.55484 | 0 | 0.30888 | 0 | 1.4118 | 0.068197 | 0.75566 | 0 | 0.12277 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 8.0763 |  | STD2013 | 0 | 0 | 0.11868 | 0.036401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15508 |  |  | STD2013 | 11.1059 | 5.8086 | 12.9715 | 7.2123 | 0 | 14.7801 | 0.71396 | 7.911 | 0 | 1.2852 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 101.5005
STD2010 | 0.13548 | 0.058979 | 0.1163 | 0.12543 | 0 | 0.19239 | 0.0088263 | 0.088979 | 0 | 0.016525 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.1463 |  | STD2010 | 4.3485 | 1.8931 | 11.8678 | 8.5608 | 0 | 6.1752 | 0.28331 | 2.856 | 0 | 0.53042 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 49.4617 |  | STD2010 | 1.2745 | 0.55484 | 0 | 0.57003 | 0 | 1.8098 | 0.083032 | 0.83706 | 0 | 0.15546 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 9.0792 |  | STD2010 | 0 | 0 | 0.11868 | 0.066159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18484 |  |  | STD2010 | 13.3426 | 5.8086 | 12.9715 | 13.1988 | 0 | 18.9473 | 0.86926 | 8.7632 | 0 | 1.6275 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 115.2523
STD2007 | 0.1171 | 0.074714 | 0.11637 | 0.18017 | 0 | 0.19362 | 0.0091241 | 0.094789 | 0 | 0.02248 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2193 |  | STD2007 | 3.7586 | 2.3982 | 11.8742 | 12.4668 | 0 | 6.2147 | 0.29287 | 3.0425 | 0 | 0.72156 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 53.9587 |  | STD2007 | 1.1016 | 0.70286 | 0 | 0.7959 | 0 | 1.8214 | 0.085834 | 0.89171 | 0 | 0.21148 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.4763 |  | STD2007 | 0 | 0 | 0.11874 | 0.097512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21625 |  |  | STD2007 | 11.5325 | 7.3583 | 12.9785 | 18.9904 | 0 | 19.0684 | 0.89859 | 9.3353 | 0 | 2.214 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 122.8444
STD2004 | 0.1171 | 0.074714 | 0.11637 | 0.19952 | 0 | 0.19939 | 0.0095382 | 0.098893 | 0 | 0.023941 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2504 |  | STD2004 | 3.7586 | 2.3982 | 11.8742 | 13.8033 | 0 | 6.4001 | 0.30616 | 3.1742 | 0 | 0.76845 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 55.6725 |  | STD2004 | 1.1016 | 0.70286 | 0 | 0.88171 | 0 | 1.8758 | 0.089729 | 0.93032 | 0 | 0.22522 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.6727 |  | STD2004 | 0 | 0 | 0.11874 | 0.10795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22669 |  |  | STD2004 | 11.5325 | 7.3583 | 12.9785 | 21.0294 | 0 | 19.6374 | 0.93938 | 9.7395 | 0 | 2.3578 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 126.0412
Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [18 empty] | Savings between editions: | [19 empty] | Savings between editions:
2004-2007 | 0 | 0 | -3.7839e-07 | 0.019349 | 0 | 0.0057771 | 0.00041408 | 0.0041038 | 0 | 0.0014609 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031105 |  | 2004-2007 | 0 | 0 | -3.8612e-05 | 1.3365 | 0 | 0.18543 | 0.013291 | 0.13172 | 0 | 0.046893 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7138 |  | 2004-2007 | 0 | 0 | 0 | 0.085805 | 0 | 0.054347 | 0.0038954 | 0.038606 | 0 | 0.013744 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1964 |  | 2004-2007 | 0 | 0 | -3.8612e-07 | 0.010437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010437 |  |  | 2004-2007 | 0 | 0 | -4.2202e-05 | 2.0391 | 0 | 0.56896 | 0.040781 | 0.40416 | 0 | 0.14388 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1968
2007-2010 | -0.01838 | 0.015735 | 6.3331e-05 | 0.054736 | 0 | 0.0012299 | 0.00029782 | 0.0058095 | 0 | 0.005955 | 0 | 0.0015022 | 0.0053784 | 0 | 0 | 0.0006828 | 0.07301 |  | 2007-2010 | -0.58994 | 0.50506 | 0.0064623 | 3.906 | 0 | 0.039478 | 0.0095594 | 0.18647 | 0 | 0.19114 | 0 | 0.048216 | 0.17263 | 0 | 0 | 0.021916 | 4.497 |  | 2007-2010 | -0.1729 | 0.14803 | 0 | 0.22587 | 0 | 0.01157 | 0.0028017 | 0.054652 | 0 | 0.056021 | 0 | 0.014131 | 0.050596 | 0 | 0 | 0.0064233 | 0.39719 |  | 2007-2010 | 0 | 0 | 6.4623e-05 | 0.031353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031418 |  |  | 2007-2010 | -1.8101 | 1.5497 | 0.0070633 | 5.7915 | 0 | 0.12113 | 0.029331 | 0.57215 | 0 | 0.58648 | 0 | 0.14794 | 0.52969 | 0 | 0 | 0.067246 | 7.5921
2010-2013 | 0.022711 | 0 | -3.8813e-07 | 0.056924 | 0 | 0.042313 | 0.0015769 | 0.0086525 | 0 | 0.003475 | 0 | 0.00011555 | 3.5015e-06 | 0 | 0 | 0 | 0.13577 |  | 2010-2013 | 0.72897 | 0 | -3.9606e-05 | 3.8669 | 0 | 1.3581 | 0.050616 | 0.27773 | 0 | 0.11154 | 0 | 0.0037089 | 0.00011239 | 0 | 0 | 0 | 6.3976 |  | 2010-2013 | 0.21365 | 0 | 0 | 0.26116 | 0 | 0.39805 | 0.014835 | 0.081397 | 0 | 0.03269 | 0 | 0.001087 | 3.294e-05 | 0 | 0 | 0 | 1.0029 |  | 2010-2013 | 0 | 0 | -3.9606e-07 | 0.029758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029758 |  |  | 2010-2013 | 2.2367 | 0 | -4.3289e-05 | 5.9866 | 0 | 4.1672 | 0.15531 | 0.85215 | 0 | 0.34224 | 0 | 0.01138 | 0.00034485 | 0 | 0 | 0 | 13.7518
2013-2016 | 0.024035 | 0.017692 | 0.00035494 | -0.00071942 | 0 | 0.0062088 | 0.0036189 | 0.0018412 | 0 | 0.00064153 | 0 | 0 | 0.0022165 | 0 | 0 | 0 | 0.055889 |  | 2013-2016 | 0.77146 | 0.56789 | 0.036218 | -0.053365 | 0 | 0.19929 | 0.11616 | 0.059098 | 0 | 0.020592 | 0 | 0 | 0.071144 | 0 | 0 | 0 | 1.7885 |  | 2013-2016 | 0.2261 | 0.16644 | 0 | -0.0026961 | 0 | 0.058408 | 0.034044 | 0.017321 | 0 | 0.0060351 | 0 | 0 | 0.020851 | 0 | 0 | 0 | 0.5265 |  | 2013-2016 | 0 | 0 | 0.00036218 | -0.00044166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9474e-05 |  |  | 2013-2016 | 2.3671 | 1.7424 | 0.039586 | -0.076498 | 0 | 0.61148 | 0.3564 | 0.18133 | 0 | 0.063181 | 0 | 0 | 0.21829 | 0 | 0 | 0 | 5.5033
2016-2019 | 0.016632 | 0 | 7.1149e-07 | 0.0023787 | 0 | 0.0025407 | 0.00014712 | -0.0011234 | 0 | 0.00034964 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020926 |  | 2016-2019 | 0.53386 | 0 | 7.2601e-05 | 0.16532 | 0 | 0.081551 | 0.0047221 | -0.03606 | 0 | 0.011223 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76069 |  | 2016-2019 | 0.15647 | 0 | 0 | 0.010412 | 0 | 0.023901 | 0.001384 | -0.010569 | 0 | 0.0032892 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18488 |  | 2016-2019 | 0 | 0 | 7.2601e-07 | 0.0012979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012986 |  |  | 2016-2019 | 1.638 | 0 | 7.9353e-05 | 0.25086 | 0 | 0.25022 | 0.014489 | -0.11064 | 0 | 0.034434 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0775
2004-2019 | 0.044998 | 0.033428 | 0.00041821 | 0.13267 | 0 | 0.058069 | 0.0060548 | 0.019284 | 0 | 0.011882 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.3167 |  | 2004-2019 | 1.4443 | 1.073 | 0.042675 | 9.2213 | 0 | 1.8639 | 0.19435 | 0.61896 | 0 | 0.38139 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 15.1576 |  | 2004-2019 | 0.42331 | 0.31446 | 0 | 0.58054 | 0 | 0.54628 | 0.05696 | 0.18141 | 0 | 0.11178 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.3079 |  | 2004-2019 | 0 | 0 | 0.00042675 | 0.072405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072831 |  |  | 2004-2019 | 4.4317 | 3.2921 | 0.046644 | 13.9915 | 0 | 5.719 | 0.59631 | 1.8991 | 0 | 1.1702 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 32.1215
Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [18 empty] | Percentage savings between editions: | [19 empty] | Percentage savings between editions:
2004-2007 | 0% | 0% | -0.0003252% | 9.698% |  | 2.897% | 4.341% | 4.15% |  | 6.102% |  | 0% | 0% |  |  | 0% | 2.488% |  | 2004-2007 | 0% | 0% | -0.0003252% | 9.682% |  | 2.897% | 4.341% | 4.15% |  | 6.102% |  | 0% | 0% |  |  | 0% | 3.078% |  | 2004-2007 | 0% | 0% |  | 9.732% |  | 2.897% | 4.341% | 4.15% |  | 6.102% |  | 0% | 0% |  |  | 0% | 2.03% |  | 2004-2007 |  |  | -0.0003252% | 9.669% | [12 empty] | 4.604% |  |  | 2004-2007 | 0% | 0% | -0.0003252% | 9.696% |  | 2.897% | 4.341% | 4.15% |  | 6.102% |  | 0% | 0% |  |  | 0% | 2.536%
2007-2010 | -15.7% | 21.06% | 0.05442% | 30.38% |  | 0.6352% | 3.264% | 6.129% |  | 26.49% |  | 2.631% | 42.45% |  |  | 0.2001% | 5.988% |  | 2007-2010 | -15.7% | 21.06% | 0.05442% | 31.33% |  | 0.6352% | 3.264% | 6.129% |  | 26.49% |  | 2.631% | 42.45% |  |  | 0.2001% | 8.334% |  | 2007-2010 | -15.7% | 21.06% |  | 28.38% |  | 0.6352% | 3.264% | 6.129% |  | 26.49% |  | 2.631% | 42.45% |  |  | 0.2001% | 4.191% |  | 2007-2010 |  |  | 0.05442% | 32.15% | [12 empty] | 14.53% |  |  | 2007-2010 | -15.7% | 21.06% | 0.05442% | 30.5% |  | 0.6352% | 3.264% | 6.129% |  | 26.49% |  | 2.631% | 42.45% |  |  | 0.2001% | 6.18%
2010-2013 | 16.76% | 0% | -0.0003337% | 45.38% |  | 21.99% | 17.87% | 9.724% |  | 21.03% |  | 0.2079% | 0.04803% |  |  | 0% | 11.84% |  | 2010-2013 | 16.76% | 0% | -0.0003337% | 45.17% |  | 21.99% | 17.87% | 9.724% |  | 21.03% |  | 0.2079% | 0.04803% |  |  | 0% | 12.93% |  | 2010-2013 | 16.76% | 0% |  | 45.81% |  | 21.99% | 17.87% | 9.724% |  | 21.03% |  | 0.2079% | 0.04803% |  |  | 0% | 11.05% |  | 2010-2013 |  |  | -0.0003337% | 44.98% | [12 empty] | 16.1% |  |  | 2010-2013 | 16.76% | 0% | -0.0003337% | 45.36% |  | 21.99% | 17.87% | 9.724% |  | 21.03% |  | 0.2079% | 0.04803% |  |  | 0% | 11.93%
2013-2016 | 21.31% | 30% | 0.3052% | -1.05% |  | 4.137% | 49.92% | 2.292% |  | 4.916% |  | 0% | 30.42% |  |  | 0% | 5.531% |  | 2013-2016 | 21.31% | 30% | 0.3052% | -1.137% |  | 4.137% | 49.92% | 2.292% |  | 4.916% |  | 0% | 30.42% |  |  | 0% | 4.153% |  | 2013-2016 | 21.31% | 30% |  | -0.8729% |  | 4.137% | 49.92% | 2.292% |  | 4.916% |  | 0% | 30.42% |  |  | 0% | 6.519% |  | 2013-2016 |  |  | 0.3052% | -1.213% | [12 empty] | -0.05125% |  |  | 2013-2016 | 21.31% | 30% | 0.3052% | -1.061% |  | 4.137% | 49.92% | 2.292% |  | 4.916% |  | 0% | 30.42% |  |  | 0% | 5.422%
2016-2019 | 18.74% | 0% | 0.0006136% | 3.436% |  | 1.766% | 4.052% | -1.431% |  | 2.818% |  | 0% | 0% |  |  | 0% | 2.192% |  | 2016-2019 | 18.74% | 0% | 0.0006136% | 3.482% |  | 1.766% | 4.052% | -1.431% |  | 2.818% |  | 0% | 0% |  |  | 0% | 1.843% |  | 2016-2019 | 18.74% | 0% |  | 3.342% |  | 1.766% | 4.052% | -1.431% |  | 2.818% |  | 0% | 0% |  |  | 0% | 2.449% |  | 2016-2019 |  |  | 0.0006136% | 3.523% | [12 empty] | 0.837% |  |  | 2016-2019 | 18.74% | 0% | 0.0006136% | 3.442% |  | 1.766% | 4.052% | -1.431% |  | 2.818% |  | 0% | 0% |  |  | 0% | 2.164%
2004-2019 | 38.43% | 44.74% | 0.3594% | 66.5% |  | 29.12% | 63.48% | 19.5% |  | 49.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.33% |  | 2004-2019 | 38.43% | 44.74% | 0.3594% | 66.8% |  | 29.12% | 63.48% | 19.5% |  | 49.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 27.23% |  | 2004-2019 | 38.43% | 44.74% |  | 65.84% |  | 29.12% | 63.48% | 19.5% |  | 49.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.86% |  | 2004-2019 |  |  | 0.3594% | 67.07% | [12 empty] | 32.13% |  |  | 2004-2019 | 38.43% | 44.74% | 0.3594% | 66.53% |  | 29.12% | 63.48% | 19.5% |  | 49.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.48%
Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [18 empty] | Climate Zone Detail: | [19 empty] | Climate Zone Detail:
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2019 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2019 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2019 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [7 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight |  | STD2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.0721 | 0.04135 | 0.081816 | 0 | 0 | 0.47109 | 0.020015 | 0.13497 | 0 | 0.016433 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.2388 | 0% | CZ 0A | 2.3143 | 1.3272 | 8.3486 | 0 | 0 | 15.1208 | 0.64243 | 4.3321 | 0 | 0.52745 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 45.4845 | 0% | CZ 0A | 0.67827 | 0.38899 | 0 | 0 | 0 | 4.4317 | 0.18829 | 1.2697 | 0 | 0.15459 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 10.8839 | 0% | CZ 0A | 0 | 0 | 0.083486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083486 | 0% |  | CZ 0A | 7.1008 | 4.0723 | 9.125 | 0 | 0 | 46.3951 | 1.9712 | 13.2923 | 0 | 1.6184 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 123.0687 | 0%
CZ 0B | 0.0721 | 0.04136 | 0.081394 | 7.0031e-06 | 0 | 0.39336 | 0.014195 | 0.13372 | 0 | 0.016968 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.1541 | 0% | CZ 0B | 2.3143 | 1.3276 | 8.3055 | 0.00022478 | 0 | 12.6261 | 0.45564 | 4.2922 | 0 | 0.54465 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 42.7378 | 0% | CZ 0B | 0.67827 | 0.38909 | 0 | 6.588e-05 | 0 | 3.7005 | 0.13354 | 1.258 | 0 | 0.15963 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 10.0915 | 0% | CZ 0B | 0 | 0 | 0.083055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083055 | 0% |  | CZ 0B | 7.1008 | 4.0734 | 9.0779 | 0.0006897 | 0 | 38.7405 | 1.398 | 13.1698 | 0 | 1.6711 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 114.726 | 0%
CZ 1A | 0.0721 | 0.041364 | 0.089439 | 0 | 0 | 0.32408 | 0.007875 | 0.11035 | 0 | 0.012665 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.0589 | 14.96% | CZ 1A | 2.3143 | 1.3277 | 9.1265 | 0 | 0 | 10.4022 | 0.25277 | 3.5421 | 0 | 0.40652 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 40.2436 | 14.96% | CZ 1A | 0.67827 | 0.38912 | 0 | 0 | 0 | 3.0487 | 0.074082 | 1.0381 | 0 | 0.11914 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 9.1199 | 14.96% | CZ 1A | 0 | 0 | 0.091265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091265 | 14.96% |  | CZ 1A | 7.1008 | 4.0737 | 9.9752 | 0 | 0 | 31.9169 | 0.77557 | 10.8683 | 0 | 1.2473 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 105.4515 | 14.96%
CZ 1B | 0.0721 | 0.041311 | 0.089655 | 0.00079975 | 0 | 0.30779 | 0.010613 | 0.11889 | 0 | 0.015141 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.0573 | 0% | CZ 1B | 2.3143 | 1.326 | 9.1485 | 0.036299 | 0 | 9.8792 | 0.34066 | 3.8163 | 0 | 0.48598 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 40.2187 | 0% | CZ 1B | 0.67827 | 0.38863 | 0 | 0.0060939 | 0 | 2.8954 | 0.099842 | 1.1185 | 0 | 0.14243 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 9.1016 | 0% | CZ 1B | 0 | 0 | 0.091485 | 0.00015506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09164 | 0% |  | CZ 1B | 7.1008 | 4.0685 | 9.9993 | 0.080746 | 0 | 30.3123 | 1.0452 | 11.7094 | 0 | 1.4911 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 105.3012 | 0%
CZ 2A | 0.0721 | 0.041297 | 0.098155 | 0.0019106 | 0 | 0.25203 | 0.0084037 | 0.093428 | 0 | 0.012451 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.98078 | 12.37% | CZ 2A | 2.3143 | 1.3255 | 10.0158 | 0.11586 | 0 | 8.0895 | 0.26974 | 2.9988 | 0 | 0.39967 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 38.4008 | 12.37% | CZ 2A | 0.67827 | 0.3885 | 0 | 0.01064 | 0 | 2.3709 | 0.079056 | 0.87891 | 0 | 0.11714 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 8.2958 | 12.37% | CZ 2A | 0 | 0 | 0.10016 | 0.00079554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10095 | 12.37% |  | CZ 2A | 7.1008 | 4.0672 | 10.9473 | 0.19834 | 0 | 24.8209 | 0.82764 | 9.2013 | 0 | 1.2263 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 97.8834 | 12.37%
CZ 2B | 0.0721 | 0.041329 | 0.098698 | 0.0020469 | 0 | 0.20442 | 0.0025386 | 0.09785 | 0 | 0.012896 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.93289 | 0.8671% | CZ 2B | 2.3143 | 1.3266 | 10.0712 | 0.11238 | 0 | 6.5615 | 0.081484 | 3.1408 | 0 | 0.41394 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 36.8937 | 0.8671% | CZ 2B | 0.67827 | 0.38879 | 0 | 0.012978 | 0 | 1.9231 | 0.023882 | 0.92051 | 0 | 0.12132 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.8413 | 0.8671% | CZ 2B | 0 | 0 | 0.10071 | 0.00068093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10139 | 0.8671% |  | CZ 2B | 7.1008 | 4.0703 | 11.0079 | 0.2103 | 0 | 20.1327 | 0.25002 | 9.6368 | 0 | 1.2701 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 93.1725 | 0.8671%
CZ 3A | 0.0721 | 0.041318 | 0.11308 | 0.040585 | 0 | 0.13247 | 0.0032564 | 0.075041 | 0 | 0.01187 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.89073 | 5.906% | CZ 3A | 2.3143 | 1.3262 | 11.5385 | 2.7601 | 0 | 4.252 | 0.10452 | 2.4087 | 0 | 0.38101 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 37.9568 | 5.906% | CZ 3A | 0.67827 | 0.38869 | 0 | 0.18578 | 0 | 1.2462 | 0.030634 | 0.70594 | 0 | 0.11167 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.1196 | 5.906% | CZ 3A | 0 | 0 | 0.11538 | 0.021262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13665 | 5.906% |  | CZ 3A | 7.1008 | 4.0692 | 12.6116 | 4.2689 | 0 | 13.0464 | 0.32071 | 7.3905 | 0 | 1.169 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 89.4707 | 5.906%
CZ 3B | 0.0721 | 0.041318 | 0.10926 | 0.009096 | 0 | 0.15002 | 0.0019223 | 0.086803 | 0 | 0.01158 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.88311 | 6.552% | CZ 3B | 2.3143 | 1.3262 | 11.1493 | 0.57917 | 0 | 4.8153 | 0.061703 | 2.7862 | 0 | 0.37168 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 36.2753 | 6.552% | CZ 3B | 0.67827 | 0.38869 | 0 | 0.04694 | 0 | 1.4113 | 0.018084 | 0.81659 | 0 | 0.10893 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.2412 | 6.552% | CZ 3B | 0 | 0 | 0.11149 | 0.0041901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11568 | 6.552% |  | CZ 3B | 7.1008 | 4.0692 | 12.1861 | 0.94939 | 0 | 14.7748 | 0.18932 | 8.5488 | 0 | 1.1404 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 88.4526 | 6.552%
CZ 3C | 0.0721 | 0.041311 | 0.11479 | 0.0065598 | 0 | 0.025537 | 0.00035015 | 0.044385 | 0 | 0.0051227 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.71116 | 3.035% | CZ 3C | 2.3143 | 1.326 | 11.7129 | 0.43083 | 0 | 0.81967 | 0.011239 | 1.4247 | 0 | 0.16443 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 31.0755 | 3.035% | CZ 3C | 0.67827 | 0.38863 | 0 | 0.032084 | 0 | 0.24023 | 0.003294 | 0.41755 | 0 | 0.048191 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 5.5807 | 3.035% | CZ 3C | 0 | 0 | 0.11713 | 0.0032136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12034 | 3.035% |  | CZ 3C | 7.1008 | 4.0685 | 12.8022 | 0.68713 | 0 | 2.515 | 0.034485 | 4.3713 | 0 | 0.50452 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 71.5776 | 3.035%
CZ 4A | 0.0721 | 0.041255 | 0.12484 | 0.099654 | 0 | 0.091331 | 0.002213 | 0.071242 | 0 | 0.012714 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.91636 | 33.86% | CZ 4A | 2.3143 | 1.3242 | 12.7385 | 6.8375 | 0 | 2.9315 | 0.071032 | 2.2867 | 0 | 0.40809 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.7834 | 33.86% | CZ 4A | 0.67827 | 0.3881 | 0 | 0.44805 | 0 | 0.85918 | 0.020818 | 0.6702 | 0 | 0.11961 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 6.9567 | 33.86% | CZ 4A | 0 | 0 | 0.12739 | 0.053088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18047 | 33.86% |  | CZ 4A | 7.1008 | 4.063 | 13.9232 | 10.4931 | 0 | 8.9947 | 0.21795 | 7.0163 | 0 | 1.2522 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 92.555 | 33.86%
CZ 4B | 0.0721 | 0.041287 | 0.12152 | 0.029875 | 0 | 0.11008 | 0.001187 | 0.079215 | 0 | 0.011517 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.86779 | 0% | CZ 4B | 2.3143 | 1.3252 | 12.4001 | 1.9794 | 0 | 3.5334 | 0.038101 | 2.5426 | 0 | 0.36966 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 37.3743 | 0% | CZ 4B | 0.67827 | 0.3884 | 0 | 0.14378 | 0 | 1.0356 | 0.011167 | 0.7452 | 0 | 0.10834 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 6.8832 | 0% | CZ 4B | 0 | 0 | 0.124 | 0.014888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13889 | 0% |  | CZ 4B | 7.1008 | 4.0661 | 13.5533 | 3.1326 | 0 | 10.8414 | 0.1169 | 7.8015 | 0 | 1.1342 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 87.2405 | 0%
CZ 4C | 0.0721 | 0.04121 | 0.12839 | 0.046823 | 0 | 0.028072 | 0.00035015 | 0.055492 | 0 | 0.010354 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.7838 | 5.13% | CZ 4C | 2.3143 | 1.3227 | 13.1008 | 3.1916 | 0 | 0.90104 | 0.011239 | 1.7812 | 0 | 0.33234 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 35.8267 | 5.13% | CZ 4C | 0.67827 | 0.38767 | 0 | 0.21335 | 0 | 0.26408 | 0.003294 | 0.52204 | 0 | 0.097404 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 5.9385 | 5.13% | CZ 4C | 0 | 0 | 0.13101 | 0.024636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15564 | 5.13% |  | CZ 4C | 7.1008 | 4.0585 | 14.3192 | 4.9263 | 0 | 2.7647 | 0.034485 | 5.4652 | 0 | 1.0197 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 79.1825 | 5.13%
CZ 5A | 0.0721 | 0.041269 | 0.13479 | 0.16129 | 0 | 0.048251 | 0.00084737 | 0.06926 | 0 | 0.011818 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.94064 | 14.08% | CZ 5A | 2.3143 | 1.3246 | 13.7544 | 11.101 | 0 | 1.5488 | 0.027199 | 2.2231 | 0 | 0.37932 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 45.5443 | 14.08% | CZ 5A | 0.67827 | 0.38823 | 0 | 0.72057 | 0 | 0.45392 | 0.0079715 | 0.65156 | 0 | 0.11117 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 6.7841 | 14.08% | CZ 5A | 0 | 0 | 0.13754 | 0.086424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22397 | 14.08% |  | CZ 5A | 7.1008 | 4.0644 | 15.0336 | 16.9897 | 0 | 4.752 | 0.083454 | 6.8211 | 0 | 1.1639 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 95.5027 | 14.08%
CZ 5B | 0.0721 | 0.041269 | 0.132 | 0.077845 | 0 | 0.081631 | 0.00078084 | 0.077724 | 0 | 0.011205 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.89556 | 1.936% | CZ 5B | 2.3143 | 1.3246 | 13.4691 | 5.2891 | 0 | 2.6202 | 0.025063 | 2.4948 | 0 | 0.35965 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 40.7683 | 1.936% | CZ 5B | 0.67827 | 0.38823 | 0 | 0.35701 | 0 | 0.76793 | 0.0073457 | 0.73117 | 0 | 0.10541 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 6.8078 | 1.936% | CZ 5B | 0 | 0 | 0.13469 | 0.04071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1754 | 1.936% |  | CZ 5B | 7.1008 | 4.0644 | 14.7218 | 8.1871 | 0 | 8.0395 | 0.076902 | 7.6546 | 0 | 1.1035 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 90.4422 | 1.936%
CZ 5C | 0.0721 | 0.041206 | 0.13403 | 0.028511 | 0 | 0.026153 | 0.00028012 | 0.05301 | 0 | 0.010028 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.76633 | 0% | CZ 5C | 2.3143 | 1.3226 | 13.6767 | 1.9317 | 0 | 0.83945 | 0.0089913 | 1.7015 | 0 | 0.32189 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 34.9886 | 0% | CZ 5C | 0.67827 | 0.38764 | 0 | 0.1315 | 0 | 0.24603 | 0.0026352 | 0.49868 | 0 | 0.094341 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 5.8115 | 0% | CZ 5C | 0 | 0 | 0.13677 | 0.01483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1516 | 0% |  | CZ 5C | 7.1008 | 4.0582 | 14.9486 | 2.9975 | 0 | 2.5757 | 0.027588 | 5.2207 | 0 | 0.98765 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 77.4104 | 0%
CZ 6A | 0.0721 | 0.041252 | 0.14216 | 0.2385 | 0 | 0.058308 | 0.0011065 | 0.077114 | 0 | 0.013992 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.0455 | 1.175% | CZ 6A | 2.3143 | 1.3241 | 14.5066 | 16.3549 | 0 | 1.8715 | 0.035516 | 2.4752 | 0 | 0.44912 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 52.2027 | 1.175% | CZ 6A | 0.67827 | 0.38807 | 0 | 1.0735 | 0 | 0.54852 | 0.010409 | 0.72544 | 0 | 0.13163 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.3283 | 1.175% | CZ 6A | 0 | 0 | 0.14507 | 0.12692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27199 | 1.175% |  | CZ 6A | 7.1008 | 4.0627 | 15.8557 | 25.1111 | 0 | 5.7424 | 0.10897 | 7.5946 | 0 | 1.378 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 106.448 | 1.175%
CZ 6B | 0.0721 | 0.04122 | 0.1403 | 0.15167 | 0 | 0.046556 | 0.00048321 | 0.075829 | 0 | 0.011769 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.94094 | 0.09221% | CZ 6B | 2.3143 | 1.3231 | 14.3159 | 10.3438 | 0 | 1.4944 | 0.01551 | 2.434 | 0 | 0.37775 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 45.4902 | 0.09221% | CZ 6B | 0.67827 | 0.38777 | 0 | 0.69039 | 0 | 0.43797 | 0.0045457 | 0.71335 | 0 | 0.11071 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 6.7955 | 0.09221% | CZ 6B | 0 | 0 | 0.14316 | 0.079882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22304 | 0.09221% |  | CZ 6B | 7.1008 | 4.0596 | 15.6473 | 15.9588 | 0 | 4.5851 | 0.047589 | 7.4681 | 0 | 1.159 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 95.52 | 0.09221%
CZ 7 | 0.0721 | 0.041196 | 0.15094 | 0.22116 | 0 | 0.050061 | 0.00081936 | 0.07745 | 0 | 0.012662 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.0274 | 0.04244% | CZ 7 | 2.3143 | 1.3223 | 15.4024 | 15.1464 | 0 | 1.6069 | 0.0263 | 2.486 | 0 | 0.40641 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 51.5825 | 0.04244% | CZ 7 | 0.67827 | 0.38754 | 0 | 0.99815 | 0 | 0.47095 | 0.007708 | 0.7286 | 0 | 0.11911 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.1628 | 0.04244% | CZ 7 | 0 | 0 | 0.15402 | 0.11741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27143 | 0.04244% |  | CZ 7 | 7.1008 | 4.0572 | 16.8348 | 23.2823 | 0 | 4.9303 | 0.080695 | 7.6277 | 0 | 1.247 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 104.6544 | 0.04244%
CZ 8 | 0.0721 | 0.040968 | 0.16275 | 0.27989 | 0 | 0.035527 | 0.00036066 | 0.088109 | 0 | 0.012959 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.0937 | 0% | CZ 8 | 2.3143 | 1.315 | 16.607 | 19.0322 | 0 | 1.1403 | 0.011576 | 2.8281 | 0 | 0.41596 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 56.536 | 0% | CZ 8 | 0.67827 | 0.3854 | 0 | 1.2815 | 0 | 0.33421 | 0.0033928 | 0.82887 | 0 | 0.12191 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.406 | 0% | CZ 8 | 0 | 0 | 0.16607 | 0.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31267 | 0% |  | CZ 8 | 7.1008 | 4.0347 | 18.1515 | 29.4389 | 0 | 3.4989 | 0.03552 | 8.6775 | 0 | 1.2763 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 111.7077 | 0%
US Weighted | 0.0721 | 0.041287 | 0.11595 | 0.066847 | 0 | 0.14132 | 0.0034834 | 0.079609 | 0 | 0.012059 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.93367 | 100% | US Weighted | 2.3143 | 1.3252 | 11.8315 | 4.582 | 0 | 4.5362 | 0.11181 | 2.5553 | 0 | 0.38706 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 40.5149 | 100% | US Weighted | 0.67827 | 0.3884 | 0 | 0.30116 | 0 | 1.3295 | 0.03277 | 0.74891 | 0 | 0.11344 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.3649 | 100% | US Weighted | 0 | 0 | 0.11832 | 0.035545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15386 | 100% |  | US Weighted | 7.1008 | 4.0661 | 12.9318 | 7.0379 | 0 | 13.9184 | 0.34306 | 7.8403 | 0 | 1.1876 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 93.9197 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2016 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2016 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2016 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2016 | [17 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2016 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [7 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight |  | STD2016 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.088732 | 0.04135 | 0.081814 | 0 | 0 | 0.51088 | 0.021524 | 0.13824 | 0 | 0.016601 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.3002 | 0% | CZ 0A | 2.8481 | 1.3272 | 8.3483 | 0 | 0 | 16.3982 | 0.69087 | 4.4373 | 0 | 0.53285 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 47.4545 | 0% | CZ 0A | 0.83474 | 0.38899 | 0 | 0 | 0 | 4.806 | 0.20248 | 1.3005 | 0 | 0.15617 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 11.4614 | 0% | CZ 0A | 0 | 0 | 0.083483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083483 | 0% |  | CZ 0A | 8.7389 | 4.0723 | 9.1247 | 0 | 0 | 50.3144 | 2.1198 | 13.615 | 0 | 1.6349 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 129.1137 | 0%
CZ 0B | 0.088732 | 0.04136 | 0.081393 | 1.0505e-05 | 0 | 0.41339 | 0.014804 | 0.13527 | 0 | 0.016916 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.1929 | 0% | CZ 0B | 2.8481 | 1.3276 | 8.3054 | 0.00033718 | 0 | 13.269 | 0.47519 | 4.342 | 0 | 0.54296 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 43.9822 | 0% | CZ 0B | 0.83474 | 0.38909 | 0 | 9.882e-05 | 0 | 3.8889 | 0.13927 | 1.2726 | 0 | 0.15913 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 10.4563 | 0% | CZ 0B | 0 | 0 | 0.083054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083054 | 0% |  | CZ 0B | 8.7389 | 4.0734 | 9.0778 | 0.0010346 | 0 | 40.713 | 1.458 | 13.3226 | 0 | 1.666 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 118.5444 | 0%
CZ 1A | 0.088732 | 0.041364 | 0.089439 | 0 | 0 | 0.33497 | 0.0083267 | 0.10821 | 0 | 0.013327 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.0854 | 14.96% | CZ 1A | 2.8481 | 1.3277 | 9.1265 | 0 | 0 | 10.7517 | 0.26727 | 3.4734 | 0 | 0.42776 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.0939 | 14.96% | CZ 1A | 0.83474 | 0.38912 | 0 | 0 | 0 | 3.1512 | 0.078332 | 1.018 | 0 | 0.12537 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 9.3691 | 14.96% | CZ 1A | 0 | 0 | 0.091265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091265 | 14.96% |  | CZ 1A | 8.7389 | 4.0737 | 9.9752 | 0 | 0 | 32.9894 | 0.82005 | 10.6573 | 0 | 1.3125 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 108.0607 | 14.96%
CZ 1B | 0.088732 | 0.041311 | 0.089655 | 0.003168 | 0 | 0.33285 | 0.011706 | 0.12246 | 0 | 0.015568 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.1065 | 0% | CZ 1B | 2.8481 | 1.326 | 9.1485 | 0.20081 | 0 | 10.6838 | 0.37573 | 3.9307 | 0 | 0.49969 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.8849 | 0% | CZ 1B | 0.83474 | 0.38863 | 0 | 0.01647 | 0 | 3.1313 | 0.11012 | 1.152 | 0 | 0.14645 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 9.5521 | 0% | CZ 1B | 0 | 0 | 0.091485 | 0.0014461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092931 | 0% |  | CZ 1B | 8.7389 | 4.0685 | 9.9993 | 0.33049 | 0 | 32.7811 | 1.1528 | 12.0605 | 0 | 1.5332 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 110.1584 | 0%
CZ 2A | 0.088732 | 0.041297 | 0.098155 | 0.0093023 | 0 | 0.25453 | 0.0089044 | 0.090049 | 0 | 0.012395 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.0044 | 12.37% | CZ 2A | 2.8481 | 1.3255 | 10.0158 | 0.62692 | 0 | 8.1699 | 0.28581 | 2.8904 | 0 | 0.39787 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 39.4319 | 12.37% | CZ 2A | 0.83474 | 0.3885 | 0 | 0.043349 | 0 | 2.3945 | 0.083767 | 0.84712 | 0 | 0.11661 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 8.481 | 12.37% | CZ 2A | 0 | 0 | 0.10016 | 0.0047901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10495 | 12.37% |  | CZ 2A | 8.7389 | 4.0672 | 10.9473 | 0.97738 | 0 | 25.0675 | 0.87695 | 8.8685 | 0 | 1.2208 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 100.2581 | 12.37%
CZ 2B | 0.088732 | 0.041329 | 0.098699 | 0.0068363 | 0 | 0.20635 | 0.0026997 | 0.095564 | 0 | 0.01284 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.95406 | 0.8671% | CZ 2B | 2.8481 | 1.3266 | 10.0713 | 0.43994 | 0 | 6.6235 | 0.086654 | 3.0674 | 0 | 0.41214 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 37.7472 | 0.8671% | CZ 2B | 0.83474 | 0.38879 | 0 | 0.034653 | 0 | 1.9412 | 0.025397 | 0.899 | 0 | 0.12079 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 8.017 | 0.8671% | CZ 2B | 0 | 0 | 0.10071 | 0.003217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10393 | 0.8671% |  | CZ 2B | 8.7389 | 4.0703 | 11.008 | 0.7144 | 0 | 20.3227 | 0.26588 | 9.4117 | 0 | 1.2646 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 95.29 | 0.8671%
CZ 3A | 0.088732 | 0.041318 | 0.11308 | 0.082819 | 0 | 0.12935 | 0.003421 | 0.073795 | 0 | 0.011594 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.94512 | 5.906% | CZ 3A | 2.8481 | 1.3262 | 11.5387 | 5.6949 | 0 | 4.1519 | 0.10981 | 2.3687 | 0 | 0.37213 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.282 | 5.906% | CZ 3A | 0.83474 | 0.38869 | 0 | 0.37068 | 0 | 1.2168 | 0.032183 | 0.69421 | 0 | 0.10906 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.4188 | 5.906% | CZ 3A | 0 | 0 | 0.11539 | 0.044302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15969 | 5.906% |  | CZ 3A | 8.7389 | 4.0692 | 12.6118 | 8.7228 | 0 | 12.7391 | 0.33692 | 7.2677 | 0 | 1.1418 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 95.1219 | 5.906%
CZ 3B | 0.088732 | 0.041318 | 0.10926 | 0.030477 | 0 | 0.14355 | 0.0019539 | 0.083147 | 0 | 0.011492 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.91094 | 6.552% | CZ 3B | 2.8481 | 1.3262 | 11.1494 | 2.0681 | 0 | 4.6076 | 0.062715 | 2.6689 | 0 | 0.36887 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 37.9714 | 6.552% | CZ 3B | 0.83474 | 0.38869 | 0 | 0.14013 | 0 | 1.3504 | 0.018381 | 0.7822 | 0 | 0.10811 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.3951 | 6.552% | CZ 3B | 0 | 0 | 0.11149 | 0.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12739 | 6.552% |  | CZ 3B | 8.7389 | 4.0692 | 12.1863 | 3.2048 | 0 | 14.1375 | 0.19243 | 8.1888 | 0 | 1.1318 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 91.3433 | 6.552%
CZ 3C | 0.088732 | 0.041311 | 0.11479 | 0.0066947 | 0 | 0.02629 | 0.00035716 | 0.044914 | 0 | 0.0052803 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.72938 | 3.035% | CZ 3C | 2.8481 | 1.326 | 11.7129 | 0.43993 | 0 | 0.84384 | 0.011464 | 1.4416 | 0 | 0.16949 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 31.6649 | 3.035% | CZ 3C | 0.83474 | 0.38863 | 0 | 0.03271 | 0 | 0.24731 | 0.0033599 | 0.42252 | 0 | 0.049674 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 5.7514 | 3.035% | CZ 3C | 0 | 0 | 0.11713 | 0.0032833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12041 | 3.035% |  | CZ 3C | 8.7389 | 4.0685 | 12.8022 | 0.7013 | 0 | 2.5891 | 0.035175 | 4.4234 | 0 | 0.52003 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 73.3722 | 3.035%
CZ 4A | 0.088732 | 0.041255 | 0.12484 | 0.088534 | 0 | 0.094885 | 0.0022235 | 0.071298 | 0 | 0.013348 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.92612 | 33.86% | CZ 4A | 2.8481 | 1.3242 | 12.7387 | 6.0643 | 0 | 3.0456 | 0.071369 | 2.2885 | 0 | 0.42844 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.6807 | 33.86% | CZ 4A | 0.83474 | 0.3881 | 0 | 0.39943 | 0 | 0.89261 | 0.020917 | 0.67073 | 0 | 0.12557 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.1045 | 33.86% | CZ 4A | 0 | 0 | 0.12739 | 0.047014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1744 | 33.86% |  | CZ 4A | 8.7389 | 4.063 | 13.9233 | 9.3203 | 0 | 9.3448 | 0.21898 | 7.0218 | 0 | 1.3146 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 93.4393 | 33.86%
CZ 4B | 0.088732 | 0.041287 | 0.12152 | 0.053078 | 0 | 0.10283 | 0.0011625 | 0.076558 | 0 | 0.011541 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.89771 | 0% | CZ 4B | 2.8481 | 1.3252 | 12.4 | 3.6122 | 0 | 3.3005 | 0.037314 | 2.4573 | 0 | 0.37044 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 39.2226 | 0% | CZ 4B | 0.83474 | 0.3884 | 0 | 0.24264 | 0 | 0.96732 | 0.010936 | 0.7202 | 0 | 0.10857 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.0452 | 0% | CZ 4B | 0 | 0 | 0.124 | 0.027843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15184 | 0% |  | CZ 4B | 8.7389 | 4.0661 | 13.5532 | 5.5834 | 0 | 10.1269 | 0.11449 | 7.5398 | 0 | 1.1366 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 90.353 | 0%
CZ 4C | 0.088732 | 0.04121 | 0.12839 | 0.097929 | 0 | 0.016342 | 0.0002241 | 0.053822 | 0 | 0.0096292 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.83729 | 5.13% | CZ 4C | 2.8481 | 1.3227 | 13.101 | 6.7401 | 0 | 0.52453 | 0.0071931 | 1.7276 | 0 | 0.30908 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 39.4519 | 5.13% | CZ 4C | 0.83474 | 0.38767 | 0 | 0.43748 | 0 | 0.15373 | 0.0021082 | 0.50632 | 0 | 0.090585 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 6.1851 | 5.13% | CZ 4C | 0 | 0 | 0.13101 | 0.052474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18348 | 5.13% |  | CZ 4C | 8.7389 | 4.0585 | 14.3194 | 10.3154 | 0 | 1.6094 | 0.02207 | 5.3007 | 0 | 0.94834 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 84.8064 | 5.13%
CZ 5A | 0.088732 | 0.041269 | 0.13479 | 0.14802 | 0 | 0.052733 | 0.00089989 | 0.069257 | 0 | 0.012423 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.94914 | 14.08% | CZ 5A | 2.8481 | 1.3246 | 13.7544 | 10.1775 | 0 | 1.6926 | 0.028885 | 2.223 | 0 | 0.39877 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 45.3195 | 14.08% | CZ 5A | 0.83474 | 0.38823 | 0 | 0.66259 | 0 | 0.49608 | 0.0084656 | 0.65152 | 0 | 0.11687 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 6.9309 | 14.08% | CZ 5A | 0 | 0 | 0.13754 | 0.079168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21671 | 14.08% |  | CZ 5A | 8.7389 | 4.0644 | 15.0336 | 15.5897 | 0 | 5.1934 | 0.088627 | 6.8208 | 0 | 1.2235 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 96.2466 | 14.08%
CZ 5B | 0.088732 | 0.041269 | 0.132 | 0.11731 | 0 | 0.073634 | 0.00071431 | 0.077198 | 0 | 0.011303 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.94317 | 1.936% | CZ 5B | 2.8481 | 1.3246 | 13.4691 | 8.0472 | 0 | 2.3635 | 0.022928 | 2.4779 | 0 | 0.3628 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 43.7878 | 1.936% | CZ 5B | 0.83474 | 0.38823 | 0 | 0.5277 | 0 | 0.6927 | 0.0067198 | 0.72623 | 0 | 0.10633 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.0551 | 1.936% | CZ 5B | 0 | 0 | 0.13469 | 0.062467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19716 | 1.936% |  | CZ 5B | 8.7389 | 4.0644 | 14.7218 | 12.3521 | 0 | 7.2519 | 0.070349 | 7.6029 | 0 | 1.1132 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 95.4091 | 1.936%
CZ 5C | 0.088732 | 0.041206 | 0.13403 | 0.083218 | 0 | 0.0085262 | 9.8043e-05 | 0.050342 | 0 | 0.0093316 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.8165 | 0% | CZ 5C | 2.8481 | 1.3226 | 13.6769 | 5.7443 | 0 | 0.27367 | 0.003147 | 1.6159 | 0 | 0.29952 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 38.6557 | 0% | CZ 5C | 0.83474 | 0.38764 | 0 | 0.36952 | 0 | 0.080209 | 0.00092232 | 0.47358 | 0 | 0.087785 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 6.0068 | 0% | CZ 5C | 0 | 0 | 0.13677 | 0.044835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1816 | 0% |  | CZ 5C | 8.7389 | 4.0582 | 14.9488 | 8.7689 | 0 | 0.83971 | 0.0096558 | 4.9579 | 0 | 0.91903 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 82.7348 | 0%
CZ 6A | 0.088732 | 0.041252 | 0.14217 | 0.21789 | 0 | 0.065745 | 0.0011905 | 0.077549 | 0 | 0.014787 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.0503 | 1.175% | CZ 6A | 2.8481 | 1.3241 | 14.5067 | 14.9482 | 0 | 2.1103 | 0.038213 | 2.4891 | 0 | 0.47463 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 51.6109 | 1.175% | CZ 6A | 0.83474 | 0.38807 | 0 | 0.9799 | 0 | 0.61848 | 0.0112 | 0.72953 | 0 | 0.13911 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.4735 | 1.175% | CZ 6A | 0 | 0 | 0.14507 | 0.11605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26111 | 1.175% |  | CZ 6A | 8.7389 | 4.0627 | 15.8558 | 22.9426 | 0 | 6.4749 | 0.11725 | 7.6374 | 0 | 1.4563 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 106.7795 | 1.175%
CZ 6B | 0.088732 | 0.04122 | 0.1403 | 0.15919 | 0 | 0.050188 | 0.00051823 | 0.078175 | 0 | 0.012585 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.97192 | 0.09221% | CZ 6B | 2.8481 | 1.3231 | 14.3159 | 10.8897 | 0 | 1.6109 | 0.016634 | 2.5093 | 0 | 0.40394 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 46.7891 | 0.09221% | CZ 6B | 0.83474 | 0.38777 | 0 | 0.72017 | 0 | 0.47213 | 0.0048751 | 0.73542 | 0 | 0.11839 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.0459 | 0.09221% | CZ 6B | 0 | 0 | 0.14316 | 0.084325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22748 | 0.09221% |  | CZ 6B | 8.7389 | 4.0596 | 15.6473 | 16.7562 | 0 | 4.9427 | 0.051038 | 7.6991 | 0 | 1.2394 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 98.6279 | 0.09221%
CZ 7 | 0.088732 | 0.041196 | 0.15095 | 0.2409 | 0 | 0.055289 | 0.00089289 | 0.081876 | 0 | 0.014178 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.075 | 0.04244% | CZ 7 | 2.8481 | 1.3223 | 15.4026 | 16.5608 | 0 | 1.7747 | 0.02866 | 2.6281 | 0 | 0.45507 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 53.8918 | 0.04244% | CZ 7 | 0.83474 | 0.38754 | 0 | 1.0788 | 0 | 0.52012 | 0.0083997 | 0.77024 | 0 | 0.13337 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.5057 | 0.04244% | CZ 7 | 0 | 0 | 0.15403 | 0.1288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28282 | 0.04244% |  | CZ 7 | 8.7389 | 4.0572 | 16.835 | 25.3719 | 0 | 5.4452 | 0.087937 | 8.0636 | 0 | 1.3963 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 109.4897 | 0.04244%
CZ 8 | 0.088732 | 0.040968 | 0.16275 | 0.29968 | 0 | 0.040688 | 0.00041318 | 0.092854 | 0 | 0.014696 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 1.1418 | 0% | CZ 8 | 2.8481 | 1.315 | 16.6071 | 20.5012 | 0 | 1.306 | 0.013262 | 2.9804 | 0 | 0.47171 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 58.9144 | 0% | CZ 8 | 0.83474 | 0.3854 | 0 | 1.3556 | 0 | 0.38276 | 0.0038869 | 0.87351 | 0 | 0.13825 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.7466 | 0% | CZ 8 | 0 | 0 | 0.16607 | 0.15876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32483 | 0% |  | CZ 8 | 8.7389 | 4.0347 | 18.1516 | 31.5441 | 0 | 4.0072 | 0.040692 | 9.1447 | 0 | 1.4473 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 116.6028 | 0%
US Weighted | 0.088732 | 0.041287 | 0.11595 | 0.069226 | 0 | 0.14387 | 0.0036305 | 0.078486 | 0 | 0.012409 | 0 | 0.055468 | 0.0050702 | 0 | 0 | 0.34047 | 0.95459 | 100% | US Weighted | 2.8481 | 1.3252 | 11.8316 | 4.7473 | 0 | 4.6178 | 0.11653 | 2.5192 | 0 | 0.39829 | 0 | 1.7804 | 0.16274 | 0 | 0 | 10.9284 | 41.2756 | 100% | US Weighted | 0.83474 | 0.3884 | 0 | 0.31157 | 0 | 1.3534 | 0.034154 | 0.73834 | 0 | 0.11673 | 0 | 0.5218 | 0.047697 | 0 | 0 | 3.2029 | 7.5498 | 100% | US Weighted | 0 | 0 | 0.11832 | 0.036843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15516 | 100% |  | US Weighted | 8.7389 | 4.0661 | 12.9319 | 7.2888 | 0 | 14.1686 | 0.35755 | 7.7297 | 0 | 1.2221 | 0 | 5.4628 | 0.49934 | 0 | 0 | 33.5315 | 95.9972 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2013 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2013 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2013 | [17 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2013 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [7 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight |  | STD2013 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.11277 | 0.059071 | 0.082008 | 0 | 0 | 0.5301 | 0.028089 | 0.14421 | 0 | 0.017483 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.377 | 0% | CZ 0A | 3.6196 | 1.896 | 8.3681 | 0 | 0 | 17.0151 | 0.90161 | 4.629 | 0 | 0.56117 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 49.9333 | 0% | CZ 0A | 1.0608 | 0.5557 | 0 | 0 | 0 | 4.9868 | 0.26425 | 1.3567 | 0 | 0.16447 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 12.1821 | 0% | CZ 0A | 0 | 0 | 0.083681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083681 | 0% |  | CZ 0A | 11.1059 | 5.8176 | 9.1464 | 0 | 0 | 52.2072 | 2.7664 | 14.203 | 0 | 1.7218 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 136.6803 | 0%
CZ 0B | 0.11277 | 0.059081 | 0.081588 | 7.0031e-06 | 0 | 0.42864 | 0.022613 | 0.14089 | 0 | 0.018176 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.267 | 0% | CZ 0B | 3.6196 | 1.8964 | 8.3253 | 0.00022478 | 0 | 13.7585 | 0.72583 | 4.5223 | 0 | 0.58343 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 46.3743 | 0% | CZ 0B | 1.0608 | 0.5558 | 0 | 6.588e-05 | 0 | 4.0324 | 0.21273 | 1.3254 | 0 | 0.17099 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 11.1515 | 0% | CZ 0B | 0 | 0 | 0.083253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083253 | 0% |  | CZ 0B | 11.1059 | 5.8187 | 9.0996 | 0.0006897 | 0 | 42.2152 | 2.227 | 13.8757 | 0 | 1.7901 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 125.8448 | 0%
CZ 1A | 0.11277 | 0.059088 | 0.089667 | 0 | 0 | 0.34244 | 0.016737 | 0.11032 | 0 | 0.013733 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.148 | 14.96% | CZ 1A | 3.6196 | 1.8966 | 9.1497 | 0 | 0 | 10.9917 | 0.53723 | 3.5409 | 0 | 0.4408 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 43.1192 | 14.96% | CZ 1A | 1.0608 | 0.55586 | 0 | 0 | 0 | 3.2215 | 0.15745 | 1.0378 | 0 | 0.12919 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 9.9559 | 14.96% | CZ 1A | 0 | 0 | 0.091497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091497 | 14.96% |  | CZ 1A | 11.1059 | 5.8193 | 10.0007 | 0 | 0 | 33.7257 | 1.6484 | 10.8645 | 0 | 1.3525 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 114.2289 | 14.96%
CZ 1B | 0.11277 | 0.059015 | 0.089886 | 0.0025865 | 0 | 0.33856 | 0.017469 | 0.12416 | 0 | 0.015872 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.1636 | 0% | CZ 1B | 3.6196 | 1.8943 | 9.1721 | 0.16058 | 0 | 10.8672 | 0.56072 | 3.9854 | 0 | 0.50947 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 43.712 | 0% | CZ 1B | 1.0608 | 0.55517 | 0 | 0.013901 | 0 | 3.185 | 0.16434 | 1.1681 | 0 | 0.14932 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 10.0899 | 0% | CZ 1B | 0 | 0 | 0.091721 | 0.0011315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092852 | 0% |  | CZ 1B | 11.1059 | 5.8121 | 10.0251 | 0.2692 | 0 | 33.3436 | 1.7205 | 12.2284 | 0 | 1.5632 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 115.7799 | 0%
CZ 2A | 0.11277 | 0.058994 | 0.098426 | 0.0088229 | 0 | 0.26029 | 0.01339 | 0.091698 | 0 | 0.0127 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.0603 | 12.37% | CZ 2A | 3.6196 | 1.8936 | 10.0435 | 0.59343 | 0 | 8.3549 | 0.42979 | 2.9433 | 0 | 0.40764 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 41.2284 | 12.37% | CZ 2A | 1.0608 | 0.55498 | 0 | 0.041274 | 0 | 2.4487 | 0.12596 | 0.86264 | 0 | 0.11947 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 9.0071 | 12.37% | CZ 2A | 0 | 0 | 0.10043 | 0.004526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10496 | 12.37% |  | CZ 2A | 11.1059 | 5.81 | 10.9775 | 0.92679 | 0 | 25.6351 | 1.3187 | 9.0309 | 0 | 1.2508 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 105.7677 | 12.37%
CZ 2B | 0.11277 | 0.059036 | 0.098976 | 0.0063168 | 0 | 0.21108 | 0.0084702 | 0.097241 | 0 | 0.013148 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.0103 | 0.8671% | CZ 2B | 3.6196 | 1.8949 | 10.0995 | 0.40431 | 0 | 6.7753 | 0.27188 | 3.1212 | 0 | 0.42203 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 39.5515 | 0.8671% | CZ 2B | 1.0608 | 0.55537 | 0 | 0.032314 | 0 | 1.9857 | 0.079682 | 0.91478 | 0 | 0.12369 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 8.5457 | 0.8671% | CZ 2B | 0 | 0 | 0.101 | 0.0029406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10394 | 0.8671% |  | CZ 2B | 11.1059 | 5.8142 | 11.0388 | 0.6597 | 0 | 20.7886 | 0.83419 | 9.5768 | 0 | 1.2949 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 100.8251 | 0.8671%
CZ 3A | 0.11277 | 0.059025 | 0.11343 | 0.080389 | 0 | 0.13299 | 0.0063518 | 0.07474 | 0 | 0.011853 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 0.99477 | 5.906% | CZ 3A | 3.6196 | 1.8946 | 11.574 | 5.5262 | 0 | 4.2686 | 0.20388 | 2.399 | 0 | 0.38045 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 42.809 | 5.906% | CZ 3A | 1.0608 | 0.55527 | 0 | 0.36004 | 0 | 1.2511 | 0.059753 | 0.70311 | 0 | 0.1115 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 7.8949 | 5.906% | CZ 3A | 0 | 0 | 0.11574 | 0.042977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15872 | 5.906% |  | CZ 3A | 11.1059 | 5.8131 | 12.6504 | 8.4666 | 0 | 13.0974 | 0.62556 | 7.3608 | 0 | 1.1673 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 99.9991 | 5.906%
CZ 3B | 0.11277 | 0.059022 | 0.10959 | 0.028508 | 0 | 0.1476 | 0.0059911 | 0.084384 | 0 | 0.0118 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 0.96289 | 6.552% | CZ 3B | 3.6196 | 1.8945 | 11.1827 | 1.9311 | 0 | 4.7375 | 0.1923 | 2.7085 | 0 | 0.37876 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 39.5877 | 6.552% | CZ 3B | 1.0608 | 0.55524 | 0 | 0.13153 | 0 | 1.3885 | 0.056361 | 0.79382 | 0 | 0.11101 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 7.8906 | 6.552% | CZ 3B | 0 | 0 | 0.11183 | 0.014823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12665 | 6.552% |  | CZ 3B | 11.1059 | 5.8128 | 12.2227 | 2.9972 | 0 | 14.5361 | 0.59004 | 8.3105 | 0 | 1.1621 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 96.4494 | 6.552%
CZ 3C | 0.11277 | 0.059015 | 0.11514 | 0.0056699 | 0 | 0.02887 | 0.0013271 | 0.045674 | 0 | 0.0054484 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 0.77714 | 3.035% | CZ 3C | 3.6196 | 1.8943 | 11.7487 | 0.36892 | 0 | 0.92667 | 0.042596 | 1.466 | 0 | 0.17488 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 33.1843 | 3.035% | CZ 3C | 1.0608 | 0.55517 | 0 | 0.028197 | 0 | 0.27159 | 0.012484 | 0.42967 | 0 | 0.051255 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 6.2025 | 3.035% | CZ 3C | 0 | 0 | 0.11749 | 0.0027271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12021 | 3.035% |  | CZ 3C | 11.1059 | 5.8121 | 12.8414 | 0.59326 | 0 | 2.8433 | 0.1307 | 4.4982 | 0 | 0.53659 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 78.0734 | 3.035%
CZ 4A | 0.11277 | 0.058934 | 0.12523 | 0.087223 | 0 | 0.10345 | 0.0050247 | 0.073746 | 0 | 0.014363 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 0.98397 | 33.86% | CZ 4A | 3.6196 | 1.8917 | 12.7788 | 5.9665 | 0 | 3.3206 | 0.16128 | 2.3671 | 0 | 0.46103 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 43.5093 | 33.86% | CZ 4A | 1.0608 | 0.55442 | 0 | 0.39459 | 0 | 0.97322 | 0.047269 | 0.69375 | 0 | 0.13512 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 7.6525 | 33.86% | CZ 4A | 0 | 0 | 0.12779 | 0.046202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17399 | 33.86% |  | CZ 4A | 11.1059 | 5.8042 | 13.9672 | 9.1808 | 0 | 10.1886 | 0.49486 | 7.2629 | 0 | 1.4146 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 99.131 | 33.86%
CZ 4B | 0.11277 | 0.05898 | 0.1219 | 0.050066 | 0 | 0.11405 | 0.0044189 | 0.080133 | 0 | 0.012606 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 0.95814 | 0% | CZ 4B | 3.6196 | 1.8931 | 12.4391 | 3.3923 | 0 | 3.6606 | 0.14184 | 2.5721 | 0 | 0.40461 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 41.0659 | 0% | CZ 4B | 1.0608 | 0.55484 | 0 | 0.23088 | 0 | 1.0729 | 0.04157 | 0.75384 | 0 | 0.11858 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 7.6267 | 0% | CZ 4B | 0 | 0 | 0.12439 | 0.026045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15044 | 0% |  | CZ 4B | 11.1059 | 5.8087 | 13.5959 | 5.2638 | 0 | 11.2318 | 0.4352 | 7.8919 | 0 | 1.2415 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 96.2865 | 0%
CZ 4C | 0.11277 | 0.058868 | 0.12881 | 0.09547 | 0 | 0.0204 | 0.0009104 | 0.05503 | 0 | 0.010771 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 0.88625 | 5.13% | CZ 4C | 3.6196 | 1.8895 | 13.1436 | 6.5644 | 0 | 0.65479 | 0.029222 | 1.7663 | 0 | 0.34572 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 40.9559 | 5.13% | CZ 4C | 1.0608 | 0.55379 | 0 | 0.42737 | 0 | 0.19191 | 0.0085644 | 0.51769 | 0 | 0.10132 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 6.6548 | 5.13% | CZ 4C | 0 | 0 | 0.13144 | 0.051062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1825 | 5.13% |  | CZ 4C | 11.1059 | 5.7976 | 14.366 | 10.0551 | 0 | 2.0091 | 0.089661 | 5.4197 | 0 | 1.0608 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 89.6158 | 5.13%
CZ 5A | 0.11277 | 0.058955 | 0.13524 | 0.1484 | 0 | 0.056672 | 0.0025841 | 0.070644 | 0 | 0.012994 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.0015 | 14.08% | CZ 5A | 3.6196 | 1.8923 | 13.8002 | 10.2 | 0 | 1.8191 | 0.082945 | 2.2675 | 0 | 0.41709 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 47.0414 | 14.08% | CZ 5A | 1.0608 | 0.55461 | 0 | 0.6648 | 0 | 0.53314 | 0.02431 | 0.66457 | 0 | 0.12224 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 7.4178 | 14.08% | CZ 5A | 0 | 0 | 0.138 | 0.079317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21732 | 14.08% |  | CZ 5A | 11.1059 | 5.8062 | 15.0836 | 15.6291 | 0 | 5.5814 | 0.2545 | 6.9574 | 0 | 1.2797 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 101.4098 | 14.08%
CZ 5B | 0.11277 | 0.058955 | 0.13243 | 0.11633 | 0 | 0.079464 | 0.0029938 | 0.079247 | 0 | 0.011968 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 0.99739 | 1.936% | CZ 5B | 3.6196 | 1.8923 | 13.5135 | 7.9736 | 0 | 2.5506 | 0.096095 | 2.5437 | 0 | 0.38416 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 45.5162 | 1.936% | CZ 5B | 1.0608 | 0.55461 | 0 | 0.52418 | 0 | 0.74754 | 0.028164 | 0.7455 | 0 | 0.11259 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 7.5667 | 1.936% | CZ 5B | 0 | 0 | 0.13514 | 0.061851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19699 | 1.936% |  | CZ 5B | 11.1059 | 5.8062 | 14.7703 | 12.2479 | 0 | 7.826 | 0.29485 | 7.8047 | 0 | 1.1787 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 100.7465 | 1.936%
CZ 5C | 0.11277 | 0.058864 | 0.13448 | 0.081266 | 0 | 0.011009 | 0.00050072 | 0.051017 | 0 | 0.0099549 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 0.86308 | 0% | CZ 5C | 3.6196 | 1.8894 | 13.7223 | 5.6065 | 0 | 0.35336 | 0.016072 | 1.6375 | 0 | 0.31953 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 40.107 | 0% | CZ 5C | 1.0608 | 0.55376 | 0 | 0.36125 | 0 | 0.10356 | 0.0047104 | 0.47994 | 0 | 0.093649 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 6.451 | 0% | CZ 5C | 0 | 0 | 0.13722 | 0.043739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18096 | 0% |  | CZ 5C | 11.1059 | 5.7973 | 14.9985 | 8.5626 | 0 | 1.0842 | 0.049314 | 5.0245 | 0 | 0.98041 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 87.3146 | 0%
CZ 6A | 0.11277 | 0.058927 | 0.14265 | 0.23227 | 0 | 0.065853 | 0.0030743 | 0.079268 | 0 | 0.015113 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.1131 | 1.175% | CZ 6A | 3.6196 | 1.8914 | 14.5565 | 15.9338 | 0 | 2.1138 | 0.09868 | 2.5443 | 0 | 0.48508 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 54.1859 | 1.175% | CZ 6A | 1.0608 | 0.55435 | 0 | 1.0446 | 0 | 0.61951 | 0.028921 | 0.7457 | 0 | 0.14217 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 7.9894 | 1.175% | CZ 6A | 0 | 0 | 0.14556 | 0.1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26926 | 1.175% |  | CZ 6A | 11.1059 | 5.8035 | 15.9102 | 24.4561 | 0 | 6.4856 | 0.30278 | 7.8067 | 0 | 1.4884 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 113.0712 | 1.175%
CZ 6B | 0.11277 | 0.058885 | 0.14077 | 0.16975 | 0 | 0.050212 | 0.0019609 | 0.079828 | 0 | 0.012858 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.0303 | 0.09221% | CZ 6B | 3.6196 | 1.8901 | 14.364 | 11.6118 | 0 | 1.6117 | 0.062939 | 2.5623 | 0 | 0.4127 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 49.0778 | 0.09221% | CZ 6B | 1.0608 | 0.55395 | 0 | 0.76797 | 0 | 0.47236 | 0.018446 | 0.75097 | 0 | 0.12096 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 7.5388 | 0.09221% | CZ 6B | 0 | 0 | 0.14364 | 0.089915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23356 | 0.09221% |  | CZ 6B | 11.1059 | 5.7993 | 15.6999 | 17.8676 | 0 | 4.9452 | 0.19312 | 7.8619 | 0 | 1.2663 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 104.4511 | 0.09221%
CZ 7 | 0.11277 | 0.058847 | 0.15147 | 0.25184 | 0 | 0.05566 | 0.0025001 | 0.083491 | 0 | 0.014444 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.1342 | 0.04244% | CZ 7 | 3.6196 | 1.8889 | 15.456 | 17.3118 | 0 | 1.7866 | 0.080248 | 2.6799 | 0 | 0.46362 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 56.2292 | 0.04244% | CZ 7 | 1.0608 | 0.55359 | 0 | 1.128 | 0 | 0.52362 | 0.023519 | 0.78542 | 0 | 0.13588 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 8.0041 | 0.04244% | CZ 7 | 0 | 0 | 0.15456 | 0.13463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28919 | 0.04244% |  | CZ 7 | 11.1059 | 5.7956 | 16.8934 | 26.524 | 0 | 5.4817 | 0.24622 | 8.2226 | 0 | 1.4225 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 115.4038 | 0.04244%
CZ 8 | 0.11277 | 0.058525 | 0.16335 | 0.33338 | 0 | 0.0383 | 0.0015862 | 0.096803 | 0 | 0.014994 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.2229 | 0% | CZ 8 | 3.6196 | 1.8785 | 16.6687 | 22.7951 | 0 | 1.2293 | 0.050913 | 3.1072 | 0 | 0.48126 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 62.7733 | 0% | CZ 8 | 1.0608 | 0.55056 | 0 | 1.5096 | 0 | 0.3603 | 0.014922 | 0.91066 | 0 | 0.14105 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 8.3412 | 0% | CZ 8 | 0 | 0 | 0.16669 | 0.17644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34313 | 0% |  | CZ 8 | 11.1059 | 5.7638 | 18.2189 | 35.0891 | 0 | 3.772 | 0.15622 | 9.5337 | 0 | 1.4766 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 124.8282 | 0%
US Weighted | 0.11277 | 0.058979 | 0.1163 | 0.068507 | 0 | 0.15007 | 0.0072494 | 0.080327 | 0 | 0.01305 | 0 | 0.055468 | 0.0072867 | 0 | 0 | 0.34047 | 1.0105 | 100% | US Weighted | 3.6196 | 1.8931 | 11.8678 | 4.694 | 0 | 4.8171 | 0.23269 | 2.5783 | 0 | 0.41888 | 0 | 1.7804 | 0.23389 | 0 | 0 | 10.9284 | 43.0641 | 100% | US Weighted | 1.0608 | 0.55484 | 0 | 0.30888 | 0 | 1.4118 | 0.068197 | 0.75566 | 0 | 0.12277 | 0 | 0.5218 | 0.068548 | 0 | 0 | 3.2029 | 8.0763 | 100% | US Weighted | 0 | 0 | 0.11868 | 0.036401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15508 | 100% |  | US Weighted | 11.1059 | 5.8086 | 12.9715 | 7.2123 | 0 | 14.7801 | 0.71396 | 7.911 | 0 | 1.2852 | 0 | 5.4628 | 0.71763 | 0 | 0 | 33.5315 | 101.5005 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2010 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2010 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2010 | [17 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2010 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [7 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight |  | STD2010 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.13548 | 0.059071 | 0.082006 | 0 | 0 | 0.65034 | 0.033576 | 0.16237 | 0 | 0.021132 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.5473 | 0% | CZ 0A | 4.3485 | 1.896 | 8.368 | 0 | 0 | 20.8744 | 1.0777 | 5.2116 | 0 | 0.67828 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 55.4012 | 0% | CZ 0A | 1.2745 | 0.5557 | 0 | 0 | 0 | 6.1179 | 0.31586 | 1.5274 | 0 | 0.19879 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 13.7846 | 0% | CZ 0A | 0 | 0 | 0.08368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08368 | 0% |  | CZ 0A | 13.3426 | 5.8176 | 9.1462 | 0 | 0 | 64.0487 | 3.3068 | 15.9907 | 0 | 2.0812 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 153.4575 | 0%
CZ 0B | 0.13548 | 0.059081 | 0.081587 | 0.00012346 | 0 | 0.5188 | 0.027249 | 0.15707 | 0 | 0.02525 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.408 | 0% | CZ 0B | 4.3485 | 1.8964 | 8.3252 | 0.0042708 | 0 | 16.6524 | 0.87463 | 5.0416 | 0 | 0.81046 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 50.9 | 0% | CZ 0B | 1.2745 | 0.5558 | 0 | 0.00112 | 0 | 4.8805 | 0.25634 | 1.4776 | 0 | 0.23753 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 12.4778 | 0% | CZ 0B | 0 | 0 | 0.083252 | 4.4946e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083256 | 0% |  | CZ 0B | 13.3426 | 5.8187 | 9.0994 | 0.012216 | 0 | 51.0944 | 2.6836 | 15.469 | 0 | 2.4867 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 139.7303 | 0%
CZ 1A | 0.13548 | 0.059088 | 0.089665 | 0 | 0 | 0.46323 | 0.021321 | 0.12803 | 0 | 0.018782 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.3189 | 14.96% | CZ 1A | 4.3485 | 1.8966 | 9.1495 | 0 | 0 | 14.8688 | 0.68435 | 4.1095 | 0 | 0.60287 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 48.6067 | 14.96% | CZ 1A | 1.2745 | 0.55586 | 0 | 0 | 0 | 4.3578 | 0.20057 | 1.2044 | 0 | 0.17669 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 11.5642 | 14.96% | CZ 1A | 0 | 0 | 0.091495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091495 | 14.96% |  | CZ 1A | 13.3426 | 5.8193 | 10.0004 | 0 | 0 | 45.6216 | 2.0998 | 12.6091 | 0 | 1.8498 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 131.0663 | 14.96%
CZ 1B | 0.13548 | 0.059015 | 0.089885 | 0.008252 | 0 | 0.41332 | 0.020929 | 0.13798 | 0 | 0.021787 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.29 | 0% | CZ 1B | 4.3485 | 1.8943 | 9.172 | 0.52219 | 0 | 13.2668 | 0.67177 | 4.4289 | 0 | 0.6993 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 47.9503 | 0% | CZ 1B | 1.2745 | 0.55517 | 0 | 0.04302 | 0 | 3.8883 | 0.19688 | 1.298 | 0 | 0.20495 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 11.2553 | 0% | CZ 1B | 0 | 0 | 0.09172 | 0.0037541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095474 | 0% |  | CZ 1B | 13.3426 | 5.8121 | 10.025 | 0.8607 | 0 | 40.7065 | 2.0612 | 13.5892 | 0 | 2.1457 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 128.2665 | 0%
CZ 2A | 0.13548 | 0.058994 | 0.098422 | 0.015483 | 0 | 0.33604 | 0.016468 | 0.10225 | 0 | 0.017735 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.1842 | 12.37% | CZ 2A | 4.3485 | 1.8936 | 10.043 | 1.0262 | 0 | 10.7862 | 0.52858 | 3.282 | 0 | 0.56926 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 45.4239 | 12.37% | CZ 2A | 1.2745 | 0.55498 | 0 | 0.074478 | 0 | 3.1613 | 0.15492 | 0.96189 | 0 | 0.16684 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 10.1433 | 12.37% | CZ 2A | 0 | 0 | 0.10043 | 0.0077206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10815 | 12.37% |  | CZ 2A | 13.3426 | 5.81 | 10.977 | 1.6236 | 0 | 33.0953 | 1.6218 | 10.07 | 0 | 1.7467 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 118.0106 | 12.37%
CZ 2B | 0.13548 | 0.059036 | 0.098974 | 0.01253 | 0 | 0.25851 | 0.0098288 | 0.105 | 0 | 0.017529 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.1002 | 0.8671% | CZ 2B | 4.3485 | 1.8949 | 10.0994 | 0.79222 | 0 | 8.2975 | 0.31548 | 3.3702 | 0 | 0.56263 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 42.6275 | 0.8671% | CZ 2B | 1.2745 | 0.55537 | 0 | 0.065419 | 0 | 2.4319 | 0.092463 | 0.98774 | 0 | 0.1649 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 9.3667 | 0.8671% | CZ 2B | 0 | 0 | 0.10099 | 0.0056901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10668 | 0.8671% |  | CZ 2B | 13.3426 | 5.8142 | 11.0387 | 1.3068 | 0 | 25.4593 | 0.96799 | 10.3407 | 0 | 1.7263 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 109.7202 | 0.8671%
CZ 3A | 0.13548 | 0.059025 | 0.11342 | 0.10111 | 0 | 0.17107 | 0.007875 | 0.081411 | 0 | 0.016069 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.0888 | 5.906% | CZ 3A | 4.3485 | 1.8946 | 11.5738 | 6.8853 | 0 | 5.4911 | 0.25277 | 2.6131 | 0 | 0.51577 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 46.5215 | 5.906% | CZ 3A | 1.2745 | 0.55527 | 0 | 0.46162 | 0 | 1.6094 | 0.074082 | 0.76586 | 0 | 0.15116 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 8.6862 | 5.906% | CZ 3A | 0 | 0 | 0.11574 | 0.053102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16884 | 5.906% |  | CZ 3A | 13.3426 | 5.8131 | 12.6501 | 10.6368 | 0 | 16.8484 | 0.77557 | 8.0178 | 0 | 1.5825 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 109.3906 | 5.906%
CZ 3B | 0.13548 | 0.059022 | 0.10959 | 0.041755 | 0 | 0.18137 | 0.0070346 | 0.090746 | 0 | 0.015022 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.0434 | 6.552% | CZ 3B | 4.3485 | 1.8945 | 11.1826 | 2.8044 | 0 | 5.8216 | 0.2258 | 2.9127 | 0 | 0.48216 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 42.6189 | 6.552% | CZ 3B | 1.2745 | 0.55524 | 0 | 0.19586 | 0 | 1.7062 | 0.066177 | 0.85368 | 0 | 0.14131 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 8.5874 | 6.552% | CZ 3B | 0 | 0 | 0.11183 | 0.021362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13319 | 6.552% |  | CZ 3B | 13.3426 | 5.8128 | 12.2226 | 4.3853 | 0 | 17.8622 | 0.6928 | 8.9371 | 0 | 1.4794 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 104.4585 | 6.552%
CZ 3C | 0.13548 | 0.059015 | 0.11514 | 0.015351 | 0 | 0.037988 | 0.0017403 | 0.047968 | 0 | 0.0099864 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 0.82601 | 3.035% | CZ 3C | 4.3485 | 1.8943 | 11.7485 | 1.0017 | 0 | 1.2193 | 0.055859 | 1.5397 | 0 | 0.32054 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 35.0749 | 3.035% | CZ 3C | 1.2745 | 0.55517 | 0 | 0.07596 | 0 | 0.35737 | 0.016371 | 0.45125 | 0 | 0.093945 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 6.619 | 3.035% | CZ 3C | 0 | 0 | 0.11748 | 0.007425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12491 | 3.035% |  | CZ 3C | 13.3426 | 5.8121 | 12.8411 | 1.6068 | 0 | 3.7413 | 0.17139 | 4.7241 | 0 | 0.98351 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 82.9465 | 3.035%
CZ 4A | 0.13548 | 0.058934 | 0.12523 | 0.18263 | 0 | 0.12665 | 0.005809 | 0.080203 | 0 | 0.017028 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.1353 | 33.86% | CZ 4A | 4.3485 | 1.8917 | 12.779 | 12.4687 | 0 | 4.0651 | 0.18646 | 2.5743 | 0 | 0.54656 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 51.8068 | 33.86% | CZ 4A | 1.2745 | 0.55442 | 0 | 0.8295 | 0 | 1.1914 | 0.054648 | 0.75449 | 0 | 0.16019 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 8.6136 | 33.86% | CZ 4A | 0 | 0 | 0.12779 | 0.096384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22417 | 33.86% |  | CZ 4A | 13.3426 | 5.8042 | 13.9674 | 19.2188 | 0 | 12.4729 | 0.57211 | 7.8988 | 0 | 1.677 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 114.6775 | 33.86%
CZ 4B | 0.13548 | 0.05898 | 0.1219 | 0.063793 | 0 | 0.14015 | 0.0051473 | 0.085476 | 0 | 0.0154 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.0297 | 0% | CZ 4B | 4.3485 | 1.8931 | 12.4391 | 4.2874 | 0 | 4.4986 | 0.16522 | 2.7436 | 0 | 0.4943 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 43.8164 | 0% | CZ 4B | 1.2745 | 0.55484 | 0 | 0.29887 | 0 | 1.3185 | 0.048422 | 0.8041 | 0 | 0.14487 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 8.2385 | 0% | CZ 4B | 0 | 0 | 0.12439 | 0.032677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15707 | 0% |  | CZ 4B | 13.3426 | 5.8087 | 13.5959 | 6.7004 | 0 | 13.803 | 0.50693 | 8.4181 | 0 | 1.5167 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 103.4159 | 0%
CZ 4C | 0.13548 | 0.058868 | 0.12881 | 0.11296 | 0 | 0.027238 | 0.001159 | 0.058066 | 0 | 0.013365 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 0.93929 | 5.13% | CZ 4C | 4.3485 | 1.8895 | 13.1434 | 7.6948 | 0 | 0.8743 | 0.037202 | 1.8638 | 0 | 0.429 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 43.2271 | 5.13% | CZ 4C | 1.2745 | 0.55379 | 0 | 0.51541 | 0 | 0.25624 | 0.010903 | 0.54625 | 0 | 0.12573 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 7.0772 | 5.13% | CZ 4C | 0 | 0 | 0.13143 | 0.059362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1908 | 5.13% |  | CZ 4C | 13.3426 | 5.7976 | 14.3657 | 11.8842 | 0 | 2.6826 | 0.11415 | 5.7187 | 0 | 1.3163 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 94.9454 | 5.13%
CZ 5A | 0.13548 | 0.058955 | 0.13524 | 0.27638 | 0 | 0.064446 | 0.0028503 | 0.078991 | 0 | 0.015407 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.1711 | 14.08% | CZ 5A | 4.3485 | 1.8923 | 13.8003 | 18.9392 | 0 | 2.0686 | 0.091487 | 2.5354 | 0 | 0.49452 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 57.1169 | 14.08% | CZ 5A | 1.2745 | 0.55461 | 0 | 1.2459 | 0 | 0.60626 | 0.026813 | 0.7431 | 0 | 0.14494 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 8.3905 | 14.08% | CZ 5A | 0 | 0 | 0.138 | 0.14688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28489 | 14.08% |  | CZ 5A | 13.3426 | 5.8062 | 15.0837 | 29.0972 | 0 | 6.347 | 0.28071 | 7.7795 | 0 | 1.5173 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 118.9779 | 14.08%
CZ 5B | 0.13548 | 0.058955 | 0.13243 | 0.1398 | 0 | 0.096485 | 0.0034525 | 0.084534 | 0 | 0.014626 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.0691 | 1.936% | CZ 5B | 4.3485 | 1.8923 | 13.5134 | 9.4957 | 0 | 3.097 | 0.11082 | 2.7134 | 0 | 0.46946 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 48.5871 | 1.936% | CZ 5B | 1.2745 | 0.55461 | 0 | 0.64148 | 0 | 0.90767 | 0.032479 | 0.79524 | 0 | 0.13759 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 8.138 | 1.936% | CZ 5B | 0 | 0 | 0.13513 | 0.07307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2082 | 1.936% |  | CZ 5B | 13.3426 | 5.8062 | 14.7702 | 14.7021 | 0 | 9.5024 | 0.34002 | 8.3254 | 0 | 1.4404 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 107.953 | 1.936%
CZ 5C | 0.13548 | 0.058864 | 0.13448 | 0.10015 | 0 | 0.012199 | 0.00054274 | 0.053279 | 0 | 0.01187 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 0.91021 | 0% | CZ 5C | 4.3485 | 1.8894 | 13.7222 | 6.8433 | 0 | 0.39157 | 0.017421 | 1.7102 | 0 | 0.38101 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 42.2501 | 0% | CZ 5C | 1.2745 | 0.55376 | 0 | 0.45411 | 0 | 0.11476 | 0.0051057 | 0.50122 | 0 | 0.11167 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 6.8095 | 0% | CZ 5C | 0 | 0 | 0.13722 | 0.052938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19016 | 0% |  | CZ 5C | 13.3426 | 5.7973 | 14.9983 | 10.5403 | 0 | 1.2015 | 0.053452 | 5.2472 | 0 | 1.169 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 92.0733 | 0%
CZ 6A | 0.13548 | 0.058927 | 0.14265 | 0.38968 | 0 | 0.074033 | 0.003365 | 0.089587 | 0 | 0.017847 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.3149 | 1.175% | CZ 6A | 4.3485 | 1.8914 | 14.5565 | 26.5493 | 0 | 2.3763 | 0.10801 | 2.8755 | 0 | 0.57286 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 66.225 | 1.175% | CZ 6A | 1.2745 | 0.55435 | 0 | 1.7773 | 0 | 0.69645 | 0.031655 | 0.84277 | 0 | 0.1679 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 9.1393 | 1.175% | CZ 6A | 0 | 0 | 0.14556 | 0.20485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35042 | 1.175% |  | CZ 6A | 13.3426 | 5.8035 | 15.9102 | 40.9965 | 0 | 7.2912 | 0.3314 | 8.823 | 0 | 1.7577 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 133.9797 | 1.175%
CZ 6B | 0.13548 | 0.058885 | 0.14077 | 0.26428 | 0 | 0.054403 | 0.0019994 | 0.087661 | 0 | 0.014868 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.1617 | 0.09221% | CZ 6B | 4.3485 | 1.8901 | 14.3638 | 17.9507 | 0 | 1.7462 | 0.064176 | 2.8137 | 0 | 0.47722 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 56.601 | 0.09221% | CZ 6B | 1.2745 | 0.55395 | 0 | 1.2127 | 0 | 0.51179 | 0.018809 | 0.82466 | 0 | 0.13986 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 8.3307 | 0.09221% | CZ 6B | 0 | 0 | 0.14364 | 0.13813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28177 | 0.09221% |  | CZ 6B | 13.3426 | 5.7993 | 15.6996 | 27.7935 | 0 | 5.3579 | 0.19691 | 8.6333 | 0 | 1.4642 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 118.0111 | 0.09221%
CZ 7 | 0.13548 | 0.058847 | 0.15147 | 0.35413 | 0 | 0.059337 | 0.0025806 | 0.089349 | 0 | 0.016506 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.271 | 0.04244% | CZ 7 | 4.3485 | 1.8889 | 15.456 | 24.2088 | 0 | 1.9046 | 0.082833 | 2.8679 | 0 | 0.52981 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 64.2338 | 0.04244% | CZ 7 | 1.2745 | 0.55359 | 0 | 1.6042 | 0 | 0.5582 | 0.024277 | 0.84053 | 0 | 0.15528 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 8.805 | 0.04244% | CZ 7 | 0 | 0 | 0.15456 | 0.18735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34191 | 0.04244% |  | CZ 7 | 13.3426 | 5.7956 | 16.8934 | 37.2721 | 0 | 5.8438 | 0.25415 | 8.7995 | 0 | 1.6256 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 129.5505 | 0.04244%
CZ 8 | 0.13548 | 0.058525 | 0.16335 | 0.44363 | 0 | 0.034546 | 0.0013691 | 0.10465 | 0 | 0.016223 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.3611 | 0% | CZ 8 | 4.3485 | 1.8785 | 16.6687 | 30.0619 | 0 | 1.1089 | 0.043945 | 3.3591 | 0 | 0.52071 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 70.9368 | 0% | CZ 8 | 1.2745 | 0.55056 | 0 | 2.0452 | 0 | 0.32499 | 0.01288 | 0.98448 | 0 | 0.15261 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 9.1396 | 0% | CZ 8 | 0 | 0 | 0.16669 | 0.23084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39752 | 0% |  | CZ 8 | 13.3426 | 5.7638 | 18.2189 | 46.6418 | 0 | 3.4023 | 0.13484 | 10.3065 | 0 | 1.5977 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 139.1321 | 0%
US Weighted | 0.13548 | 0.058979 | 0.1163 | 0.12543 | 0 | 0.19239 | 0.0088263 | 0.088979 | 0 | 0.016525 | 0 | 0.055583 | 0.0072902 | 0 | 0 | 0.34047 | 1.1463 | 100% | US Weighted | 4.3485 | 1.8931 | 11.8678 | 8.5608 | 0 | 6.1752 | 0.28331 | 2.856 | 0 | 0.53042 | 0 | 1.7841 | 0.234 | 0 | 0 | 10.9284 | 49.4617 | 100% | US Weighted | 1.2745 | 0.55484 | 0 | 0.57003 | 0 | 1.8098 | 0.083032 | 0.83706 | 0 | 0.15546 | 0 | 0.52289 | 0.068581 | 0 | 0 | 3.2029 | 9.0792 | 100% | US Weighted | 0 | 0 | 0.11868 | 0.066159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18484 | 100% |  | US Weighted | 13.3426 | 5.8086 | 12.9715 | 13.1988 | 0 | 18.9473 | 0.86926 | 8.7632 | 0 | 1.6275 | 0 | 5.4742 | 0.71798 | 0 | 0 | 33.5315 | 115.2523 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2007 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2007 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2007 | [17 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2007 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [7 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight |  | STD2007 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.1171 | 0.074831 | 0.082043 | 0 | 0 | 0.67833 | 0.035856 | 0.16794 | 0 | 0.028524 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.5955 | 0% | CZ 0A | 3.7586 | 2.4019 | 8.3717 | 0 | 0 | 21.7729 | 1.1509 | 5.3906 | 0 | 0.91554 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 56.9515 | 0% | CZ 0A | 1.1016 | 0.70396 | 0 | 0 | 0 | 6.3813 | 0.33731 | 1.5799 | 0 | 0.26833 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 14.2379 | 0% | CZ 0A | 0 | 0 | 0.083717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083717 | 0% |  | CZ 0A | 11.5325 | 7.3698 | 9.1503 | 0 | 0 | 66.8054 | 3.5313 | 16.5401 | 0 | 2.8092 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 158.207 | 0%
CZ 0B | 0.1171 | 0.074845 | 0.081612 | 0.00023212 | 0 | 0.54208 | 0.028877 | 0.16672 | 0 | 0.034059 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.4564 | 0% | CZ 0B | 3.7586 | 2.4024 | 8.3278 | 0.0089908 | 0 | 17.3997 | 0.92689 | 5.3513 | 0 | 1.0932 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 52.4582 | 0% | CZ 0B | 1.1016 | 0.7041 | 0 | 0.0019764 | 0 | 5.0996 | 0.27166 | 1.5684 | 0 | 0.32041 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 12.9332 | 0% | CZ 0B | 0 | 0 | 0.083278 | 2.2473e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0833 | 0% |  | CZ 0B | 11.5325 | 7.3712 | 9.1023 | 0.023147 | 0 | 53.3873 | 2.844 | 16.4194 | 0 | 3.3544 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 144.5026 | 0%
CZ 1A | 0.1171 | 0.074852 | 0.089705 | 7.0031e-06 | 0 | 0.47326 | 0.022501 | 0.1308 | 0 | 0.025645 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.3448 | 14.96% | CZ 1A | 3.7586 | 2.4026 | 9.1536 | 0.00022478 | 0 | 15.1908 | 0.72223 | 4.1984 | 0 | 0.82316 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 49.4388 | 14.96% | CZ 1A | 1.1016 | 0.70416 | 0 | 6.588e-05 | 0 | 4.4522 | 0.21167 | 1.2305 | 0 | 0.24125 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 11.8069 | 14.96% | CZ 1A | 0 | 0 | 0.091536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091536 | 14.96% |  | CZ 1A | 11.5325 | 7.3719 | 10.0048 | 0.0006897 | 0 | 46.6096 | 2.216 | 12.8819 | 0 | 2.5257 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 133.6116 | 14.96%
CZ 1B | 0.1171 | 0.074758 | 0.089925 | 0.010028 | 0 | 0.42004 | 0.021668 | 0.14386 | 0 | 0.028583 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.3169 | 0% | CZ 1B | 3.7586 | 2.3996 | 9.176 | 0.63973 | 0 | 13.4824 | 0.69548 | 4.6177 | 0 | 0.91745 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 48.8763 | 0% | CZ 1B | 1.1016 | 0.70327 | 0 | 0.051584 | 0 | 3.9515 | 0.20383 | 1.3534 | 0 | 0.26889 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 11.4996 | 0% | CZ 1B | 0 | 0 | 0.09176 | 0.0046373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096398 | 0% |  | CZ 1B | 11.5325 | 7.3626 | 10.0294 | 1.0469 | 0 | 41.3679 | 2.1339 | 14.1685 | 0 | 2.815 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 130.9252 | 0%
CZ 2A | 0.1171 | 0.074733 | 0.098473 | 0.024942 | 0 | 0.343 | 0.017133 | 0.10491 | 0 | 0.023744 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2149 | 12.37% | CZ 2A | 3.7586 | 2.3988 | 10.0483 | 1.683 | 0 | 11.0094 | 0.54993 | 3.3675 | 0 | 0.76213 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 46.7669 | 12.37% | CZ 2A | 1.1016 | 0.70304 | 0 | 0.11595 | 0 | 3.2267 | 0.16118 | 0.98695 | 0 | 0.22337 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 10.3843 | 12.37% | CZ 2A | 0 | 0 | 0.10048 | 0.012874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11336 | 12.37% |  | CZ 2A | 11.5325 | 7.3601 | 10.9828 | 2.621 | 0 | 33.7802 | 1.6874 | 10.3324 | 0 | 2.3384 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 121.1033 | 12.37%
CZ 2B | 0.1171 | 0.074786 | 0.099019 | 0.020638 | 0 | 0.26354 | 0.010126 | 0.1101 | 0 | 0.02352 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.1297 | 0.8671% | CZ 2B | 3.7586 | 2.4005 | 10.1039 | 1.3408 | 0 | 8.4592 | 0.32504 | 3.5338 | 0 | 0.75494 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 43.8661 | 0.8671% | CZ 2B | 1.1016 | 0.70354 | 0 | 0.1029 | 0 | 2.4792 | 0.095263 | 1.0357 | 0 | 0.22126 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.605 | 0.8671% | CZ 2B | 0 | 0 | 0.10104 | 0.0098971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11094 | 0.8671% |  | CZ 2B | 11.5325 | 7.3653 | 11.0436 | 2.1591 | 0 | 25.9552 | 0.99731 | 10.8428 | 0 | 2.3164 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 112.6806 | 0.8671%
CZ 3A | 0.1171 | 0.074772 | 0.11348 | 0.14389 | 0 | 0.17209 | 0.0080921 | 0.086047 | 0 | 0.021815 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.1482 | 5.906% | CZ 3A | 3.7586 | 2.4 | 11.5799 | 9.9442 | 0 | 5.5236 | 0.25974 | 2.7619 | 0 | 0.7002 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 50.1175 | 5.906% | CZ 3A | 1.1016 | 0.7034 | 0 | 0.63733 | 0 | 1.6189 | 0.076125 | 0.80947 | 0 | 0.20522 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.0176 | 5.906% | CZ 3A | 0 | 0 | 0.1158 | 0.077697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1935 | 5.906% |  | CZ 3A | 11.5325 | 7.3639 | 12.6569 | 15.1644 | 0 | 16.948 | 0.79695 | 8.4744 | 0 | 2.1484 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 115.554 | 5.906%
CZ 3B | 0.1171 | 0.074768 | 0.10964 | 0.062668 | 0 | 0.1812 | 0.0071116 | 0.09548 | 0 | 0.019822 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.0787 | 6.552% | CZ 3B | 3.7586 | 2.3999 | 11.1882 | 4.2736 | 0 | 5.8162 | 0.22827 | 3.0647 | 0 | 0.63625 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 44.555 | 6.552% | CZ 3B | 1.1016 | 0.70337 | 0 | 0.28529 | 0 | 1.7046 | 0.066901 | 0.89821 | 0 | 0.18647 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 8.812 | 6.552% | CZ 3B | 0 | 0 | 0.11188 | 0.033001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14488 | 6.552% |  | CZ 3B | 11.5325 | 7.3636 | 12.2288 | 6.5938 | 0 | 17.8457 | 0.70039 | 9.4034 | 0 | 1.9522 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 108.0888 | 6.552%
CZ 3C | 0.1171 | 0.074758 | 0.1152 | 0.026683 | 0 | 0.033758 | 0.0015792 | 0.048787 | 0 | 0.013204 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 0.84198 | 3.035% | CZ 3C | 3.7586 | 2.3996 | 11.755 | 1.7892 | 0 | 1.0836 | 0.050689 | 1.566 | 0 | 0.42383 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 36.0157 | 3.035% | CZ 3C | 1.1016 | 0.70327 | 0 | 0.12557 | 0 | 0.31758 | 0.014856 | 0.45895 | 0 | 0.12422 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 6.7116 | 3.035% | CZ 3C | 0 | 0 | 0.11755 | 0.013607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13116 | 3.035% |  | CZ 3C | 11.5325 | 7.3626 | 12.8482 | 2.8019 | 0 | 3.3247 | 0.15553 | 4.8048 | 0 | 1.3004 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 84.5991 | 3.035%
CZ 4A | 0.1171 | 0.07466 | 0.1253 | 0.26453 | 0 | 0.12588 | 0.0059421 | 0.087556 | 0 | 0.023457 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2353 | 33.86% | CZ 4A | 3.7586 | 2.3964 | 12.7862 | 18.3387 | 0 | 4.0405 | 0.19073 | 2.8104 | 0 | 0.75291 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 58.2637 | 33.86% | CZ 4A | 1.1016 | 0.70235 | 0 | 1.164 | 0 | 1.1842 | 0.055899 | 0.82367 | 0 | 0.22067 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.1179 | 33.86% | CZ 4A | 0 | 0 | 0.12786 | 0.14367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27153 | 33.86% |  | CZ 4A | 11.5325 | 7.3529 | 13.9753 | 27.889 | 0 | 12.3974 | 0.58521 | 8.623 | 0 | 2.3102 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 125.134 | 33.86%
CZ 4B | 0.1171 | 0.074716 | 0.12197 | 0.096511 | 0 | 0.13364 | 0.0049477 | 0.089517 | 0 | 0.020022 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.0693 | 0% | CZ 4B | 3.7586 | 2.3982 | 12.4459 | 6.5949 | 0 | 4.2895 | 0.15881 | 2.8733 | 0 | 0.64266 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 46.3513 | 0% | CZ 4B | 1.1016 | 0.70288 | 0 | 0.43754 | 0 | 1.2572 | 0.046544 | 0.84211 | 0 | 0.18835 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 8.4418 | 0% | CZ 4B | 0 | 0 | 0.12446 | 0.05102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17548 | 0% |  | CZ 4B | 11.5325 | 7.3584 | 13.6034 | 10.1572 | 0 | 13.1616 | 0.48727 | 8.8161 | 0 | 1.9719 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 107.5568 | 0%
CZ 4C | 0.1171 | 0.074572 | 0.12888 | 0.16552 | 0 | 0.022865 | 0.00099093 | 0.063833 | 0 | 0.017277 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.0019 | 5.13% | CZ 4C | 3.7586 | 2.3936 | 13.1511 | 11.4392 | 0 | 0.73392 | 0.031807 | 2.0489 | 0 | 0.55454 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 47.301 | 5.13% | CZ 4C | 1.1016 | 0.70153 | 0 | 0.73315 | 0 | 0.2151 | 0.0093221 | 0.6005 | 0 | 0.16253 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 7.3893 | 5.13% | CZ 4C | 0 | 0 | 0.13151 | 0.089377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22089 | 5.13% |  | CZ 4C | 11.5325 | 7.3443 | 14.3742 | 17.4442 | 0 | 2.2519 | 0.097593 | 6.2866 | 0 | 1.7015 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 101.5013 | 5.13%
CZ 5A | 0.1171 | 0.074681 | 0.13532 | 0.38934 | 0 | 0.06148 | 0.0027837 | 0.088634 | 0 | 0.021083 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.3013 | 14.08% | CZ 5A | 3.7586 | 2.3971 | 13.8084 | 26.9762 | 0 | 1.9734 | 0.089351 | 2.845 | 0 | 0.67671 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 65.714 | 14.08% | CZ 5A | 1.1016 | 0.70255 | 0 | 1.7152 | 0 | 0.57836 | 0.026187 | 0.83381 | 0 | 0.19833 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.0215 | 14.08% | CZ 5A | 0 | 0 | 0.13808 | 0.21124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34932 | 14.08% |  | CZ 5A | 11.5325 | 7.355 | 15.0925 | 41.0446 | 0 | 6.0549 | 0.27416 | 8.7292 | 0 | 2.0763 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 132.6277 | 14.08%
CZ 5B | 0.1171 | 0.074684 | 0.13251 | 0.19245 | 0 | 0.089055 | 0.0032004 | 0.090819 | 0 | 0.018684 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.1294 | 1.936% | CZ 5B | 3.7586 | 2.3972 | 13.521 | 13.2441 | 0 | 2.8585 | 0.10273 | 2.9151 | 0 | 0.59972 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 52.5863 | 1.936% | CZ 5B | 1.1016 | 0.70258 | 0 | 0.85994 | 0 | 0.83777 | 0.030107 | 0.85437 | 0 | 0.17577 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 8.4277 | 1.936% | CZ 5B | 0 | 0 | 0.13521 | 0.1031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23831 | 1.936% |  | CZ 5B | 11.5325 | 7.3553 | 14.7785 | 20.2715 | 0 | 8.7706 | 0.31519 | 8.9444 | 0 | 1.8401 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 114.2766 | 1.936%
CZ 5C | 0.1171 | 0.074569 | 0.13456 | 0.13184 | 0 | 0.0078364 | 0.00036066 | 0.05663 | 0 | 0.014941 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 0.94874 | 0% | CZ 5C | 3.7586 | 2.3935 | 13.7304 | 9.1238 | 0 | 0.25153 | 0.011576 | 1.8177 | 0 | 0.47958 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 44.756 | 0% | CZ 5C | 1.1016 | 0.70149 | 0 | 0.58232 | 0 | 0.07372 | 0.0033928 | 0.53274 | 0 | 0.14056 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 7.0014 | 0% | CZ 5C | 0 | 0 | 0.1373 | 0.071369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20867 | 0% |  | CZ 5C | 11.5325 | 7.3439 | 15.0073 | 13.8969 | 0 | 0.77178 | 0.03552 | 5.5773 | 0 | 1.4715 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 96.1052 | 0%
CZ 6A | 0.1171 | 0.074646 | 0.14274 | 0.53937 | 0 | 0.070391 | 0.0034945 | 0.10081 | 0 | 0.028082 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.4875 | 1.175% | CZ 6A | 3.7586 | 2.396 | 14.5651 | 37.1969 | 0 | 2.2594 | 0.11217 | 3.2359 | 0 | 0.90138 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 77.6147 | 1.175% | CZ 6A | 1.1016 | 0.70222 | 0 | 2.3996 | 0 | 0.6622 | 0.032874 | 0.94838 | 0 | 0.26418 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.9766 | 1.175% | CZ 6A | 0 | 0 | 0.14565 | 0.29009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43575 | 1.175% |  | CZ 6A | 11.5325 | 7.3515 | 15.9197 | 56.8289 | 0 | 6.9325 | 0.34416 | 9.9286 | 0 | 2.7657 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 152.0721 | 1.175%
CZ 6B | 0.1171 | 0.074593 | 0.14086 | 0.36637 | 0 | 0.050265 | 0.0018663 | 0.10018 | 0 | 0.01942 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2816 | 0.09221% | CZ 6B | 3.7586 | 2.3943 | 14.3731 | 25.1378 | 0 | 1.6134 | 0.059905 | 3.2156 | 0 | 0.62332 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 64.3653 | 0.09221% | CZ 6B | 1.1016 | 0.70172 | 0 | 1.6472 | 0 | 0.47286 | 0.017557 | 0.94245 | 0 | 0.18269 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 8.9316 | 0.09221% | CZ 6B | 0 | 0 | 0.14373 | 0.19517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33891 | 0.09221% |  | CZ 6B | 11.5325 | 7.3463 | 15.7098 | 38.5772 | 0 | 4.9503 | 0.18381 | 9.8665 | 0 | 1.9125 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 130.5476 | 0.09221%
CZ 7 | 0.1171 | 0.074548 | 0.15157 | 0.46776 | 0 | 0.053773 | 0.0023951 | 0.098523 | 0 | 0.021731 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.3983 | 0.04244% | CZ 7 | 3.7586 | 2.3928 | 15.4659 | 32.1226 | 0 | 1.726 | 0.076876 | 3.1624 | 0 | 0.6975 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 72.5919 | 0.04244% | CZ 7 | 1.1016 | 0.7013 | 0 | 2.0993 | 0 | 0.50586 | 0.022531 | 0.92684 | 0 | 0.20443 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.4274 | 0.04244% | CZ 7 | 0 | 0 | 0.15466 | 0.2496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40425 | 0.04244% |  | CZ 7 | 11.5325 | 7.3419 | 16.9042 | 49.2589 | 0 | 5.2959 | 0.23588 | 9.7031 | 0 | 2.1401 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 142.8809 | 0.04244%
CZ 8 | 0.1171 | 0.074138 | 0.16345 | 0.52391 | 0 | 0.027414 | 0.0011065 | 0.11223 | 0 | 0.020235 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.4505 | 0% | CZ 8 | 3.7586 | 2.3797 | 16.6784 | 35.5867 | 0 | 0.87992 | 0.035516 | 3.6024 | 0 | 0.64951 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 76.76 | 0% | CZ 8 | 1.1016 | 0.69744 | 0 | 2.4039 | 0 | 0.25789 | 0.010409 | 1.0558 | 0 | 0.19036 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.583 | 0% | CZ 8 | 0 | 0 | 0.16678 | 0.27384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44063 | 0% |  | CZ 8 | 11.5325 | 7.3015 | 18.2295 | 55.0981 | 0 | 2.6998 | 0.10897 | 11.0531 | 0 | 1.9929 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 148.4849 | 0%
US Weighted | 0.1171 | 0.074714 | 0.11637 | 0.18017 | 0 | 0.19362 | 0.0091241 | 0.094789 | 0 | 0.02248 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2193 | 100% | US Weighted | 3.7586 | 2.3982 | 11.8742 | 12.4668 | 0 | 6.2147 | 0.29287 | 3.0425 | 0 | 0.72156 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 53.9587 | 100% | US Weighted | 1.1016 | 0.70286 | 0 | 0.7959 | 0 | 1.8214 | 0.085834 | 0.89171 | 0 | 0.21148 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.4763 | 100% | US Weighted | 0 | 0 | 0.11874 | 0.097512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21625 | 100% |  | US Weighted | 11.5325 | 7.3583 | 12.9785 | 18.9904 | 0 | 19.0684 | 0.89859 | 9.3353 | 0 | 2.214 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 122.8444 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Detail for Standard 90.1-2004 | [5 empty] | Energy Cost Index $/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [5 empty] | Energy Use Index Site kBtu/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment |  |  |  | Electric Detail for Standard 90.1-2004 | [5 empty] | Electric Use Intensity kWh/sq ft/yr | [5 empty] | Prototype Floor Area: | 84352 | Gas Detail for Standard 90.1-2004 | [17 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Detail for Standard 90.1-2004 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  |  | Natural Gas Rate, $/therm: | 0.98 | [16 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 | [20 empty] | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [7 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight |  | STD2004 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.1171 | 0.074831 | 0.082043 | 0 | 0 | 0.6795 | 0.036076 | 0.16856 | 0 | 0.028748 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.5978 | 0% | CZ 0A | 3.7586 | 2.4019 | 8.3717 | 0 | 0 | 21.8104 | 1.158 | 5.4105 | 0 | 0.92274 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 57.0232 | 0% | CZ 0A | 1.1016 | 0.70396 | 0 | 0 | 0 | 6.3923 | 0.33938 | 1.5857 | 0 | 0.27044 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 14.2589 | 0% | CZ 0A | 0 | 0 | 0.083717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083717 | 0% |  | CZ 0A | 11.5325 | 7.3698 | 9.1503 | 0 | 0 | 66.9206 | 3.553 | 16.6011 | 0 | 2.8312 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 158.427 | 0%
CZ 0B | 0.1171 | 0.074845 | 0.081612 | 0.00027874 | 0 | 0.54362 | 0.029021 | 0.16716 | 0 | 0.034371 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.4589 | 0% | CZ 0B | 3.7586 | 2.4024 | 8.3278 | 0.010564 | 0 | 17.4489 | 0.9315 | 5.3656 | 0 | 1.1032 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 52.5379 | 0% | CZ 0B | 1.1016 | 0.7041 | 0 | 0.0024046 | 0 | 5.114 | 0.27301 | 1.5726 | 0 | 0.32334 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 12.9565 | 0% | CZ 0B | 0 | 0 | 0.083278 | 2.3597e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083301 | 0% |  | CZ 0B | 11.5325 | 7.3712 | 9.1023 | 0.027753 | 0 | 53.5384 | 2.8581 | 16.4632 | 0 | 3.3851 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 144.7469 | 0%
CZ 1A | 0.1171 | 0.074852 | 0.089705 | 1.0505e-05 | 0 | 0.47388 | 0.022585 | 0.13111 | 0 | 0.025813 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.346 | 14.96% | CZ 1A | 3.7586 | 2.4026 | 9.1536 | 0.00033718 | 0 | 15.2107 | 0.72493 | 4.2084 | 0 | 0.82855 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 49.4769 | 14.96% | CZ 1A | 1.1016 | 0.70416 | 0 | 9.882e-05 | 0 | 4.458 | 0.21246 | 1.2334 | 0 | 0.24283 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 11.8181 | 14.96% | CZ 1A | 0 | 0 | 0.091536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091536 | 14.96% |  | CZ 1A | 11.5325 | 7.3719 | 10.0048 | 0.0010346 | 0 | 46.6707 | 2.2243 | 12.9126 | 0 | 2.5422 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 133.7285 | 14.96%
CZ 1B | 0.1171 | 0.074758 | 0.089925 | 0.010586 | 0 | 0.42014 | 0.021797 | 0.14437 | 0 | 0.028961 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.3185 | 0% | CZ 1B | 3.7586 | 2.3996 | 9.176 | 0.67558 | 0 | 13.4857 | 0.69964 | 4.634 | 0 | 0.92959 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 48.948 | 0% | CZ 1B | 1.1016 | 0.70327 | 0 | 0.054417 | 0 | 3.9524 | 0.20505 | 1.3582 | 0 | 0.27245 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 11.5129 | 0% | CZ 1B | 0 | 0 | 0.09176 | 0.0048991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096659 | 0% |  | CZ 1B | 11.5325 | 7.3626 | 10.0294 | 1.1052 | 0 | 41.3779 | 2.1467 | 14.2185 | 0 | 2.8523 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 131.0935 | 0%
CZ 2A | 0.1171 | 0.074733 | 0.098473 | 0.041661 | 0 | 0.35591 | 0.018691 | 0.11324 | 0 | 0.027259 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.258 | 12.37% | CZ 2A | 3.7586 | 2.3988 | 10.0483 | 2.8246 | 0 | 11.4238 | 0.59995 | 3.6347 | 0 | 0.87497 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 48.753 | 12.37% | CZ 2A | 1.1016 | 0.70304 | 0 | 0.19188 | 0 | 3.3481 | 0.17583 | 1.0653 | 0 | 0.25644 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 10.7078 | 12.37% | CZ 2A | 0 | 0 | 0.10048 | 0.021699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12218 | 12.37% |  | CZ 2A | 11.5325 | 7.3601 | 10.9828 | 4.3804 | 0 | 35.0516 | 1.8408 | 11.1525 | 0 | 2.6847 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 125.4539 | 12.37%
CZ 2B | 0.1171 | 0.074786 | 0.09902 | 0.041613 | 0 | 0.28334 | 0.011233 | 0.12041 | 0 | 0.028065 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.1865 | 0.8671% | CZ 2B | 3.7586 | 2.4005 | 10.104 | 2.7648 | 0 | 9.0947 | 0.36055 | 3.8648 | 0 | 0.90082 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 46.4381 | 0.8671% | CZ 2B | 1.1016 | 0.70354 | 0 | 0.19925 | 0 | 2.6655 | 0.10567 | 1.1327 | 0 | 0.26402 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 10.0378 | 0.8671% | CZ 2B | 0 | 0 | 0.10104 | 0.020849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12189 | 0.8671% |  | CZ 2B | 11.5325 | 7.3653 | 11.0437 | 4.3648 | 0 | 27.9053 | 1.1063 | 11.8584 | 0 | 2.764 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 118.4088 | 0.8671%
CZ 3A | 0.1171 | 0.074772 | 0.11348 | 0.13035 | 0 | 0.19291 | 0.009153 | 0.090854 | 0 | 0.024458 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.164 | 5.906% | CZ 3A | 3.7586 | 2.4 | 11.5797 | 8.9807 | 0 | 6.1921 | 0.29379 | 2.9162 | 0 | 0.78506 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 50.0955 | 5.906% | CZ 3A | 1.1016 | 0.7034 | 0 | 0.58106 | 0 | 1.8148 | 0.086106 | 0.8547 | 0 | 0.23009 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.2373 | 5.906% | CZ 3A | 0 | 0 | 0.1158 | 0.069981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18578 | 5.906% |  | CZ 3A | 11.5325 | 7.3639 | 12.6566 | 13.732 | 0 | 18.9992 | 0.90144 | 8.9478 | 0 | 2.4088 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 117.0109 | 5.906%
CZ 3B | 0.1171 | 0.074768 | 0.10964 | 0.050639 | 0 | 0.20951 | 0.0082531 | 0.10257 | 0 | 0.022686 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.1061 | 6.552% | CZ 3B | 3.7586 | 2.3999 | 11.1882 | 3.4093 | 0 | 6.725 | 0.26491 | 3.2924 | 0 | 0.72819 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 44.9558 | 6.552% | CZ 3B | 1.1016 | 0.70337 | 0 | 0.23644 | 0 | 1.971 | 0.07764 | 0.96495 | 0 | 0.21342 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.1339 | 6.552% | CZ 3B | 0 | 0 | 0.11188 | 0.026026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13791 | 6.552% |  | CZ 3B | 11.5325 | 7.3636 | 12.2288 | 5.32 | 0 | 20.6341 | 0.81281 | 10.102 | 0 | 2.2343 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 110.6966 | 6.552%
CZ 3C | 0.1171 | 0.074758 | 0.1152 | 0.015963 | 0 | 0.12184 | 0.0055394 | 0.07266 | 0 | 0.026051 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 0.96002 | 3.035% | CZ 3C | 3.7586 | 2.3996 | 11.7551 | 0.99135 | 0 | 3.9107 | 0.1778 | 2.3322 | 0 | 0.83619 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 39.3508 | 3.035% | CZ 3C | 1.1016 | 0.70327 | 0 | 0.085743 | 0 | 1.1462 | 0.052111 | 0.68354 | 0 | 0.24507 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 7.883 | 3.035% | CZ 3C | 0 | 0 | 0.11755 | 0.0069879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12454 | 3.035% |  | CZ 3C | 11.5325 | 7.3626 | 12.8484 | 1.6614 | 0 | 11.9991 | 0.54555 | 7.156 | 0 | 2.5657 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 96.1396 | 3.035%
CZ 4A | 0.1171 | 0.07466 | 0.1253 | 0.29294 | 0 | 0.12282 | 0.0058511 | 0.089615 | 0 | 0.023768 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.263 | 33.86% | CZ 4A | 3.7586 | 2.3964 | 12.7862 | 20.3196 | 0 | 3.9423 | 0.18781 | 2.8764 | 0 | 0.76292 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 60.2195 | 33.86% | CZ 4A | 1.1016 | 0.70235 | 0 | 1.2874 | 0 | 1.1554 | 0.055043 | 0.84304 | 0 | 0.2236 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.234 | 33.86% | CZ 4A | 0 | 0 | 0.12786 | 0.15927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28713 | 33.86% |  | CZ 4A | 11.5325 | 7.3529 | 13.9753 | 30.8862 | 0 | 12.096 | 0.57624 | 8.8258 | 0 | 2.3408 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 128.0542 | 33.86%
CZ 4B | 0.1171 | 0.074716 | 0.12197 | 0.11666 | 0 | 0.12792 | 0.0047586 | 0.09062 | 0 | 0.020099 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.0847 | 0% | CZ 4B | 3.7586 | 2.3982 | 12.4458 | 7.9937 | 0 | 4.1059 | 0.15274 | 2.9087 | 0 | 0.64513 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 47.5981 | 0% | CZ 4B | 1.1016 | 0.70288 | 0 | 0.52589 | 0 | 1.2034 | 0.044766 | 0.85249 | 0 | 0.18908 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 8.4856 | 0% | CZ 4B | 0 | 0 | 0.12446 | 0.061994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18645 | 0% |  | CZ 4B | 11.5325 | 7.3584 | 13.6033 | 12.2815 | 0 | 12.5981 | 0.46865 | 8.9247 | 0 | 1.9794 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 109.2151 | 0%
CZ 4C | 0.1171 | 0.074572 | 0.12888 | 0.19076 | 0 | 0.020379 | 0.00087889 | 0.066221 | 0 | 0.016902 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.0266 | 5.13% | CZ 4C | 3.7586 | 2.3936 | 13.1509 | 13.1964 | 0 | 0.65412 | 0.02821 | 2.1256 | 0 | 0.54252 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 49.0393 | 5.13% | CZ 4C | 1.1016 | 0.70153 | 0 | 0.8431 | 0 | 0.19171 | 0.008268 | 0.62296 | 0 | 0.159 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 7.4937 | 5.13% | CZ 4C | 0 | 0 | 0.13151 | 0.1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23471 | 5.13% |  | CZ 4C | 11.5325 | 7.3443 | 14.374 | 20.106 | 0 | 2.007 | 0.086557 | 6.5218 | 0 | 1.6646 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 104.1052 | 5.13%
CZ 5A | 0.1171 | 0.074681 | 0.13532 | 0.43612 | 0 | 0.057908 | 0.0026647 | 0.092304 | 0 | 0.021839 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.3488 | 14.08% | CZ 5A | 3.7586 | 2.3971 | 13.8082 | 30.2089 | 0 | 1.8587 | 0.08553 | 2.9628 | 0 | 0.70099 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 68.9701 | 14.08% | CZ 5A | 1.1016 | 0.70255 | 0 | 1.9225 | 0 | 0.54476 | 0.025067 | 0.86834 | 0 | 0.20545 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.2358 | 14.08% | CZ 5A | 0 | 0 | 0.13808 | 0.23649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37458 | 14.08% |  | CZ 5A | 11.5325 | 7.355 | 15.0924 | 45.975 | 0 | 5.7031 | 0.26243 | 9.0906 | 0 | 2.1508 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 137.6304 | 14.08%
CZ 5B | 0.1171 | 0.074684 | 0.13251 | 0.23009 | 0 | 0.082787 | 0.0029833 | 0.093901 | 0 | 0.018754 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.1637 | 1.936% | CZ 5B | 3.7586 | 2.3972 | 13.5209 | 15.8278 | 0 | 2.6573 | 0.095758 | 3.014 | 0 | 0.60197 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 55.0629 | 1.936% | CZ 5B | 1.1016 | 0.70258 | 0 | 1.0291 | 0 | 0.7788 | 0.028065 | 0.88336 | 0 | 0.17643 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 8.5655 | 1.936% | CZ 5B | 0 | 0 | 0.13521 | 0.12317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25838 | 1.936% |  | CZ 5B | 11.5325 | 7.3553 | 14.7784 | 24.2355 | 0 | 8.1533 | 0.29381 | 9.2479 | 0 | 1.847 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 117.9122 | 1.936%
CZ 5C | 0.1171 | 0.074569 | 0.13456 | 0.1669 | 0 | 0.0055184 | 0.00025211 | 0.060384 | 0 | 0.014875 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 0.98506 | 0% | CZ 5C | 3.7586 | 2.3935 | 13.7304 | 11.5528 | 0 | 0.17713 | 0.0080922 | 1.9382 | 0 | 0.47744 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 47.2254 | 0% | CZ 5C | 1.1016 | 0.70149 | 0 | 0.73671 | 0 | 0.051914 | 0.0023717 | 0.56805 | 0 | 0.13993 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 7.1676 | 0% | CZ 5C | 0 | 0 | 0.1373 | 0.090392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2277 | 0% |  | CZ 5C | 11.5325 | 7.3439 | 15.0073 | 17.5924 | 0 | 0.54348 | 0.024829 | 5.9469 | 0 | 1.4649 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 99.9248 | 0%
CZ 6A | 0.1171 | 0.074646 | 0.14274 | 0.59796 | 0 | 0.066063 | 0.003428 | 0.10578 | 0 | 0.030821 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.5494 | 1.175% | CZ 6A | 3.7586 | 2.396 | 14.5651 | 41.2985 | 0 | 2.1205 | 0.11003 | 3.3955 | 0 | 0.98927 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 81.8228 | 1.175% | CZ 6A | 1.1016 | 0.70222 | 0 | 2.652 | 0 | 0.62148 | 0.032248 | 0.99515 | 0 | 0.28994 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 10.2602 | 1.175% | CZ 6A | 0 | 0 | 0.14565 | 0.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46815 | 1.175% |  | CZ 6A | 11.5325 | 7.3515 | 15.9197 | 63.0132 | 0 | 6.5063 | 0.33761 | 10.4183 | 0 | 3.0354 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 158.583 | 1.175%
CZ 6B | 0.1171 | 0.074593 | 0.14086 | 0.41965 | 0 | 0.046917 | 0.0017543 | 0.10567 | 0 | 0.019857 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.3373 | 0.09221% | CZ 6B | 3.7586 | 2.3943 | 14.373 | 28.7353 | 0 | 1.5059 | 0.056308 | 3.3916 | 0 | 0.63737 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 68.0417 | 0.09221% | CZ 6B | 1.1016 | 0.70172 | 0 | 1.8947 | 0 | 0.44136 | 0.016503 | 0.99403 | 0 | 0.1868 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.2022 | 0.09221% | CZ 6B | 0 | 0 | 0.14373 | 0.22271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36644 | 0.09221% |  | CZ 6B | 11.5325 | 7.3463 | 15.7097 | 44.177 | 0 | 4.6206 | 0.17277 | 10.4065 | 0 | 1.9556 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 136.3897 | 0.09221%
CZ 7 | 0.1171 | 0.074548 | 0.15156 | 0.57401 | 0 | 0.053546 | 0.0024511 | 0.11101 | 0 | 0.02463 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.5198 | 0.04244% | CZ 7 | 3.7586 | 2.3928 | 15.4656 | 39.381 | 0 | 1.7187 | 0.078674 | 3.563 | 0 | 0.79056 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 80.3383 | 0.04244% | CZ 7 | 1.1016 | 0.7013 | 0 | 2.5813 | 0 | 0.50372 | 0.023058 | 1.0443 | 0 | 0.2317 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 10.0525 | 0.04244% | CZ 7 | 0 | 0 | 0.15466 | 0.30573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46039 | 0.04244% |  | CZ 7 | 11.5325 | 7.3419 | 16.9039 | 60.4407 | 0 | 5.2735 | 0.2414 | 10.9324 | 0 | 2.4257 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 155.5604 | 0.04244%
CZ 8 | 0.1171 | 0.074138 | 0.16345 | 0.58777 | 0 | 0.025029 | 0.0010189 | 0.11885 | 0 | 0.020645 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.5189 | 0% | CZ 8 | 3.7586 | 2.3797 | 16.6783 | 39.6859 | 0 | 0.80338 | 0.032706 | 3.8147 | 0 | 0.66266 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 81.0052 | 0% | CZ 8 | 1.1016 | 0.69744 | 0 | 2.7291 | 0 | 0.23546 | 0.0095856 | 1.118 | 0 | 0.19422 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.951 | 0% | CZ 8 | 0 | 0 | 0.16678 | 0.30374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47052 | 0% |  | CZ 8 | 11.5325 | 7.3015 | 18.2293 | 61.7701 | 0 | 2.465 | 0.10035 | 11.7046 | 0 | 2.0332 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 155.6052 | 0%
US Weighted | 0.1171 | 0.074714 | 0.11637 | 0.19952 | 0 | 0.19939 | 0.0095382 | 0.098893 | 0 | 0.023941 | 0 | 0.057086 | 0.012669 | 0 | 0 | 0.34115 | 1.2504 | 100% | US Weighted | 3.7586 | 2.3982 | 11.8742 | 13.8033 | 0 | 6.4001 | 0.30616 | 3.1742 | 0 | 0.76845 | 0 | 1.8323 | 0.40663 | 0 | 0 | 10.9503 | 55.6725 | 100% | US Weighted | 1.1016 | 0.70286 | 0 | 0.88171 | 0 | 1.8758 | 0.089729 | 0.93032 | 0 | 0.22522 | 0 | 0.53702 | 0.11918 | 0 | 0 | 3.2094 | 9.6727 | 100% | US Weighted | 0 | 0 | 0.11874 | 0.10795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22669 | 100% |  | US Weighted | 11.5325 | 7.3583 | 12.9785 | 21.0294 | 0 | 19.6374 | 0.93938 | 9.7395 | 0 | 2.3578 | 0 | 5.6221 | 1.2477 | 0 | 0 | 33.5988 | 126.0412 | 100%
Building Type: | High-rise Apartment |  |  |  | End Use Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  |  | End Use Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 84352 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 84352 | [16 empty] | Prototype Floor Area: | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [7 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight |  | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 0.044998 | 0.033482 | 0.00022684 | 0 | 0 | 0.20841 | 0.016062 | 0.033597 | 0 | 0.012315 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.35899 | 0% | CZ 0A | 1.4443 | 1.0747 | 0.023147 | 0 | 0 | 6.6896 | 0.51554 | 1.0784 | 0 | 0.39528 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 11.5387 | 0% | CZ 0A | 0.42331 | 0.31497 | 0 | 0 | 0 | 1.9606 | 0.1511 | 0.31606 | 0 | 0.11585 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 3.375 | 0% | CZ 0A | 0 | 0 | 0.00023147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00023147 | 0% |  | CZ 0A | 4.4317 | 3.2975 | 0.0253 | 0 | 0 | 20.5255 | 1.5818 | 3.3088 | 0 | 1.2128 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 35.3583 | 0%
CZ 0B | 0.044998 | 0.033485 | 0.00021803 | 0.00027173 | 0 | 0.15025 | 0.014826 | 0.03344 | 0 | 0.017403 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.30479 | 0% | CZ 0B | 1.4443 | 1.0748 | 0.022248 | 0.010339 | 0 | 4.8228 | 0.47587 | 1.0733 | 0 | 0.55859 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 9.8001 | 0% | CZ 0B | 0.42331 | 0.31501 | 0 | 0.0023387 | 0 | 1.4135 | 0.13947 | 0.31458 | 0 | 0.16371 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.865 | 0% | CZ 0B | 0 | 0 | 0.00022248 | 2.3597e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00024608 | 0% |  | CZ 0B | 4.4317 | 3.2978 | 0.024317 | 0.027063 | 0 | 14.7979 | 1.4601 | 3.2933 | 0 | 1.7139 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 30.0209 | 0%
CZ 1A | 0.044998 | 0.033489 | 0.00026538 | 1.0505e-05 | 0 | 0.14981 | 0.01471 | 0.020757 | 0 | 0.013148 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.28708 | 14.96% | CZ 1A | 1.4443 | 1.0749 | 0.02708 | 0.00033718 | 0 | 4.8085 | 0.47216 | 0.66626 | 0 | 0.42203 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 9.2333 | 14.96% | CZ 1A | 0.42331 | 0.31504 | 0 | 9.882e-05 | 0 | 1.4093 | 0.13838 | 0.19527 | 0 | 0.12369 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.6982 | 14.96% | CZ 1A | 0 | 0 | 0.0002708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002708 | 14.96% |  | CZ 1A | 4.4317 | 3.2981 | 0.029598 | 0.0010346 | 0 | 14.7537 | 1.4487 | 2.0443 | 0 | 1.2949 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 28.277 | 14.96%
CZ 1B | 0.044998 | 0.033447 | 0.00026979 | 0.0097859 | 0 | 0.11236 | 0.011184 | 0.025477 | 0 | 0.013821 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.26124 | 0% | CZ 1B | 1.4443 | 1.0736 | 0.027529 | 0.63928 | 0 | 3.6064 | 0.35898 | 0.81776 | 0 | 0.44361 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 8.7292 | 0% | CZ 1B | 0.42331 | 0.31464 | 0 | 0.048323 | 0 | 1.057 | 0.10521 | 0.23967 | 0 | 0.13001 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.4113 | 0% | CZ 1B | 0 | 0 | 0.00027529 | 0.004744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0050193 | 0% |  | CZ 1B | 4.4317 | 3.294 | 0.03009 | 1.0244 | 0 | 11.0656 | 1.1015 | 2.5091 | 0 | 1.3611 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 25.7923 | 0%
CZ 2A | 0.044998 | 0.033436 | 0.00031824 | 0.039751 | 0 | 0.10388 | 0.010288 | 0.019812 | 0 | 0.014808 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.27719 | 12.37% | CZ 2A | 1.4443 | 1.0732 | 0.032473 | 2.7087 | 0 | 3.3343 | 0.33021 | 0.63591 | 0 | 0.4753 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 10.3522 | 12.37% | CZ 2A | 0.42331 | 0.31455 | 0 | 0.18124 | 0 | 0.97724 | 0.096778 | 0.18638 | 0 | 0.1393 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.4119 | 12.37% | CZ 2A | 0 | 0 | 0.00032473 | 0.020903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021228 | 12.37% |  | CZ 2A | 4.4317 | 3.293 | 0.035493 | 4.1821 | 0 | 10.2307 | 1.0132 | 1.9512 | 0 | 1.4584 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 27.5705 | 12.37%
CZ 2B | 0.044998 | 0.033457 | 0.00032154 | 0.039566 | 0 | 0.078921 | 0.0086943 | 0.022557 | 0 | 0.015169 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.25358 | 0.8671% | CZ 2B | 1.4443 | 1.0739 | 0.03281 | 2.6524 | 0 | 2.5332 | 0.27907 | 0.72403 | 0 | 0.48688 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 9.5444 | 0.8671% | CZ 2B | 0.42331 | 0.31474 | 0 | 0.18628 | 0 | 0.74244 | 0.08179 | 0.2122 | 0 | 0.1427 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.1966 | 0.8671% | CZ 2B | 0 | 0 | 0.0003281 | 0.020168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020496 | 0.8671% |  | CZ 2B | 4.4317 | 3.295 | 0.035862 | 4.1545 | 0 | 7.7726 | 0.85626 | 2.2215 | 0 | 1.4939 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 25.2363 | 0.8671%
CZ 3A | 0.044998 | 0.033454 | 0.00040413 | 0.089763 | 0 | 0.060444 | 0.0058966 | 0.015813 | 0 | 0.012588 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.27326 | 5.906% | CZ 3A | 1.4443 | 1.0738 | 0.041238 | 6.2206 | 0 | 1.9401 | 0.18927 | 0.50756 | 0 | 0.40405 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 12.1387 | 5.906% | CZ 3A | 0.42331 | 0.31471 | 0 | 0.39528 | 0 | 0.56861 | 0.055471 | 0.14876 | 0 | 0.11842 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.1177 | 5.906% | CZ 3A | 0 | 0 | 0.00041238 | 0.048719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049131 | 5.906% |  | CZ 3A | 4.4317 | 3.2947 | 0.045073 | 9.4632 | 0 | 5.9528 | 0.58073 | 1.5573 | 0 | 1.2397 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 27.5401 | 5.906%
CZ 3B | 0.044998 | 0.03345 | 0.00038211 | 0.041543 | 0 | 0.059495 | 0.0063308 | 0.015771 | 0 | 0.011107 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.22298 | 6.552% | CZ 3B | 1.4443 | 1.0737 | 0.03899 | 2.8302 | 0 | 1.9096 | 0.2032 | 0.50621 | 0 | 0.35651 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 8.6805 | 6.552% | CZ 3B | 0.42331 | 0.31468 | 0 | 0.1895 | 0 | 0.55969 | 0.059556 | 0.14836 | 0 | 0.10449 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 1.8927 | 6.552% | CZ 3B | 0 | 0 | 0.0003899 | 0.021836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022226 | 6.552% |  | CZ 3B | 4.4317 | 3.2944 | 0.042617 | 4.3706 | 0 | 5.8594 | 0.62349 | 1.5532 | 0 | 1.0939 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 22.244 | 6.552%
CZ 3C | 0.044998 | 0.033447 | 0.00041404 | 0.0094028 | 0 | 0.096299 | 0.0051893 | 0.028275 | 0 | 0.020929 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.24885 | 3.035% | CZ 3C | 1.4443 | 1.0736 | 0.042249 | 0.56052 | 0 | 3.091 | 0.16656 | 0.90756 | 0 | 0.67177 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 8.2753 | 3.035% | CZ 3C | 0.42331 | 0.31464 | 0 | 0.053659 | 0 | 0.90592 | 0.048817 | 0.26599 | 0 | 0.19688 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.3024 | 3.035% | CZ 3C | 0 | 0 | 0.00042249 | 0.0037743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041968 | 3.035% |  | CZ 3C | 4.4317 | 3.294 | 0.046178 | 0.97429 | 0 | 9.4841 | 0.51107 | 2.7847 | 0 | 2.0612 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 24.562 | 3.035%
CZ 4A | 0.044998 | 0.033405 | 0.0004669 | 0.19328 | 0 | 0.031489 | 0.0036381 | 0.018373 | 0 | 0.011054 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.34661 | 33.86% | CZ 4A | 1.4443 | 1.0722 | 0.047643 | 13.4821 | 0 | 1.0107 | 0.11678 | 0.58972 | 0 | 0.35482 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 18.4361 | 33.86% | CZ 4A | 0.42331 | 0.31425 | 0 | 0.83938 | 0 | 0.29623 | 0.034225 | 0.17284 | 0 | 0.10399 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.2773 | 33.86% | CZ 4A | 0 | 0 | 0.00047643 | 0.10618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10666 | 33.86% |  | CZ 4A | 4.4317 | 3.2899 | 0.052073 | 20.3931 | 0 | 3.1012 | 0.3583 | 1.8094 | 0 | 1.0887 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 35.4992 | 33.86%
CZ 4B | 0.044998 | 0.033429 | 0.00044818 | 0.086781 | 0 | 0.017837 | 0.0035716 | 0.011405 | 0 | 0.0085823 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.21695 | 0% | CZ 4B | 1.4443 | 1.073 | 0.045732 | 6.0143 | 0 | 0.57252 | 0.11464 | 0.36606 | 0 | 0.27547 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 10.2238 | 0% | CZ 4B | 0.42331 | 0.31448 | 0 | 0.38211 | 0 | 0.1678 | 0.033599 | 0.10729 | 0 | 0.080736 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 1.6024 | 0% | CZ 4B | 0 | 0 | 0.00045732 | 0.047105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047563 | 0% |  | CZ 4B | 4.4317 | 3.2923 | 0.049985 | 9.1489 | 0 | 1.7567 | 0.35175 | 1.1232 | 0 | 0.84523 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 21.9745 | 0%
CZ 4C | 0.044998 | 0.033363 | 0.00049112 | 0.14393 | 0 | -0.0076929 | 0.00052873 | 0.010729 | 0 | 0.0065479 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.2428 | 5.13% | CZ 4C | 1.4443 | 1.0709 | 0.050115 | 10.0049 | 0 | -0.24692 | 0.016971 | 0.34437 | 0 | 0.21017 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 13.2125 | 5.13% | CZ 4C | 0.42331 | 0.31385 | 0 | 0.62975 | 0 | -0.072369 | 0.004974 | 0.10093 | 0 | 0.061598 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 1.5552 | 5.13% | CZ 4C | 0 | 0 | 0.00050115 | 0.078562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.079063 | 5.13% |  | CZ 4C | 4.4317 | 3.2857 | 0.054775 | 15.1797 | 0 | -0.75764 | 0.052072 | 1.0566 | 0 | 0.64487 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 24.9227 | 5.13%
CZ 5A | 0.044998 | 0.033412 | 0.00052746 | 0.27483 | 0 | 0.0096572 | 0.0018173 | 0.023044 | 0 | 0.010021 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.40821 | 14.08% | CZ 5A | 1.4443 | 1.0724 | 0.053823 | 19.1079 | 0 | 0.30998 | 0.058331 | 0.73965 | 0 | 0.32167 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 23.4259 | 14.08% | CZ 5A | 0.42331 | 0.31431 | 0 | 1.2019 | 0 | 0.090849 | 0.017096 | 0.21678 | 0 | 0.094275 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.4516 | 14.08% | CZ 5A | 0 | 0 | 0.00053823 | 0.15007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15061 | 14.08% |  | CZ 5A | 4.4317 | 3.2906 | 0.058828 | 28.9853 | 0 | 0.9511 | 0.17898 | 2.2695 | 0 | 0.98696 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 42.1277 | 14.08%
CZ 5B | 0.044998 | 0.033415 | 0.00050764 | 0.15225 | 0 | 0.0011555 | 0.0022025 | 0.016177 | 0 | 0.0075493 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.26815 | 1.936% | CZ 5B | 1.4443 | 1.0726 | 0.0518 | 10.5388 | 0 | 0.037089 | 0.070694 | 0.51925 | 0 | 0.24232 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 14.2946 | 1.936% | CZ 5B | 0.42331 | 0.31435 | 0 | 0.67208 | 0 | 0.01087 | 0.020719 | 0.15218 | 0 | 0.071019 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 1.7577 | 1.936% | CZ 5B | 0 | 0 | 0.000518 | 0.082456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082974 | 1.936% |  | CZ 5B | 4.4317 | 3.2909 | 0.056617 | 16.0485 | 0 | 0.1138 | 0.21691 | 1.5932 | 0 | 0.7435 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 27.47 | 1.936%
CZ 5C | 0.044998 | 0.033363 | 0.00052636 | 0.13838 | 0 | -0.020635 | -2.8012e-05 | 0.0073742 | 0 | 0.0048461 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.21873 | 0% | CZ 5C | 1.4443 | 1.0709 | 0.05371 | 9.6212 | 0 | -0.66232 | -0.00089913 | 0.2367 | 0 | 0.15555 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 12.2368 | 0% | CZ 5C | 0.42331 | 0.31385 | 0 | 0.60521 | 0 | -0.19412 | -0.00026352 | 0.069372 | 0 | 0.045589 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 1.3561 | 0% | CZ 5C | 0 | 0 | 0.0005371 | 0.075562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076099 | 0% |  | CZ 5C | 4.4317 | 3.2857 | 0.058705 | 14.5948 | 0 | -2.0322 | -0.0027588 | 0.72625 | 0 | 0.47727 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 22.5144 | 0%
CZ 6A | 0.044998 | 0.033394 | 0.00057371 | 0.35946 | 0 | 0.0077559 | 0.0023215 | 0.028671 | 0 | 0.016828 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.5039 | 1.175% | CZ 6A | 1.4443 | 1.0719 | 0.058542 | 24.9436 | 0 | 0.24895 | 0.074516 | 0.92026 | 0 | 0.54015 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 29.62 | 1.175% | CZ 6A | 0.42331 | 0.31415 | 0 | 1.5785 | 0 | 0.072962 | 0.021839 | 0.26971 | 0 | 0.15831 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.9319 | 1.175% | CZ 6A | 0 | 0 | 0.00058542 | 0.19558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19616 | 1.175% |  | CZ 6A | 4.4317 | 3.2888 | 0.063986 | 37.9022 | 0 | 0.76384 | 0.22864 | 2.8236 | 0 | 1.6574 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 52.135 | 1.175%
CZ 6B | 0.044998 | 0.033373 | 0.0005594 | 0.26798 | 0 | 0.00036066 | 0.0012711 | 0.029837 | 0 | 0.0080886 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.39637 | 0.09221% | CZ 6B | 1.4443 | 1.0712 | 0.057081 | 18.3915 | 0 | 0.011576 | 0.040798 | 0.95769 | 0 | 0.25962 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 22.5515 | 0.09221% | CZ 6B | 0.42331 | 0.31395 | 0 | 1.2043 | 0 | 0.0033928 | 0.011957 | 0.28068 | 0 | 0.076092 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.4068 | 0.09221% | CZ 6B | 0 | 0 | 0.00057081 | 0.14283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1434 | 0.09221% |  | CZ 6B | 4.4317 | 3.2868 | 0.06239 | 28.2182 | 0 | 0.03552 | 0.12518 | 2.9385 | 0 | 0.7966 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 40.8697 | 0.09221%
CZ 7 | 0.044998 | 0.033352 | 0.00061996 | 0.35285 | 0 | 0.003484 | 0.0016317 | 0.033555 | 0 | 0.011968 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.49236 | 0.04244% | CZ 7 | 1.4443 | 1.0705 | 0.063261 | 24.2345 | 0 | 0.11183 | 0.052375 | 1.0771 | 0 | 0.38416 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 28.7558 | 0.04244% | CZ 7 | 0.42331 | 0.31375 | 0 | 1.5832 | 0 | 0.032775 | 0.01535 | 0.31567 | 0 | 0.11259 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.8897 | 0.04244% | CZ 7 | 0 | 0 | 0.00063261 | 0.18833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18896 | 0.04244% |  | CZ 7 | 4.4317 | 3.2847 | 0.069145 | 37.1584 | 0 | 0.34313 | 0.1607 | 3.3047 | 0 | 1.1787 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 50.906 | 0.04244%
CZ 8 | 0.044998 | 0.03317 | 0.00069814 | 0.30789 | 0 | -0.010498 | 0.00065829 | 0.030736 | 0 | 0.0076859 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.42523 | 0% | CZ 8 | 1.4443 | 1.0647 | 0.071239 | 20.6537 | 0 | -0.33695 | 0.02113 | 0.98657 | 0 | 0.2467 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 24.4691 | 0% | CZ 8 | 0.42331 | 0.31204 | 0 | 1.4477 | 0 | -0.098755 | 0.0061927 | 0.28915 | 0 | 0.072304 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.545 | 0% | CZ 8 | 0 | 0 | 0.00071239 | 0.15714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15786 | 0% |  | CZ 8 | 4.4317 | 3.2668 | 0.077864 | 32.3312 | 0 | -1.0339 | 0.064832 | 3.0271 | 0 | 0.75695 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 43.8974 | 0%
US Weighted | 0.044998 | 0.033428 | 0.00041821 | 0.13267 | 0 | 0.058069 | 0.0060548 | 0.019284 | 0 | 0.011882 | 0 | 0.0016177 | 0.0075983 | 0 | 0 | 0.0006828 | 0.3167 | 100% | US Weighted | 1.4443 | 1.073 | 0.042675 | 9.2213 | 0 | 1.8639 | 0.19435 | 0.61896 | 0 | 0.38139 | 0 | 0.051925 | 0.24389 | 0 | 0 | 0.021916 | 15.1576 | 100% | US Weighted | 0.42331 | 0.31446 | 0 | 0.58054 | 0 | 0.54628 | 0.05696 | 0.18141 | 0 | 0.11178 | 0 | 0.015218 | 0.07148 | 0 | 0 | 0.0064233 | 2.3079 | 100% | US Weighted | 0 | 0 | 0.00042675 | 0.072405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072831 | 100% |  | US Weighted | 4.4317 | 3.2921 | 0.046644 | 13.9915 | 0 | 5.719 | 0.59631 | 1.8991 | 0 | 1.1702 | 0 | 0.15932 | 0.74833 | 0 | 0 | 0.067246 | 32.1215 | 100%
Building Type: | High-rise Apartment |  |  |  | Percentage Cost Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Cost Index $/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Percentage Site Energy Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Energy Use Index Site kBtu/sq ft/yr | Building Type: | High-rise Apartment |  |  |  | Percentage Electric Savings from Standard 90.1-2004 to 90.1-2019 | [12 empty] | Electric Use Intensity kWh/sq ft/yr | Gas Savings % from 90.1-2004 to 2019 | [17 empty] | Gas Use Intensity therms/sq ft/yr |  | Building Type: | High-rise Apartment |  |  | Percentage Source Energy Savings from Standard 90.1-2004 to 90.1-2019 | [13 empty] | Energy Use Index Source kBtus/sq ft/yr
[6 empty] | Electric Rate, $/kWh: | 0.1063 |  |  |  | Natural Gas Rate, $/therm: | 0.98 |  |  |  |  | Prototype Floor Area: | 84352 | [8 empty] | Electric Conversion, kBtu/kWh: | 3.412 |  |  |  | Natural Gas Conversion, kBtu/therm: | 100 |  |  | Prototype Floor Area: | 84352 | [17 empty] | Prototype Floor Area: | 84352 | Building Type: | High-rise Apartment | [15 empty] | Prototype Floor Area: | 84352 | [7 empty] | Electric Conversion, kBtu/kWh: | 10.469 |  |  |  | Natural Gas Conversion, kBtu/therm: | 109.3
2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight |  | 2004-2019 | Light.Int | Light.Ext | SHW | Heat | Humidfy | Cool | Ht.Rej | Fans | Ht.Rcvy | Pumps | Refrig | Elevator | Txfmr | Cook | IT | Equip | Total | Weight
CZ 0A | 38.43% | 44.74% | 0.2765% |  |  | 30.67% | 44.52% | 19.93% |  | 42.84% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.47% | 0% | CZ 0A | 38.43% | 44.74% | 0.2765% |  |  | 30.67% | 44.52% | 19.93% |  | 42.84% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.24% | 0% | CZ 0A | 38.43% | 44.74% |  |  |  | 30.67% | 44.52% | 19.93% |  | 42.84% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.67% | 0% | CZ 0A |  |  | 0.2765% | [13 empty] | 0.2765% | 0% |  | CZ 0A | 38.43% | 44.74% | 0.2765% |  |  | 30.67% | 44.52% | 19.93% |  | 42.84% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.32% | 0%
CZ 0B | 38.43% | 44.74% | 0.2672% | 97.49% |  | 27.64% | 51.09% | 20% |  | 50.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.89% | 0% | CZ 0B | 38.43% | 44.74% | 0.2672% | 97.87% |  | 27.64% | 51.09% | 20% |  | 50.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 18.65% | 0% | CZ 0B | 38.43% | 44.74% |  | 97.26% |  | 27.64% | 51.09% | 20% |  | 50.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.11% | 0% | CZ 0B |  |  | 0.2672% | 100% | [12 empty] | 0.2954% | 0% |  | CZ 0B | 38.43% | 44.74% | 0.2672% | 97.51% |  | 27.64% | 51.09% | 20% |  | 50.63% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.74% | 0%
CZ 1A | 38.43% | 44.74% | 0.2958% | 100% |  | 31.61% | 65.13% | 15.83% |  | 50.94% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.33% | 14.96% | CZ 1A | 38.43% | 44.74% | 0.2958% | 100% |  | 31.61% | 65.13% | 15.83% |  | 50.94% |  | 2.834% | 59.98% |  |  | 0.2001% | 18.66% | 14.96% | CZ 1A | 38.43% | 44.74% |  | 100% |  | 31.61% | 65.13% | 15.83% |  | 50.94% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.83% | 14.96% | CZ 1A |  |  | 0.2958% | [13 empty] | 0.2958% | 14.96% |  | CZ 1A | 38.43% | 44.74% | 0.2958% | 100% |  | 31.61% | 65.13% | 15.83% |  | 50.94% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.15% | 14.96%
CZ 1B | 38.43% | 44.74% | 0.3% | 92.44% |  | 26.74% | 51.31% | 17.65% |  | 47.72% |  | 2.834% | 59.98% |  |  | 0.2001% | 19.81% | 0% | CZ 1B | 38.43% | 44.74% | 0.3% | 94.63% |  | 26.74% | 51.31% | 17.65% |  | 47.72% |  | 2.834% | 59.98% |  |  | 0.2001% | 17.83% | 0% | CZ 1B | 38.43% | 44.74% |  | 88.8% |  | 26.74% | 51.31% | 17.65% |  | 47.72% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.94% | 0% | CZ 1B |  |  | 0.3% | 96.83% | [12 empty] | 5.193% | 0% |  | CZ 1B | 38.43% | 44.74% | 0.3% | 92.69% |  | 26.74% | 51.31% | 17.65% |  | 47.72% |  | 2.834% | 59.98% |  |  | 0.2001% | 19.67% | 0%
CZ 2A | 38.43% | 44.74% | 0.3232% | 95.41% |  | 29.19% | 55.04% | 17.5% |  | 54.32% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.03% | 12.37% | CZ 2A | 38.43% | 44.74% | 0.3232% | 95.9% |  | 29.19% | 55.04% | 17.5% |  | 54.32% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.23% | 12.37% | CZ 2A | 38.43% | 44.74% |  | 94.45% |  | 29.19% | 55.04% | 17.5% |  | 54.32% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.52% | 12.37% | CZ 2A |  |  | 0.3232% | 96.33% | [12 empty] | 17.37% | 12.37% |  | CZ 2A | 38.43% | 44.74% | 0.3232% | 95.47% |  | 29.19% | 55.04% | 17.5% |  | 54.32% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.98% | 12.37%
CZ 2B | 38.43% | 44.74% | 0.3247% | 95.08% |  | 27.85% | 77.4% | 18.73% |  | 54.05% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.37% | 0.8671% | CZ 2B | 38.43% | 44.74% | 0.3247% | 95.94% |  | 27.85% | 77.4% | 18.73% |  | 54.05% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.55% | 0.8671% | CZ 2B | 38.43% | 44.74% |  | 93.49% |  | 27.85% | 77.4% | 18.73% |  | 54.05% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.88% | 0.8671% | CZ 2B |  |  | 0.3247% | 96.73% | [12 empty] | 16.82% | 0.8671% |  | CZ 2B | 38.43% | 44.74% | 0.3247% | 95.18% |  | 27.85% | 77.4% | 18.73% |  | 54.05% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.31% | 0.8671%
CZ 3A | 38.43% | 44.74% | 0.3561% | 68.86% |  | 31.33% | 64.42% | 17.4% |  | 51.47% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.48% | 5.906% | CZ 3A | 38.43% | 44.74% | 0.3561% | 69.27% |  | 31.33% | 64.42% | 17.4% |  | 51.47% |  | 2.834% | 59.98% |  |  | 0.2001% | 24.23% | 5.906% | CZ 3A | 38.43% | 44.74% |  | 68.03% |  | 31.33% | 64.42% | 17.4% |  | 51.47% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.93% | 5.906% | CZ 3A |  |  | 0.3561% | 69.62% | [12 empty] | 26.45% | 5.906% |  | CZ 3A | 38.43% | 44.74% | 0.3561% | 68.91% |  | 31.33% | 64.42% | 17.4% |  | 51.47% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.54% | 5.906%
CZ 3B | 38.43% | 44.74% | 0.3485% | 82.04% |  | 28.4% | 76.71% | 15.38% |  | 48.96% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.16% | 6.552% | CZ 3B | 38.43% | 44.74% | 0.3485% | 83.01% |  | 28.4% | 76.71% | 15.38% |  | 48.96% |  | 2.834% | 59.98% |  |  | 0.2001% | 19.31% | 6.552% | CZ 3B | 38.43% | 44.74% |  | 80.15% |  | 28.4% | 76.71% | 15.38% |  | 48.96% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.72% | 6.552% | CZ 3B |  |  | 0.3485% | 83.9% | [12 empty] | 16.12% | 6.552% |  | CZ 3B | 38.43% | 44.74% | 0.3485% | 82.15% |  | 28.4% | 76.71% | 15.38% |  | 48.96% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.09% | 6.552%
CZ 3C | 38.43% | 44.74% | 0.3594% | 58.91% |  | 79.04% | 93.68% | 38.91% |  | 80.34% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.92% | 3.035% | CZ 3C | 38.43% | 44.74% | 0.3594% | 56.54% |  | 79.04% | 93.68% | 38.91% |  | 80.34% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.03% | 3.035% | CZ 3C | 38.43% | 44.74% |  | 62.58% |  | 79.04% | 93.68% | 38.91% |  | 80.34% |  | 2.834% | 59.98% |  |  | 0.2001% | 29.21% | 3.035% | CZ 3C |  |  | 0.3594% | 54.01% | [12 empty] | 3.37% | 3.035% |  | CZ 3C | 38.43% | 44.74% | 0.3594% | 58.64% |  | 79.04% | 93.68% | 38.91% |  | 80.34% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.55% | 3.035%
CZ 4A | 38.43% | 44.74% | 0.3726% | 65.98% |  | 25.64% | 62.18% | 20.5% |  | 46.51% |  | 2.834% | 59.98% |  |  | 0.2001% | 27.44% | 33.86% | CZ 4A | 38.43% | 44.74% | 0.3726% | 66.35% |  | 25.64% | 62.18% | 20.5% |  | 46.51% |  | 2.834% | 59.98% |  |  | 0.2001% | 30.61% | 33.86% | CZ 4A | 38.43% | 44.74% |  | 65.2% |  | 25.64% | 62.18% | 20.5% |  | 46.51% |  | 2.834% | 59.98% |  |  | 0.2001% | 24.66% | 33.86% | CZ 4A |  |  | 0.3726% | 66.67% | [12 empty] | 37.15% | 33.86% |  | CZ 4A | 38.43% | 44.74% | 0.3726% | 66.03% |  | 25.64% | 62.18% | 20.5% |  | 46.51% |  | 2.834% | 59.98% |  |  | 0.2001% | 27.72% | 33.86%
CZ 4B | 38.43% | 44.74% | 0.3675% | 74.39% |  | 13.94% | 75.06% | 12.59% |  | 42.7% |  | 2.834% | 59.98% |  |  | 0.2001% | 20% | 0% | CZ 4B | 38.43% | 44.74% | 0.3675% | 75.24% |  | 13.94% | 75.06% | 12.59% |  | 42.7% |  | 2.834% | 59.98% |  |  | 0.2001% | 21.48% | 0% | CZ 4B | 38.43% | 44.74% |  | 72.66% |  | 13.94% | 75.06% | 12.59% |  | 42.7% |  | 2.834% | 59.98% |  |  | 0.2001% | 18.88% | 0% | CZ 4B |  |  | 0.3675% | 75.98% | [12 empty] | 25.51% | 0% |  | CZ 4B | 38.43% | 44.74% | 0.3675% | 74.49% |  | 13.94% | 75.06% | 12.59% |  | 42.7% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.12% | 0%
CZ 4C | 38.43% | 44.74% | 0.3811% | 75.45% |  | -37.75% | 60.16% | 16.2% |  | 38.74% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.65% | 5.13% | CZ 4C | 38.43% | 44.74% | 0.3811% | 75.82% |  | -37.75% | 60.16% | 16.2% |  | 38.74% |  | 2.834% | 59.98% |  |  | 0.2001% | 26.94% | 5.13% | CZ 4C | 38.43% | 44.74% |  | 74.69% |  | -37.75% | 60.16% | 16.2% |  | 38.74% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.75% | 5.13% | CZ 4C |  |  | 0.3811% | 76.13% | [12 empty] | 33.69% | 5.13% |  | CZ 4C | 38.43% | 44.74% | 0.3811% | 75.5% |  | -37.75% | 60.16% | 16.2% |  | 38.74% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.94% | 5.13%
CZ 5A | 38.43% | 44.74% | 0.3898% | 63.02% |  | 16.68% | 68.2% | 24.96% |  | 45.89% |  | 2.834% | 59.98% |  |  | 0.2001% | 30.26% | 14.08% | CZ 5A | 38.43% | 44.74% | 0.3898% | 63.25% |  | 16.68% | 68.2% | 24.96% |  | 45.89% |  | 2.834% | 59.98% |  |  | 0.2001% | 33.97% | 14.08% | CZ 5A | 38.43% | 44.74% |  | 62.52% |  | 16.68% | 68.2% | 24.96% |  | 45.89% |  | 2.834% | 59.98% |  |  | 0.2001% | 26.55% | 14.08% | CZ 5A |  |  | 0.3898% | 63.46% | [12 empty] | 40.21% | 14.08% |  | CZ 5A | 38.43% | 44.74% | 0.3898% | 63.05% |  | 16.68% | 68.2% | 24.96% |  | 45.89% |  | 2.834% | 59.98% |  |  | 0.2001% | 30.61% | 14.08%
CZ 5B | 38.43% | 44.74% | 0.3831% | 66.17% |  | 1.396% | 73.83% | 17.23% |  | 40.25% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.04% | 1.936% | CZ 5B | 38.43% | 44.74% | 0.3831% | 66.58% |  | 1.396% | 73.83% | 17.23% |  | 40.25% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.96% | 1.936% | CZ 5B | 38.43% | 44.74% |  | 65.31% |  | 1.396% | 73.83% | 17.23% |  | 40.25% |  | 2.834% | 59.98% |  |  | 0.2001% | 20.52% | 1.936% | CZ 5B |  |  | 0.3831% | 66.95% | [12 empty] | 32.11% | 1.936% |  | CZ 5B | 38.43% | 44.74% | 0.3831% | 66.22% |  | 1.396% | 73.83% | 17.23% |  | 40.25% |  | 2.834% | 59.98% |  |  | 0.2001% | 23.3% | 1.936%
CZ 5C | 38.43% | 44.74% | 0.3912% | 82.92% |  | -373.9% | -11.11% | 12.21% |  | 32.58% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.2% | 0% | CZ 5C | 38.43% | 44.74% | 0.3912% | 83.28% |  | -373.9% | -11.11% | 12.21% |  | 32.58% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.91% | 0% | CZ 5C | 38.43% | 44.74% |  | 82.15% |  | -373.9% | -11.11% | 12.21% |  | 32.58% |  | 2.834% | 59.98% |  |  | 0.2001% | 18.92% | 0% | CZ 5C |  |  | 0.3912% | 83.59% | [12 empty] | 33.42% | 0% |  | CZ 5C | 38.43% | 44.74% | 0.3912% | 82.96% |  | -373.9% | -11.11% | 12.21% |  | 32.58% |  | 2.834% | 59.98% |  |  | 0.2001% | 22.53% | 0%
CZ 6A | 38.43% | 44.74% | 0.4019% | 60.11% |  | 11.74% | 67.72% | 27.1% |  | 54.6% |  | 2.834% | 59.98% |  |  | 0.2001% | 32.52% | 1.175% | CZ 6A | 38.43% | 44.74% | 0.4019% | 60.4% |  | 11.74% | 67.72% | 27.1% |  | 54.6% |  | 2.834% | 59.98% |  |  | 0.2001% | 36.2% | 1.175% | CZ 6A | 38.43% | 44.74% |  | 59.52% |  | 11.74% | 67.72% | 27.1% |  | 54.6% |  | 2.834% | 59.98% |  |  | 0.2001% | 28.58% | 1.175% | CZ 6A |  |  | 0.4019% | 60.64% | [12 empty] | 41.9% | 1.175% |  | CZ 6A | 38.43% | 44.74% | 0.4019% | 60.15% |  | 11.74% | 67.72% | 27.1% |  | 54.6% |  | 2.834% | 59.98% |  |  | 0.2001% | 32.88% | 1.175%
CZ 6B | 38.43% | 44.74% | 0.3971% | 63.86% |  | 0.7687% | 72.46% | 28.24% |  | 40.73% |  | 2.834% | 59.98% |  |  | 0.2001% | 29.64% | 0.09221% | CZ 6B | 38.43% | 44.74% | 0.3971% | 64% |  | 0.7687% | 72.46% | 28.24% |  | 40.73% |  | 2.834% | 59.98% |  |  | 0.2001% | 33.14% | 0.09221% | CZ 6B | 38.43% | 44.74% |  | 63.56% |  | 0.7687% | 72.46% | 28.24% |  | 40.73% |  | 2.834% | 59.98% |  |  | 0.2001% | 26.15% | 0.09221% | CZ 6B |  |  | 0.3971% | 64.13% | [12 empty] | 39.13% | 0.09221% |  | CZ 6B | 38.43% | 44.74% | 0.3971% | 63.88% |  | 0.7687% | 72.46% | 28.24% |  | 40.73% |  | 2.834% | 59.98% |  |  | 0.2001% | 29.97% | 0.09221%
CZ 7 | 38.43% | 44.74% | 0.409% | 61.47% |  | 6.507% | 66.57% | 30.23% |  | 48.59% |  | 2.834% | 59.98% |  |  | 0.2001% | 32.4% | 0.04244% | CZ 7 | 38.43% | 44.74% | 0.409% | 61.54% |  | 6.507% | 66.57% | 30.23% |  | 48.59% |  | 2.834% | 59.98% |  |  | 0.2001% | 35.79% | 0.04244% | CZ 7 | 38.43% | 44.74% |  | 61.33% |  | 6.507% | 66.57% | 30.23% |  | 48.59% |  | 2.834% | 59.98% |  |  | 0.2001% | 28.75% | 0.04244% | CZ 7 |  |  | 0.409% | 61.6% | [12 empty] | 41.04% | 0.04244% |  | CZ 7 | 38.43% | 44.74% | 0.409% | 61.48% |  | 6.507% | 66.57% | 30.23% |  | 48.59% |  | 2.834% | 59.98% |  |  | 0.2001% | 32.72% | 0.04244%
CZ 8 | 38.43% | 44.74% | 0.4271% | 52.38% |  | -41.94% | 64.6% | 25.86% |  | 37.23% |  | 2.834% | 59.98% |  |  | 0.2001% | 28% | 0% | CZ 8 | 38.43% | 44.74% | 0.4271% | 52.04% |  | -41.94% | 64.6% | 25.86% |  | 37.23% |  | 2.834% | 59.98% |  |  | 0.2001% | 30.21% | 0% | CZ 8 | 38.43% | 44.74% |  | 53.04% |  | -41.94% | 64.6% | 25.86% |  | 37.23% |  | 2.834% | 59.98% |  |  | 0.2001% | 25.58% | 0% | CZ 8 |  |  | 0.4271% | 51.74% | [12 empty] | 33.55% | 0% |  | CZ 8 | 38.43% | 44.74% | 0.4271% | 52.34% |  | -41.94% | 64.6% | 25.86% |  | 37.23% |  | 2.834% | 59.98% |  |  | 0.2001% | 28.21% | 0%
US Weighted | 38.43% | 44.74% | 0.3551% | 75.97% | 0% | 23.95% | 64.96% | 19.89% | 0% | 49.17% | 0% | 2.834% | 59.98% | 0% | 0% | 0.2001% | 25.23% | 100% | US Weighted | 38.43% | 44.74% | 0.3551% | 76.24% | 0% | 23.95% | 64.96% | 19.89% | 0% | 49.17% | 0% | 2.834% | 59.98% | 0% | 0% | 0.2001% | 26.43% | 100% | US Weighted | 38.43% | 44.74% | 0% | 75.38% | 0% | 23.95% | 64.96% | 19.89% | 0% | 49.17% | 0% | 2.834% | 59.98% | 0% | 0% | 0.2001% | 23.91% | 100% | US Weighted | 0 | 0 | 0.3551% | 61.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 26.19% | 18.41% | 0% | US Weighted | 38.43% | 44.74% | 0.3551% | 76% | 0% | 23.95% | 64.96% | 19.89% | 0% | 49.17% | 0% | 2.834% | 59.98% | 0% | 0% | 0.2001% | 25.35% | 100%